## Equipment Inventory
Equipment Type | Purpose | Major Components | Typical Inspection Points | Maintenance Activities | Common Observable Issues | Relevant Measurements | Safety Considerations | Relevant Maintenance Documents | Source | Research Notes | Maintenance Frequency (D09) | D09 Chunk / Page | D09 Scope Note
Transformer | Transfers electrical energy between voltage levels and provides isolation as designed. | Windings; core; insulation system; tank; bushings; oil/insulation system; cooling equipment; conservator/expansion arrangement; tap changer where fitted; protection/monitoring accessories. | External condition; oil leakage/staining; oil level/indicators; bushings and connections; cooling equipment; conservator/breather where fitted; temperature/monitoring indicators; earthing; unusual noise/smell; alarms. | Visual inspection; cleanliness; check leaks and connections; inspect cooling and accessories; condition monitoring/testing as specified by equipment/utility procedures; oil sampling/testing where applicable; record observations and results. | Oil leakage; abnormal temperature indication; damaged/dirty bushing; cooling equipment abnormality; loose/corroded connection; unusual external condition. | Temperature/oil-level indications; insulation/oil test results; electrical test results; vibration/noise observations where procedures specify. Do not infer a fault from one measurement alone. | Follow permit/isolating/earthing procedures and manufacturer/utility instructions; transformer-specific work must be performed by competent personnel. | D04; D06; D07; D08; D09 | D04; D06; D07; D08; D09 | Sources: NPTI O&M/transformer programmes; CEA regulations and failure report. | Hourly to 7-10 years depending on item | D09-C0009; PDF p. 26-30 | D09 directly covers power-transformer periodic inspection at manned substations. It specifies different frequencies by item; do not treat one frequency as universal.
Circuit Breaker | Makes, carries and interrupts current in normal and fault conditions as part of protection/switching. | Interrupting chamber; contacts; operating mechanism; control circuit; insulation medium/system; terminals; auxiliary/interlock components. | External condition; operating mechanism indicators; control/auxiliary wiring; terminals/connections; gas/pressure indication where applicable; signs of leakage/damage; local indication. | Inspection; mechanical/electrical functional checks; contact/operating mechanism maintenance; testing and condition monitoring; gas/oil-related checks where applicable and per manufacturer. | Gas/oil leakage where applicable; abnormal mechanism indication; damaged enclosure/insulation; corrosion; control wiring issues; overheating signs. | Operating/trip/close test results; insulation/contact-related test results; pressure/density indication for applicable designs. | Only after authorized isolation/clearance and according to breaker type, manufacturer procedure and safety rules. | D01; D02; D05; D06; D09 | D01; D02; D05; D06; D09 | Sources: NPTI switchgear/CB programmes; CEA safety regulations. | Weekly to two-yearly depending on breaker type/item | D09-C0010; D09-C0011; PDF pp. 34-35, 36-39 | D09 covers VCB/SF6 and Oil Circuit Breaker maintenance with different frequencies. Apply only to the relevant breaker type and item.
Isolator / Disconnector | Provides visible isolation of a circuit; often associated with an earth switch/interlocking scheme. | Fixed/moving contacts; operating mechanism; insulators; linkages; terminals; earth switch where fitted; interlocks. | Contact alignment/condition; insulators; linkage/mechanism; terminals; visible damage/corrosion; position indication; interlocks where accessible. | Visual/mechanical inspection; cleaning where specified; contact/mechanism inspection; lubrication/adjustment where manufacturer permits; functional/interlock checks under authorized conditions. | Misalignment; damaged insulator; corrosion; loose hardware; incomplete/abnormal position indication. | Position indication; mechanical/functional test observations; contact resistance where specified by procedure. | Never treat a visual position indication alone as proof of de-energization; follow approved isolation and earthing procedure. | D01; D02; D05; D09 | D01; D02; D05; D09 | Sources listed above. | Yearly (all listed items) | D09-C0015; PDF p. 44 | D09 lists the cited isolator/disconnector maintenance items as yearly.
CT | Provides scaled current information for protection, metering and monitoring. | Primary conductor/terminal; secondary winding/terminals; insulation; core(s); enclosure; secondary circuit wiring. | External insulation/body; terminals; signs of overheating/damage; oil leakage where oil-filled; nameplate/labels; secondary wiring condition. | Inspection; secondary circuit checks; insulation/electrical tests as specified; condition monitoring; record test results. | Cracked/damaged insulation; oil leakage where applicable; overheating/discoloration; loose/damaged terminals; damaged enclosure. | Ratio/polarity/insulation and other test results only when performed with approved test equipment/procedure. | CT secondary circuits have specific safety hazards; maintenance must follow approved isolation/shorting/testing procedures and manufacturer/utility rules. | D01; D02; D06; D09 | D01; D02; D06; D09 | Sources listed above. | Weekly to Yearly | D09-C0012; PDF p. 40-41 | D09 lists weekly and yearly CT checks/tests.
PT / CVT | Provides scaled voltage information for metering, protection and control; CVT uses capacitive division. | Primary insulation; transformer/inductive section or capacitive stack for CVT; secondary terminals; enclosure; damping/auxiliary components as applicable. | External condition; insulation/body; oil leakage where applicable; terminals; visible damage; nameplate/labels; associated secondary wiring. | Inspection; insulation/electrical tests; checks of secondary circuits and associated devices; condition monitoring per equipment procedure. | Oil leakage where applicable; cracked/damaged insulation; corrosion; overheating/discoloration; damaged enclosure. | Electrical test results and secondary measurements only when obtained through approved procedures. | Follow isolation, discharge/earthing and manufacturer procedures; do not infer internal condition from appearance alone. | D01; D02; D06; D09 | D01; D02; D06; D09 | Sources listed above. | Weekly, Yearly, and 3-Yearly | D09-C0013; PDF p. 41-42 | D09 source labels the equipment PT/VT. Do not assume every CVT has identical maintenance without applicable source/manufacturer confirmation.
Surge Arrester | Limits/controls surge overvoltage exposure of substation equipment by diverting surge energy to earth. | Nonlinear varistor elements; insulating housing; terminals; grading/sealing components as applicable; earth connection. | Housing condition; cracks/chips; contamination; signs of thermal damage; counter/monitor condition where fitted; earth connection; mounting condition. | Visual inspection; cleaning where specified; leakage/current/condition tests where applicable; earth-connection checks; record condition-monitoring results. | Cracked housing; contamination; discoloration/thermal damage; damaged counter/indicator; corroded/loose earth connection. | Leakage/current or diagnostic test results when specified; visual condition alone cannot establish arrester health. | Maintain required clearances and approved isolation/earthing; high-voltage testing requires trained personnel. | D01; D02; D06; D09 | D01; D02; D06; D09 | Sources listed above. | Monthly and Yearly | D09-C0014; PDF p. 43 | D09 lists monthly condition/monitor checks and yearly maintenance/test items.
Busbar | Common conductor arrangement that connects multiple circuits/bays in a substation. | Conductors; supports/insulators; joints; clamps/connectors; sectionalizers/couplers depending on scheme; associated earthing/structures. | Insulator condition; joints/connectors; corrosion; contamination; physical damage; clearances/foreign objects; visible hot-spot evidence where thermography is used. | Visual inspection; thermographic monitoring where authorized; joint/connection inspection during outages; insulation/support inspection; maintenance according to design and utility procedure. | Discoloration/thermal signs; damaged insulator; corrosion; loose/failed hardware; contamination; foreign-object/vegetation encroachment. | Thermal images/temperature measurements where an approved thermography process is used; electrical tests where specified. | High-voltage clearances and isolation are critical; never inspect energized equipment outside authorized procedures. | D01; D02; D05; D09 | D01; D02; D05; D09 | Sources listed above. | NOT VERIFIED | NOT VERIFIED | D09 chunk set used for this update does not provide a direct busbar maintenance frequency. Do not invent one.
Battery Bank | Provides DC backup/control power for protection, control, communication and automation equipment. | Battery cells/blocks; interconnections; terminals; racks; charger interface; monitoring equipment; electrolyte system for applicable battery type. | Terminal condition; corrosion; swelling/leakage; electrolyte condition where applicable; charger/indication; ventilation/room condition; cleanliness; physical damage. | Inspection; terminal/interconnection checks; charger and battery monitoring; charging/discharging tests as specified; capacity/condition testing per battery type and manufacturer. | Corrosion; leakage; swelling; damaged terminals; abnormal indication; poor housekeeping/ventilation conditions. | Cell/block voltage, current, specific gravity for applicable flooded batteries, capacity/condition test results—only when specified for the battery type. | Battery rooms and DC systems require specific electrical/chemical safety controls; follow battery-specific procedures and PPE. | D02; D05; D09 | D02; D05; D09 | Sources listed above. | Daily to Yearly depending on item | D09-C0017; PDF p. 46-47 | D09 lists daily, monthly, half-yearly/continuous-monitoring and yearly activities; complete overhaul follows manufacturer recommendation.
Protection Relay | Detects defined electrical abnormal conditions and initiates/commands protective action through the protection scheme. | Protection logic; measurement inputs; relay hardware/software; trip outputs; communications/settings interface; auxiliary supply. | Relay panel condition; alarms/indications; wiring/terminals; labels; event/target indications; settings record; communication status where visible. | Inspection; settings verification; secondary-injection/functional testing as applicable; trip-circuit checks; event/alarm review; documentation of settings and test results. | Alarm/target indication; wiring damage; communication/alarm abnormality; incorrect/missing documentation; visible panel damage. | Relay settings, test results, event records, trip-circuit results; visual inspection alone cannot prove protection performance. | Testing and setting changes require authorized protection personnel and approved procedures; changes must be controlled/documented. | D01; D02; D05; D09 | D01; D02; D05; D09 | Sources listed above. | NOT VERIFIED | NOT VERIFIED | D09 directly covers the Control & Relay Panel, not a standalone generic protection-relay maintenance frequency. Do not map the panel schedule onto all relays.
Earthing System | Provides a controlled path for fault current and helps control touch/step potential and earth potential rise. | Earth grid/mat; equipment earth connections; neutral earthing connections; earth electrodes/risers; bonds; test links; fences/structures as applicable. | Visible earth conductors/bonds; corrosion; loose/damaged connections; electrode/earth-pit condition where accessible; continuity of bonds; physical damage. | Visual inspection; continuity/bond checks; earth resistance/impedance measurements where specified; inspection of grid connections; documentation of test results. | Corrosion; broken/loose earth conductor; damaged bond; missing connection; degraded earth-pit hardware. | Earth resistance/impedance and continuity results obtained by approved test methods; visual condition cannot establish grid adequacy. | CEA requires substation equipment and non-current-carrying metal parts to be effectively earthed and addresses touch/step potential and earth-potential-rise safety. | D02; D05; D09 | D02; D05; D09 | Sources listed above. | Monthly, Half-Yearly, Yearly | D09-C0019; PDF p. 50-51 | D09 lists monthly earth-pit checks, half-yearly earth-connection checks and yearly earthing checks/tests.
Switchgear | Encompasses switching/protection equipment used to control, isolate and protect electrical circuits; may include breakers, disconnectors, relays and associated assemblies. | Enclosure/panels; breakers; disconnectors; busbars; protection/control; insulation; interlocks; terminals; auxiliary systems. | Enclosure condition; doors/locks; labels; indicators; terminals; breaker/disconnector condition; signs of overheating; cleanliness; interlocks/alarms where accessible. | Inspection; cleaning/maintenance; mechanical/electrical functional tests; insulation and breaker tests as applicable; fault finding; checklist-based maintenance. | Overheating/discoloration; damaged enclosure; corrosion; abnormal indicators; loose/damaged wiring; mechanism issues. | Test results from approved procedures; visual inspection is useful for external condition but not internal electrical health. | Use equipment-specific isolation/permit/earthing procedures; only qualified personnel should perform energized or high-voltage work. | D01; D02; D05; D06; D09 | D01; D02; D05; D06; D09 | Sources listed above. | NOT VERIFIED | NOT VERIFIED | D09 has direct schedules for specific switchgear such as circuit breakers and GIS, but not one universal switchgear frequency. Use equipment-specific schedules.

## KB Alignment
Equipment Type | KB Document IDs | Why These KB Sources Are Relevant
Transformer | D04; D06; D07; D08; D09 | D04/D08: transformer O&M/specification; D07: installation/testing; D06: failure analysis; D09: periodic O&M schedules
Circuit Breaker | D01; D02; D05; D06; D09 | D01: switchyard context; D02/D05: safety/O&M regulation; D06: failure analysis; D09: breaker maintenance schedules
Isolator / Disconnector | D01; D02; D05; D09 | Switchyard context, safety/O&M baseline and D09 equipment-specific maintenance
CT | D01; D02; D06; D09 | Switchyard/instrument-transformer context, safety, failure evidence and D09 maintenance
PT / CVT | D01; D02; D06; D09 | Switchyard/instrument-transformer context, safety, failure evidence and D09 PT/VT maintenance
Surge Arrester | D01; D02; D06; D09 | Technical/switchyard context, safety, failure evidence and D09 maintenance
Busbar | D01; D02; D05; D09 | Switchyard design/context and safety/O&M; no universal D09 busbar frequency
Battery Bank | D02; D05; D09 | Safety/O&M baseline and D09 battery/DC maintenance activities
Protection Relay | D01; D02; D05; D09 | Control/protection context, safety/O&M and D09 Control & Relay Panel coverage; standalone relay frequency remains NOT VERIFIED
Earthing System | D02; D05; D09 | CEA safety/O&M requirements and D09 earthing checks
Switchgear | D01; D02; D05; D06; D09 | Switchyard context, safety/O&M, failure evidence and equipment-specific D09 schedules

## D09 Frequency Map
Equipment Type | Maintenance Frequency (D09) | D09 Chunk / Page | D09 Scope Note
Transformer | Hourly to 7-10 years depending on item | D09-C0009; PDF pp. 22-26 | D09 directly covers power-transformer periodic inspection at manned substations. It specifies different frequencies by item; do not treat one frequency as universal.
Circuit Breaker | Weekly to two-yearly depending on breaker type/item | D09-C0010; D09-C0011; PDF pp. 30-35 | D09 covers VCB/SF6 and Oil Circuit Breaker maintenance with different frequencies. Apply only to the relevant breaker type and item.
Isolator / Disconnector | Yearly (all listed items) | D09-C0015; PDF p. 40 | D09 lists the cited isolator/disconnector maintenance items as yearly.
CT | Weekly to Yearly | D09-C0012; PDF pp. 36-37 | D09 lists weekly and yearly CT checks/tests.
PT / CVT | Weekly, Yearly, and 3-Yearly | D09-C0013; PDF pp. 37-38 | D09 source labels the equipment PT/VT. Do not assume every CVT has identical maintenance without applicable source/manufacturer confirmation.
Surge Arrester | Monthly and Yearly | D09-C0014; PDF p. 39 | D09 lists monthly condition/monitor checks and yearly maintenance/test items.
Busbar | NOT VERIFIED | NOT VERIFIED | D09 chunk set used for this update does not provide a direct busbar maintenance frequency. Do not invent one.
Battery Bank | Daily to Yearly depending on item | D09-C0017; PDF pp. 42-43 | D09 lists daily, monthly, half-yearly/continuous-monitoring and yearly activities; complete overhaul follows manufacturer recommendation.
Protection Relay | NOT VERIFIED | NOT VERIFIED | D09 directly covers the Control & Relay Panel, not a standalone generic protection-relay maintenance frequency. Do not map the panel schedule onto all relays.
Earthing System | Monthly, Half-Yearly, Yearly | D09-C0019; PDF pp. 46-47 | D09 lists monthly earth-pit checks, half-yearly earth-connection checks and yearly earthing checks/tests.
Switchgear | NOT VERIFIED | NOT VERIFIED | D09 has direct schedules for specific switchgear such as circuit breakers and GIS, but not one universal switchgear frequency. Use equipment-specific schedules.