## knowledge_chunks
Chunk ID | Document ID | Original Filename | Document Title | Organization | Authority Level | Equipment | Equipment Subtype | Topic | Subtopic | Knowledge Type | Verified Information | Procedure | Frequency | Technical Limit / Value | Safety Information | Troubleshooting / Failure Information | Applicability | PDF Page | Source Section | Notes
D01-C0001 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | The. sub-stations/ switchyards constitute of transmission system, which interconnects power transmission ‘circuits and transformation. between networks of different voltages. It is required to pay careful attention in planning, designing and constructing the sub-stations/ switchyards, since its reliability directly affects the power supply availability. Sub-stations generally comprise of switchgear, power transformer, control, protection, monitoring and automation equipment. The highest transmission system voltage in operation in the country is 800kV. Further, 1200kV level: is also under consideration in near future. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 9 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0002 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | AIS is most commonly used so far; however, GIS/ hybrid substation may be adopted considering techno-economic viability. GIS is generally preferred, where availability of space and safety are major constraints, seismic prone areas, coastal areas and very heavily polluted areas etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 9 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0003 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | The selection of switching schemes depends on operational flexibility, system safety, reliability & availability, ability to facilitate the system control and cost. However, other types of switching schemes can be considered, if system | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 10 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0004 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | ‘iShisae loastaad Suhekine oc Dimension ‘oltage level switching scheme Width (m) ¦ Depth (m) 1) 765kV system : Breaker & half scheme. (I-type )” 527) 320 2) 400kV system : i) Breaker and a half scheme - Hype 27 170 = .D-type 27421427 120% 27421427 170 ii) Double main & transfer bus scheme 28 120 13).220KV system: / ___i) Double main & transfer bus scheme 18 Bb A) T32KV system ¦ 7 ¦ i) Double bus scheme 12 BARTS ii) Main and Transfer 12 B © Tn case of 765kV, only [type is adopted, © Considering 765kV I-phase transformer/ fire wall, 54M may be considered. Further economization can be done based on féeders/ transformers & reactor requirements during detailed engineering, © D on one side of bus only, D on both side of bus | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 11 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0005 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | The bays shall be arranged suitably such that skew/ deviation of outgoing and incoming connections shall not exceed 30°. The safety clearances shall be reviewed critically in case skew/ deviation angle exceeds 15°, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 12 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0006 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | The necessary equipments such as JEDs, transducers etc. shall be housed either in’ switchyard control room or outdoor air conditioned kiosks (air conditioned bay control rooms) for control and protection purpose. All switchyard equipments shall be controlled either from switchyard control toom or outdoor air conditioned kiosks; moreover, equipment of generator shall be controlled from main control room of the unit(s). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 12 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0007 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | The control room shall preferably be located to oversee the entire. switchyard from the control room. However, video cameras may also be installed suitably for viewing the: switchyard. Switchyard control room building shall be air- conditioned and properly ventilated, single/ double storied, located generally inside the switchyard premises. between transformer yard and switchyard. Layout shall take into account the fire protection requirements and oil soaking/ collection pit in case of oil filled reactors/ auto-transformers located in switchyard, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 12 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0008 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | The layout of the AIS shall depend on area available for the sub-station, the number of line bays of different voltage levels, the number of main transformers, busbar/ switching schemes, protection against direct lightning and the possibility of future extension. Sufficient area shall also be taken into consideration for future expansion. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 13 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0009 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | sub-station. However, video cameras may also be installed suitably for viewing the sub-station. The dimension of the building depends on the control, protection, monitoring and automation system proposed to be provided for the sub-station. . | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 13 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0010 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | SA shall be subjected to type, routine and acceptance tests as per IEC60099-4. In case type tests are not to be performed and type test reports are to be submitted, the manufacturer shall furnish certificate of conformity to relevant Standards from independent and approved test laboratory. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 25 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0011 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | SA monitors shall also be connected in series with the test specimens during residual voltage and current impulse withstand tests to establish. its performance. Additional routine/ functional tests with one 100A and 10kA current impulse (8/20p-sec.) shall also be performed on the surge monitor. Surge monitors shall be routinely tested for water dip test at 1.5m for 30minutes. No water vapors shall be visible on the monitor glass. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 25 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0012 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | 765/400/33kKV or 765/220/33kKV or 400/220/33KV or 400/132/33kV auto- transformers (ICT) with on-load tap changer (OLTC) conforming to IEC 60076/ TS.2026 shall be provided for inter connection between 132kV or 220kV and/or 400kV and 76SkV switchyard buses. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 25 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0013 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | Tt shall be provided with minimum 5x25% unit coolers. Each unit cooler shall be provided with its own cooling fans, oil pumps etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 25 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0014 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | It shali be capable of operating at full load for at least ten (10) minutes during total failure of auxiliary power supply to cooling fans and pumps without exceeding winding hot spot temperature exceeding 140°C. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 25 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0015 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | It-shall also be capable of operating for 20 minutes in the event of failure of oil circulating pumps or blowers associated with all unit coolers except one unit Cooler without exceeding winding hot spot temperature exceeding 140°C. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 25 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0016 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | Sensors protective devices-its location, fitment, and level of redundancy Oil and oil preservation system | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 31 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0017 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | Electrical and physical interfaces with sub-station. - Earthing | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 31 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0018 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | ii) The wave trap shall be broadband type tuned for its entire carrier frequency range. The resistive component of impedance of the line trap within its bandwidth shall not be less than 450Q for 765/ 400kV system and 570Q for 220/ 132kV system. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 31 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0019 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | i) Disconnectors shall be single pole, group operated with motor operated mechanism as per IEC 62271-102. ‘The provision of emergency manual operation shall also be included. Safety interlocks shall be provided to prevent | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 63 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0020 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | i) Earth switch shall be provided with manual operating mechanism as per IEC- 62271-102. If electrical operating mechanism is envisaged, motor operated mechanism shall be provided with electrical control from local position. Safety interlocks shall be provided for closing of earth switch when disconnector is closed and vice versa. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 63 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0021 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | SN Details ¦ Unit ¦ 765kV ¦ 400kV ¦ 220kV ¦ 132kKV 33KV ¦ system system system: system {system 1) _ Nominai/ Rated voltage W 765 700 220 132 733 3) _¦ Highest system voltage W800 ¦ 420 245 18 36 3) ¦ Fault current and duration kA 40/50 40/50/63 ¦ 40/50 315 25 (Lsec) -(1'sec) ¦ (1sec) ¦ (1sec) ¦ (see) 4) _¦ Rated primary voltage KV, 800N3 ¦ 420N3 ¦ 2453 ¦ 1453 ¦ 363. 5) _¦ Rated secondary voltage”? Vv TIOAN3 1103. T10N3 TONS. i103 6) ¦ Accuracy class z i fs , i = protection 3P_ i. 3P a) 6P. OP. = metering” 02 ¦. 02°: 02 02 02 7) ¦ Lightning Full wave) impulse kVp. ¦ 2100 ¦ 1425 7050 650 170 withstand voltage (1.2/50 ps) = between line terminals and ground _ 8) ¦ Switching impulse withstand KVp ¦ 1550, . 1050 = aa — voltage (250/2500us) - between line terminals and ground (dry & wet) 9) [One minute power frequency kVims ¦ 975 630 460 275 75 withstand voltage (dry (dry ¦ - between line... | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 92 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0022 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | 5) Neutral earthing Earthed through neutral reactor | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 104 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D01-C0023 | D01 | 765_powerplants.pdf | General Guidelines for 765/400/220/132kV substations and switchyard of Thermal/Hydro Power Projects | Central Electricity Authority | HIGH | Substation / Switchyard | NOT VERIFIED | Design / Maintenance-relevant guidance | Verified OCR-extracted information | DESIGN_REFERENCE | Top oil temperature: 40°C (thermometer method); winding temperature: 45°C (resistance method) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 765/400/220/132 kV substations and switchyards of thermal/hydro power projects | PDF p. 104 | NOT VERIFIED | Verified against OCR text from the scanned PDF page. This D01 source is image-based; only OCR-confirmed pages were included in this rebuilt core. Do not treat omitted pages as NOT COVERED.
D02-C0001 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | No. CEA-TH-17-17/5/2021-TETD Division.—Whereas the public notices advertising the proposal to amend the Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Regulations, 2011 were published in six newspaper dailies, as required by sub- section (3) of section 177 of the Electricity Act, 2003 (36 of 2003) inviting objections and suggestions from all persons likely to be affected thereby, within forty seven days from the date on which the copies of the newspaper containing the said publications were made available to the public; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | No. CEA-TH-17-17/5/2021-TETD Division.—Whereas the public notices advertising the proposal to amend the Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Regulations, 2011 were published in six newspaper dailies, as required by sub- section (3) of section 177 of the Electricity Act, 2003 (36 of 2003) inviting objections and suggestions from all persons likely to be affected thereby, within forty seven days from the date on which the copies of the newspaper containing the said publications were made available to the public; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 9 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0002 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Now, therefore, in exercise of the powers conferred by clause (c) of section 73 read with sub-section (1) of section 177 of the Electricity Act, 2003, the Central Electricity Authority hereby makes the following regulations further to amend the Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Regulations, 2011, namely:─ | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Now, therefore, in exercise of the powers conferred by clause (c) of section 73 read with sub-section (1) of section 177 of the Electricity Act, 2003, the Central Electricity Authority hereby makes the following regulations further to amend the Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Regulations, 2011, namely:─ | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 9 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0003 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 1. (1) These Regulations may be called the Central Electricity Authority (Safety Requirements for Construction, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 1. (1) These Regulations may be called the Central Electricity Authority (Safety Requirements for Construction, | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 9 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0004 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Operation and Maintenance of Electrical Plants and Electric Lines) (Amendment) Regulations, 2022. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 9 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0005 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 2. In the Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 2. In the Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 9 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0006 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | "(a) Formulation of written statement of policy in respect of safety and health of employees, duly signed by owner, shall be displayed at conspicuous places at the premises;" | NOT COVERED | NOT VERIFIED | NOT VERIFIED | "(a) Formulation of written statement of policy in respect of safety and health of employees, duly signed by owner, shall be displayed at conspicuous places at the premises;" | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0007 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | “(l) establishing methodology for internal and external audit of safety management system as per relevant | NOT COVERED | NOT VERIFIED | NOT VERIFIED | “(l) establishing methodology for internal and external audit of safety management system as per relevant | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0008 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | “(5) In case of any accident, the contractor shall immediately submit a state of the same to the Owner and the safety officer, containing the details of the accident, any injury or casualities, extent of property damage and remedial action taken to prevent recurrence.” | NOT COVERED | NOT VERIFIED | NOT VERIFIED | “(5) In case of any accident, the contractor shall immediately submit a state of the same to the Owner and the safety officer, containing the details of the accident, any injury or casualities, extent of property damage and remedial action taken to prevent recurrence.” | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0009 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | Provided that this provision shall not be applicable for the hydro power stations after commissioning of the project;” | Provided that this provision shall not be applicable for the hydro power stations after commissioning of the project;” | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0010 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | “(4) Owner shall ensure availability of adequate infrastructure for imparting effective audio-visual safety training at the plant or premises. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | “(4) Owner shall ensure availability of adequate infrastructure for imparting effective audio-visual safety training at the plant or premises. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0011 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (5) Safety precautions including imparting specialized training shall be ensured in critical activities like scaffolding, electrical works, hot works, working in confined spaces.” | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (5) Safety precautions including imparting specialized training shall be ensured in critical activities like scaffolding, electrical works, hot works, working in confined spaces.” | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0012 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | “12. Safety Audit. – (1) Safety audit of generating stations shall be periodically carried out every two years by an accreditated third party and the audit report shall be sent to the Authority. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | “12. Safety Audit. – (1) Safety audit of generating stations shall be periodically carried out every two years by an accreditated third party and the audit report shall be sent to the Authority. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0013 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (3) Safety checks shall be site specific and shall include the minimum safety checks as identified in Schedule IV annexed to these Regulations. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (3) Safety checks shall be site specific and shall include the minimum safety checks as identified in Schedule IV annexed to these Regulations. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 10 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0014 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 9. In Schedule I of the said regulations. – (a) In Paragraph (A) for sub-paragraph (12), the following sub-paragraph | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0015 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | “(12) Hazard identification and risk assessment including job safety analytical framework and safe working procedure;” | NOT COVERED | NOT VERIFIED | NOT VERIFIED | “(12) Hazard identification and risk assessment including job safety analytical framework and safe working procedure;” | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0016 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 10. In Schedule II of the said regulations, in Paragraph (A), after sub-paragraph (6), the following sub-paragraph shall | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0017 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 11. In Schedule III of the said regulations, in Paragraph (1), in sub-paragraph (A). ─ (a) for Clause (b), the following | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0018 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | “(c) Major fire in battery room or switchgear room or control room, as the case may be.” | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0019 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 12. After Schedule III of the said regulations, the following Schedule shall be inserted, namely:─ | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0020 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (iii) safety Committee shall be constituted under Plant Head or Deputy Plant Head; and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (iii) safety Committee shall be constituted under Plant Head or Deputy Plant Head; and | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0021 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Safety training and awareness programmes shall be conducted at least one in a year. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Safety training and awareness programmes shall be conducted at least one in a year. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 11 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0022 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Safety promotional activities such as Signages and posters awards for safety shall be done once in a year. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Safety promotional activities such as Signages and posters awards for safety shall be done once in a year. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0023 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Special safety measures shall be taken to check or avoid vulnerable accidents viz. fall from height, confined space entry, fall of materials, lack of supervision or knowledge, Bottom ash area. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Special safety measures shall be taken to check or avoid vulnerable accidents viz. fall from height, confined space entry, fall of materials, lack of supervision or knowledge, Bottom ash area. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0024 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | Hazard Identification Study shall be done for identifying hazards in order to prevent and reduce any adverse impact that could cause injury to personnel, damage or loss of property, environment and production, or become a liability. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0025 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | The provisions of Boilers Act, 1923 (as amended from time to time) shall be complied with including the inspection and certification of the boiler by the Boiler Inspector. | The provisions of Boilers Act, 1923 (as amended from time to time) shall be complied with including the inspection and certification of the boiler by the Boiler Inspector. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0026 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Safety checks or audits of generating stations shall be periodically carried out as per the regulation 12 above. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Safety checks or audits of generating stations shall be periodically carried out as per the regulation 12 above. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0027 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Maintenance Schedule | Fire Protection | SCHEDULE | (b) Fire hydrant pumps shall be tested weekly and fire hydrant jockey pumps shall be tested daily in each shift. | NOT COVERED | (b) Fire hydrant pumps shall be tested weekly and fire hydrant jockey pumps shall be tested daily in each shift | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0028 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Inspection | Fire Protection | INSPECTION | (c) Fire tenders shall be inspected daily in each shift and adequate manpower for each shift shall be employed. | (c) Fire tenders shall be inspected daily in each shift and adequate manpower for each shift shall be employed. | (c) Fire tenders shall be inspected daily in each shift and adequate manpower for each shift shall be employed | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0029 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Maintenance Schedule | Fire Protection | SCHEDULE | (d)All external fire detection shall be checked quarterly and all heat and smoke detectors annually tested. | NOT COVERED | (d)All external fire detection shall be checked quarterly and all heat and smoke detectors annually tested | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0030 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | Boiler shall be externally inspected every time after annual maintenance or during hydro test. | NOT COVERED | Boiler shall be externally inspected every time after annual maintenance or during hydro test | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 12 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0031 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | (ii) Safe shutdown of unit shall be done strictly as per Original Equipment Manufacturer’s Operation and Maintenance Manual. | (ii) Safe shutdown of unit shall be done strictly as per Original Equipment Manufacturer’s Operation and Maintenance Manual. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 13 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0032 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Main Turbine Vibration readings shall be maintained as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | Main Turbine Vibration readings shall be maintained as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 13 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0033 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Valves required for smooth operation shall be checked after every major shutdown as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | Valves required for smooth operation shall be checked after every major shutdown as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 13 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0034 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | (i) Hydro test of lube oil system shall be carried out as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | (i) Hydro test of lube oil system shall be carried out as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 13 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0035 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | (ii) Oil pipe line shall be inspected daily as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | (ii) Oil pipe line shall be inspected daily as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | (ii) Oil pipe line shall be inspected daily as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manua | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 13 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0036 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Lubrication and maintenance of turbine bearings and turning gear shall be done continuously as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | Lubrication and maintenance of turbine bearings and turning gear shall be done continuously as mentioned in the unit specific Original Equipment Manufacturer’s Operation and Maintenance Manual. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 13 | [भाग III—खण् ड 4] | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0037 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Electrostatic charges accumulated in the Bowser Lorry during movements or transportation has to be discharged by the drivers before unloading fuel oil, using a discharge rod, to prevent Explosions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 14 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0038 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | External inspection of the acid and alkali storage tanks shall be done once in six months. | External inspection of the acid and alkali storage tanks shall be done once in six months. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 14 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0039 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Cooling Tower concrete structure shall be inspected during annual maintenance by a designated Civil Engineer. | NOT COVERED | Cooling Tower concrete structure shall be inspected during annual maintenance by a designated Civil Engineer | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 14 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D02-C0040 | D02 | Central_Electricity_Authority_Safety_Requirements_for_Construction_Operation_and_Maintenance_of_Electrical_Plants_and_Electric_Lines_Amendment_Regulations_2022.pdf | Central Electricity Authority (Safety Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Amendment Regulations, 2022 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | remaining facilities. For Air Conditioners which involves circulation shall be provided with automatically closing damper to prevent the circulation of smoke in case of any fire.” | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 14 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0001 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | xi. Sequence of events/Description of fault (SOE with time stamp, Protection operated during fault) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xi. Sequence of events/Description of fault (SOE with time stamp, Protection operated during fault) | Transformer/reactor failure reporting | PDF p. 1 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0002 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xii. Details of Tests done after failure (What tests were conducted after the discovery of failure. If no tests were conducted, reasons for the same may be stated.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xii. Details of Tests done after failure (What tests were conducted after the discovery of failure. If no tests were conducted, reasons for the same may be stated.) | Transformer/reactor failure reporting | PDF p. 1 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0003 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | xiii. Observations (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment / material etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformer/reactor failure reporting | PDF p. 1 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0004 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xv. If OEM representative had inspected the equipment or visited the site after failure, their remarks, MoM etc. may be attached. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xv. If OEM representative had inspected the equipment or visited the site after failure, their remarks, MoM etc. may be attached. | Transformer/reactor failure reporting | PDF p. 2 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0005 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | xvii. (a) Details of previous maintenance (Activities carried out in previous maintenance including the tests conducted, periodicity of the maintenance activities) (b) Whether any abnormality observed in these tests. If yes, attach the test reports. (c) What steps were taken to address the abnormality? | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformer/reactor failure reporting | PDF p. 2 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0006 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxxiii. Surge arrestor: (a) Is SA provided for protection (b) Whether healthiness of SA is monitored (c) Whether reading of SA counter changed during failure | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxxiii. Surge arrestor: (a) Is SA provided for protection (b) Whether healthiness of SA is monitored (c) Whether reading of SA counter changed during failure | Transformer/reactor failure reporting | PDF p. 3 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0007 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | xxxvi. Type of Fire protection provided (Emulsifier system/ N2 Injection based fire protection system/ foam based protection etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | xxxvi. Type of Fire protection provided (Emulsifier system/ N2 Injection based fire protection system/ foam based protection etc.) | NOT COVERED | Transformer/reactor failure reporting | PDF p. 3 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0008 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxxvii. Weather conditions at the time of failure (clear sky/rainy/thunderstorm etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxxvii. Weather conditions at the time of failure (clear sky/rainy/thunderstorm etc.) | Transformer/reactor failure reporting | PDF p. 3 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0009 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | xxxviii. Storage condition of equipment at site before commissioning: (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/Nitrogen filled/ Oil filled | xxxviii. Storage condition of equipment at site before commissioning: (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/Nitrogen filled/ Oil filled | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformer/reactor failure reporting | PDF p. 3 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0010 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | Transformer | NOT VERIFIED | Testing | General | TESTING | xxxix. Whether short circuit test was carried out on this transformer or same design transformer or short circuit withstand | xxxix. Whether short circuit test was carried out on this transformer or same design transformer or short circuit withstand | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformer/reactor failure reporting | PDF p. 3 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0011 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | capability was verified on the basis of calculation? xl. Number of through faults the equipment was subjected to before failure | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | capability was verified on the basis of calculation? xl. Number of through faults the equipment was subjected to before failure | Transformer/reactor failure reporting | PDF p. 4 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D03-C0012 | D03 | format_failure_tf.pdf | Proforma for reporting of failure of Transformer/Reactor | NOT VERIFIED | MEDIUM | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xli. Attach the following: (a) Single Line Diagram of the substation (b) Photographs of the failed equipment (c) Disturbance Recorder/Even Logger Data (d) Reports of tests conducted after failure (e) Factory test results (f) Pre-commissioning test results (g) Protection schematic diagram | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xli. Attach the following: (a) Single Line Diagram of the substation (b) Photographs of the failed equipment (c) Disturbance Recorder/Even Logger Data (d) Reports of tests conducted after failure (e) Factory test results (f) Pre-commissioning test results (g) Protection schematic diagram | Transformer/reactor failure reporting | PDF p. 4 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0001 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Analysis of cause of failure & maintaining history card for Distribution Transformer | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Analysis of cause of failure & maintaining history card for Distribution Transformer | Distribution transformers | PDF p. 4 | CONTENTS | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0002 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | General | FAILURE_ANALYSIS | faults in Distribution Transformer can cause extensive damage which not only interrupts power | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | faults in Distribution Transformer can cause extensive damage which not only interrupts power | Distribution transformers | PDF p. 8 | STATE | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0003 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | supply to the consumers but also results in huge revenue losses to the discoms. The failure rates | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | supply to the consumers but also results in huge revenue losses to the discoms. The failure rates | Distribution transformers | PDF p. 8 | STATE | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0004 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | losses of Transformers at various levels. In case we assume an Avg high 10 % DT failure rate in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | losses of Transformers at various levels. In case we assume an Avg high 10 % DT failure rate in | Distribution transformers | PDF p. 9 | 6 Lakh MVA (March 2021). As Distribution Transformer is an integral part of the Electricity | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0005 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | the country, the number of DT failure would be around about 1.3 million/year. It is generally | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | the country, the number of DT failure would be around about 1.3 million/year. It is generally | Distribution transformers | PDF p. 9 | 6 Lakh MVA (March 2021). As Distribution Transformer is an integral part of the Electricity | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0006 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | utilities on repair/ replacement of DTs. This is a huge financial burden on the utilities and it also | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 9 | 6 Lakh MVA (March 2021). As Distribution Transformer is an integral part of the Electricity | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0007 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | allowable losses at rated voltage and rated frequency permitted at 75°C for Distribution | NOT COVERED | NOT VERIFIED | 75°C | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 9 | 6 Lakh MVA (March 2021). As Distribution Transformer is an integral part of the Electricity | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0008 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | in the Schedule, which do not conform to the specified standards (i.e. IS 1180 Part-1, 2014) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0009 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Maintenance Schedule | Inspection | SCHEDULE | Regular inspections and periodic maintenance of Distribution transformers help to identify | NOT COVERED | Regular inspections and periodic maintenance of Distribution transformers help to identify | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0010 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Failure / Failure Analysis | Fire Protection | FAILURE_ANALYSIS | misaligned parts to minimize system failures and fire hazards. It is paramount that the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | misaligned parts to minimize system failures and fire hazards. It is paramount that the | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0011 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | maintenance crew pays attention to applicable Standards (Like ISO 9001-2015/ISO- 12000 ) to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0012 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | maintain a safe working environment for both the equipment and the maintenance staff. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0013 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Maintenance Schedule | SCHEDULE | The proper exercise of the maintenance schedule should also be adopted by Discoms as it will | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0014 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | lead to extension of life of Distribution Transformers, reduction in failure rate, enhanced | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | lead to extension of life of Distribution Transformers, reduction in failure rate, enhanced | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0015 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | importance to this maintenance & repair aspects including training of his O & M staff are able to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0016 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | The document covers the best practices for operation and maintenance of Distribution | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0017 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | field engineers for reducing the DT failure rates, reducing the downtime of the system, revenue | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | field engineers for reducing the DT failure rates, reducing the downtime of the system, revenue | Distribution transformers | PDF p. 10 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0018 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Transformer core for the power frequency application is made of highly permeable material. High | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 12 | CHAPTER-1 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0019 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 1. Indian Standard Code 1180- Part1: Outdoor type oil immersed distribution transformers up to 2500 KVA, 33 KV- specifications. | NOT COVERED | NOT VERIFIED | 2500 KVA; 33 KV | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 12 | CHAPTER-1 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0020 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance | General | MAINTENANCE | total losses when a transformer is heavily loaded. The utility should maintain the transformer | total losses when a transformer is heavily loaded. The utility should maintain the transformer | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 15 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0021 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | loss data as provided by OEM during supply & repairing stage (after repair). The same should be | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 15 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0022 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | assembly is immersed in a tank containing transformer oil. The transformer oil thus has dual role. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 17 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0023 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | It is an insulator and also a coolant. The porous insulation around the conductor helps the oil reach | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 17 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0024 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | windings. Annular Bakelite cylinders serve this purpose. Oil ducts are also used as part of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 17 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0025 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | insulation between windings. The oil used in the transformer tank should be free from moisture | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 17 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0026 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | The LV bushing and HV bushing stems shall be provided with suitable terminal connectors so as to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 18 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0027 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | brought out and connected to local grounding terminal by an Earthing strip as per IS 1180. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0028 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (p) Oil filling hole having M30 thread with plug and drain valve on the conservator | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0029 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | in the event of failure of locking resulting in the nuts working loose and falling off, the bolt will | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | in the event of failure of locking resulting in the nuts working loose and falling off, the bolt will | Distribution transformers | PDF p. 20 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0030 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | designed with safety factors suitable for jerk loading then the lugs tends to break. The manual | NOT COVERED | NOT VERIFIED | NOT VERIFIED | designed with safety factors suitable for jerk loading then the lugs tends to break. The manual | NOT COVERED | Distribution transformers | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0031 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | As per lifting devices standards the safety factor of 5 ensured in design of lifting lugs and with | NOT COVERED | NOT VERIFIED | NOT VERIFIED | As per lifting devices standards the safety factor of 5 ensured in design of lifting lugs and with | NOT COVERED | Distribution transformers | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0032 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | in power delivery and the integrity of the power system network as a whole. The failure of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | in power delivery and the integrity of the power system network as a whole. The failure of | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0033 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Distribution Transformers leads to failure of Distribution system and subsequent outage which | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Distribution Transformers leads to failure of Distribution system and subsequent outage which | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0034 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | leads to financial loss in repair and replacement, loss of revenue and reduces quality and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0035 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Major Reasons Minor Reasons 1. Insulation Failure 1. Oil Sample not Satisfactory 2. Damage to HT Coil 2. Lead connections cut of 3. Damage to LT Coil 3. Worn-out Bushing rods 4. Damage to Core & Laminations 4. Broken Bushings 5. Failure to Tap Switch & Tap 5. Gasket Leakage Arrangement 6. Welding Leakage 7. Leakage through Valves 8. Broken gauge glass 9. Broken vent diaphragm 10. Worn-out Breather | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Major Reasons Minor Reasons 1. Insulation Failure 1. Oil Sample not Satisfactory 2. Damage to HT Coil 2. Lead connections cut of 3. Damage to LT Coil 3. Worn-out Bushing rods 4. Damage to Core & Laminations 4. Broken Bushings 5. Failure to Tap Switch & Tap 5. Gasket Leakage Arrangement 6. Welding Leakage 7. Leakage through Valves 8. Broken gauge glass 9. Broken vent diaphragm 10. Worn-out Breather | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0036 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Transformers have operating limits beyond which transformer failure can occur like overloading | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Transformers have operating limits beyond which transformer failure can occur like overloading | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0037 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | transformer and it may cause intolerable interruption of service to customers and may also cause | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0038 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | loss to public property & life due to accidents. Since the lead time for repair and replacement of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0039 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance | General | MAINTENANCE | transformers is usually quite high, hence proper quality, timely maintenance, and adhering to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0040 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Maintenance Schedule | FAILURE_ANALYSIS | timely checks and maintenance schedule should be followed to avoid the failure of DTs. In case | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | timely checks and maintenance schedule should be followed to avoid the failure of DTs. In case | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0041 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | of failure of Distribution Transformers, the faulty transformer is to be replaced by a health | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of failure of Distribution Transformers, the faulty transformer is to be replaced by a health | Distribution transformers | PDF p. 22 | CHAPTER-2 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0042 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE |  External conditions (Moisture entry, lightning, loose conservator cap, pilferage of oil) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 24 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0043 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | foreign objects left in the tank. These causes of transformer failure can be further categorized | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | foreign objects left in the tank. These causes of transformer failure can be further categorized | Distribution transformers | PDF p. 25 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0044 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Following are the leaks in the assembly process resulting in transformer failure: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Following are the leaks in the assembly process resulting in transformer failure: | Distribution transformers | PDF p. 25 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0045 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | oil can leak. Dielectric strength will be reduced and breakdown will occur in the tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | oil can leak. Dielectric strength will be reduced and breakdown will occur in the tank. | Distribution transformers | PDF p. 25 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0046 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE |  Assembly of low voltage busbar and bushing - Bolt of busbar and bushing can be loose. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 26 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0047 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Following are the leaks in the cleaning process resulting in transformer failure: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Following are the leaks in the cleaning process resulting in transformer failure: | Distribution transformers | PDF p. 26 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0048 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | Utility Side Defects include leaks in the Operation and Maintenance process and External factors | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Utility Side Defects include leaks in the Operation and Maintenance process and External factors | Distribution transformers | PDF p. 27 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0049 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | causing DT failure. In following section, leaks in the Operation and Maintenance process and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | causing DT failure. In following section, leaks in the Operation and Maintenance process and | Distribution transformers | PDF p. 27 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0050 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS |  Line Surge - Failure caused by switching surges, voltage spikes, line faults/flashovers, and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED |  Line Surge - Failure caused by switching surges, voltage spikes, line faults/flashovers, and | Distribution transformers | PDF p. 27 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0051 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS |  Oil Contamination- resulting in slugging, carbon tracking and humidity in the oil can often result in transformer failure. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED |  Oil Contamination- resulting in slugging, carbon tracking and humidity in the oil can often result in transformer failure. | Distribution transformers | PDF p. 28 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0052 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS |  Water Ingression- Water ingression through improper sealing / damaged tank body causes loss of dielectric strength resulting to insulation failure. Mostly, the lower most HV coil gets affected due to water settling at the bottom of the tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED |  Water Ingression- Water ingression through improper sealing / damaged tank body causes loss of dielectric strength resulting to insulation failure. Mostly, the lower most HV coil gets affected due to water settling at the bottom of the tank. | Distribution transformers | PDF p. 28 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0053 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS |  Improper/inadequate Maintenance- Inadequate or improper maintenance and operation is a major cause of transformer failures. It includes disconnected or improperly set controls, loss of coolant, accumulation of dirt and oil, and corrosion. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED |  Improper/inadequate Maintenance- Inadequate or improper maintenance and operation is a major cause of transformer failures. It includes disconnected or improperly set controls, loss of coolant, accumulation of dirt and oil, and corrosion. | Distribution transformers | PDF p. 28 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0054 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer, Fire Protection | Distribution Transformer | Failure / Failure Analysis | Fire Protection | FAILURE_ANALYSIS |  External Factors- Several external factors like floods, fire explosions, lightening and moisture could also cause the failure of the distribution transformer. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE |  External Factors- Several external factors like floods, fire explosions, lightening and moisture could also cause the failure of the distribution transformer. | Distribution transformers | PDF p. 28 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0055 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Earthing | FAILURE_ANALYSIS |  Poor Earthing- Improper earthing is one of the main reason casing unbalanced voltages, floating neutral and causing DT failure. Some poor examples of earthing are given below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED |  Poor Earthing- Improper earthing is one of the main reason casing unbalanced voltages, floating neutral and causing DT failure. Some poor examples of earthing are given below: | Distribution transformers | PDF p. 28 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0056 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | Most of the DTs have very high earthing resistance value. Some sample photograph is follow as: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 29 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0057 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Improper oil level in the DTs due to poor maintenance, leakage and theft of oil as it causes temperature rise, hotspot leading to DT failure especially in rural areas. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Improper oil level in the DTs due to poor maintenance, leakage and theft of oil as it causes temperature rise, hotspot leading to DT failure especially in rural areas. | Distribution transformers | PDF p. 29 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0058 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | No use of MCB on LT side of DTs and using improper size of the fuses (for ease by maintenance staff) is another major reason for failure of DTs and affecting the safety of DTs and public life. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | No use of MCB on LT side of DTs and using improper size of the fuses (for ease by maintenance staff) is another major reason for failure of DTs and affecting the safety of DTs and public life. | NOT COVERED | Distribution transformers | PDF p. 29 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0059 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Poor maintenance of breathers/ Silica Gel or no usage of breather lead to lowering the moisture content of transformer oil and thereby causing the failure of DTs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Poor maintenance of breathers/ Silica Gel or no usage of breather lead to lowering the moisture content of transformer oil and thereby causing the failure of DTs. | Distribution transformers | PDF p. 30 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0060 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | to bear excessive pressure & weight of Cable and may lead to failure of Cable end termination. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | to bear excessive pressure & weight of Cable and may lead to failure of Cable end termination. | Distribution transformers | PDF p. 31 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0061 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | As can be seen from the above list both manufacturing and operation & maintenance related | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 32 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0062 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | factors cause failure of DTs. It is essential to improve the processes at manufacturing end, and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | factors cause failure of DTs. It is essential to improve the processes at manufacturing end, and | Distribution transformers | PDF p. 32 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0063 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | An abstract of failure due to operational and manufacturing defects is described in the table below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | An abstract of failure due to operational and manufacturing defects is described in the table below: | Distribution transformers | PDF p. 32 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0064 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Besides above, the mismanagement in procurement process, lack of skilled technician/ workers non adherence to BIS (ISI marking) mandates and guidelines, absence of root cause analysis for untimely failure, absence of asset management philosophy and aging of assets are also contributing to the failure of DTs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Besides above, the mismanagement in procurement process, lack of skilled technician/ workers non adherence to BIS (ISI marking) mandates and guidelines, absence of root cause analysis for untimely failure, absence of asset management philosophy and aging of assets are also contributing to the failure of DTs. | Distribution transformers | PDF p. 33 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0065 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance | General | MAINTENANCE | maintenance and repairing of transformers at the utility end. Some of the challenges faced by | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0066 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Installation | INSTALLATION | the industry are lack of mandatory guidelines for installation operation and maintenance of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0067 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | transformers like bad earthing practices, usage of inferior material in transformer manufacturing, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0068 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | overloading of transformers, tampering/bypassing protection equipment, theft of material/oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0069 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | drastically affects the performance of the system and DT failure rate. It is observed that the failure | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | drastically affects the performance of the system and DT failure rate. It is observed that the failure | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0070 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | it is observed that this failure rate is less than 1 % in developed countries compared to around 10 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | it is observed that this failure rate is less than 1 % in developed countries compared to around 10 | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0071 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | % in India in some utilities. High failure rates of system equipment leads to financial burden on | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | % in India in some utilities. High failure rates of system equipment leads to financial burden on | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0072 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | the utilities in terms of repair and replacement cost and indirect revenue loss due to the non- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0073 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | availability of the system. A developing country like India needs to have lower failure rates for the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | availability of the system. A developing country like India needs to have lower failure rates for the | Distribution transformers | PDF p. 34 | CHAPTER-3 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0074 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | to government utilities to keep check on failure of DTs. However, further modifications are | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | to government utilities to keep check on failure of DTs. However, further modifications are | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0075 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | ii. Use of tap-changers in DTs may be minimized to eliminate probability of failure due to tap- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ii. Use of tap-changers in DTs may be minimized to eliminate probability of failure due to tap- | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0076 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | v. Lug / clamp connection in between riser & bushing minimises the probability of internal open | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0077 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | B. Analysis of cause of failure & maintaining history card for Distribution Transformer | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | B. Analysis of cause of failure & maintaining history card for Distribution Transformer | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0078 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Distribution transformer may fail due to various reasons. The root cause of failure may be lacunae | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Distribution transformer may fail due to various reasons. The root cause of failure may be lacunae | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0079 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | in manufacturing practices or inappropriate operation and maintenance practices. Analysis of causes | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0080 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | of failure would help in taking corrective measures and reducing costs associated with | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of failure would help in taking corrective measures and reducing costs associated with | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0081 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | repairs/replacement. For the purpose of analysis, it is necessary to identify nature of failure and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | repairs/replacement. For the purpose of analysis, it is necessary to identify nature of failure and | Distribution transformers | PDF p. 35 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0082 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | the stray losses in the tank and metal support structures are the principle sources of heat that cause | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0083 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | the oil and winding temperature rise. Various investigators have not agreed on life-duration at any | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0084 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | transformer cause thermal stress in the active part. This leads to ageing and decomposition of both | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0085 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | oil and cellulose which liberate gases within the transformer. The amount and type of gases formed | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0086 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | and dissolved into the oil can be determined with the help of Dissolved Gas Analysis (DGA). Similar | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0087 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | to a blood test or scanner examination of human body, Dissolved Gas Analysis can give an early | to a blood test or scanner examination of human body, Dissolved Gas Analysis can give an early | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0088 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | or passing faults, inadequate protection, public interference, poor maintenance of LT and 11 kV lines | NOT COVERED | NOT VERIFIED | 11 kV | NOT COVERED | or passing faults, inadequate protection, public interference, poor maintenance of LT and 11 kV lines | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0089 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE |  The routine maintenance of LT and 11 kV lines and protective equipment’s associated with these | NOT COVERED | NOT VERIFIED | 11 kV | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 36 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0090 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | overloading or unbalance load deteriorate the insulating materials; ultimately leading to failure.  | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | overloading or unbalance load deteriorate the insulating materials; ultimately leading to failure.  | Distribution transformers | PDF p. 37 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0091 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Overloading/unbalanced loading due to power theft by hooking or poor maintenance is one of the major causes of transformer failure. It may be assumed that stealing of power by some of the consumers would have been done by hooking the approachable bottom most conductor i.e. B phase of the system. This resulted into severe over loading. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Overloading/unbalanced loading due to power theft by hooking or poor maintenance is one of the major causes of transformer failure. It may be assumed that stealing of power by some of the consumers would have been done by hooking the approachable bottom most conductor i.e. B phase of the system. This resulted into severe over loading. | Distribution transformers | PDF p. 41 | CASE STUDIES OF TRANSFORMER FAILURE WITH ANALYSIS | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0092 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | In A, charred paper insulation present in the oil can be seen at the bottom of the jar. As the conductor is made of Aluminum, it comes out in the melted form and solidifies, which can be clearly seen on the top of the winding. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 42 | B | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0093 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS |  This significant failure rate of distribution transformer in the country can be curbed to some extent by | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED |  This significant failure rate of distribution transformer in the country can be curbed to some extent by | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0094 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | lightning arresters. The primary side fuse is mounted inside the primary bushing and is in series with the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0095 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | It was mentioned that though rate of failure of DTs has decreased in the last few years, it is still very high. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | It was mentioned that though rate of failure of DTs has decreased in the last few years, it is still very high. | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0096 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | This high rate of failure may be due to either poor quality of product or poor operational practices adopted | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | This high rate of failure may be due to either poor quality of product or poor operational practices adopted | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0097 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | One of the most important reasons for poor operational practices is poor culture of asset maintenance, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0098 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | as some entities don’t undertake any preventive maintenance. As a result, maintenance occurs only after | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0099 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | failure of equipment. It has been noticed that culture of maintenance of the assets is better among private | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | failure of equipment. It has been noticed that culture of maintenance of the assets is better among private | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0100 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Second reason for poor maintenance is non-availability of money for maintenance. Several utilities in the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0101 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | country are facing acute cash flow problems. This results in avoidance of preventive maintenance costs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0102 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Finally, the failure rate is generally higher during the warranty period of the transformer as compared to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Finally, the failure rate is generally higher during the warranty period of the transformer as compared to | Distribution transformers | PDF p. 44 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0103 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance | General | MAINTENANCE | manufacturers state that utility staff ignores maintenance of the transformer under warranty period. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 45 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0104 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Further, without ascertaining reason for failure and thereby responsibility of failure, manufacturer is | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Further, without ascertaining reason for failure and thereby responsibility of failure, manufacturer is | Distribution transformers | PDF p. 45 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0105 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | maintenance services for the warranty period in some sample areas so that they may set an example for | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 45 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0106 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | proper maintenance of DTs and simultaneously the maintenance staff of utilities may be trained and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 45 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0107 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | accustomed for following maintenance practices. The costs associated with sample annual maintenance | NOT COVERED | The costs associated with sample annual maintenance | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 45 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0108 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Utility should go for losses testing at store for the same percentage of the random sample selected from the lot size. | Utility should go for losses testing at store for the same percentage of the random sample selected from the lot size. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 47 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0109 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance | General | MAINTENANCE | Transformer is the heart of any power system. Hence preventive maintenance is always cost | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 49 | CHAPTER-4 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0110 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | effective and saves time. Any failure of the transformer affects the functioning of the power | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | effective and saves time. Any failure of the transformer affects the functioning of the power | Distribution transformers | PDF p. 49 | CHAPTER-4 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0111 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | system and reliability of supply. Following are some operational and maintenance practices that | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 49 | CHAPTER-4 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0112 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | below may already be part of the maintenance manual of distribution utilities. Comprehensive | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 49 | CHAPTER-4 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0113 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | – Oil BDV and acidity checking at regular intervals. If acidity is between 0.5 to 1mg KOH, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 50 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0114 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE |  Periodic checking of any loose connections of the terminations of HV and LV side. | NOT COVERED |  Periodic checking of any loose connections of the terminations of HV and LV side | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 50 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0115 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | transformers, the active repair approach may be considered, to achieve technical loss | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 50 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0116 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | reduction, enhance KVA capacity and reliability Under the active repair core is kept | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 50 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0117 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | more than 20% then need to investigate. 12 Electrical Oil BDV Yearly a) BDV of transformer oil | NOT COVERED | 12 Electrical Oil BDV Yearly a) BDV of transformer oil | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 52 | HT-LT. | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0118 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Maintenance Schedule | SCHEDULE | 5. Maintenance Schedule for DTs of capacity less than 1000 KVA (As per IS 10028 Part-III 1981): | NOT COVERED | NOT VERIFIED | 1000 KVA | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 55 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0119 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 4. It should be placed in horizontal position in such a way that there is a head of oil on the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 61 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0120 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 6. Vessel or drum for handling of oil should always be clean, free from dust, dirt | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 61 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0121 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 1. Colour:- The colour of oil darkens with the age. Very dark colour may suggest excessive | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 62 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0122 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | 2. Clarity:- Cloudiness if it appears while cooling of oil sample, is indication of presence of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 2. Clarity:- Cloudiness if it appears while cooling of oil sample, is indication of presence of | NOT COVERED | Distribution transformers | PDF p. 62 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0123 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | moisture which can be confirmed by crackle test. If cloudiness is present when oil | moisture which can be confirmed by crackle test. If cloudiness is present when oil | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 62 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0124 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | sample is warm and oil does not become clear even after heating, it is an indication | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 62 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0125 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | The DTs are required to be tested at manufacturer end, thereafter routine test in the field and after carrying out the maintenance/ repair work as per IS 1180 Part-1, IS 2026 Part-1 to 5. | The DTs are required to be tested at manufacturer end, thereafter routine test in the field and after carrying out the maintenance/ repair work as per IS 1180 Part-1, IS 2026 Part-1 to 5. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 63 | CHAPTER-5 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0126 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE |  No load current and losses at rated frequency, rated voltage and at 90% & 110% voltage. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 63 | CHAPTER-5 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0127 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE |  BDV and moisture content of oil in transformer (For mineral oil: IS 335 (2018), Ester oil: IEC 60247 & IEC61099) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 63 | CHAPTER-5 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0128 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | plates after the excess pressure has been released, shall not exceed the figures for vacuum | plates after the excess pressure has been released, shall not exceed the figures for vacuum | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 63 | CHAPTER-5 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0129 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | before reaching the test pressure as specified in the above clause. The operating pressure | before reaching the test pressure as specified in the above clause. The operating pressure | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 63 | CHAPTER-5 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0130 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Transformer Oil | TESTING | - Oil samples (before and after short-circuit and temperatures rise test) for each tested transformer | - Oil samples (before and after short-circuit and temperatures rise test) for each tested transformer | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 64 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0131 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | voltage side. f) Tests on operation of standby earth fault relay on low-voltage, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | voltage side. f) Tests on operation of standby earth fault relay on low-voltage, | Distribution transformers | PDF p. 64 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0132 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Commissioning | Transformer Oil | COMMISSIONING | side. g) Tests on overcurrent relay on high- voltage side (when current transformers are not in transformer bushings). h) Voltage compensation. 4) Ratio tests a) With 415 V applied on high-voltage side, measure the voltage between all phases on the low-voltage side for every tap position. b) To check phasing, measure volts: A to a, b and c B to a, b and c C to a, b and c Where A, B and C are the terminals of three phases on high- voltage side and a, b and c are the corresponding terminals on low-voltage side. c) Magnetic balance test. 5) Tripping tests a) High voltage. b) Low voltage. c) Inter-tripping tests. d) Winding temperature trips. 6) Calibrate earthing resistance --- 7) Buchholtz relays a) Tests for angle, air injection, etc. b) Check that there is no air in protector before commissioning. c) When energizing transformer, close in on ‘Trip’, etc. d) Check for stability when oil pumps are started: 1) at ambient temperature, 2) At a winding temperature of 80°C or above. 8) Alarm circuits a) Buchholtz relay | side. g) Tests on overcurrent relay on high- voltage side (when current transformers are not in transformer bushings). h) Voltage compensation. 4) Ratio tests a) With 415 V applied on high-voltage side, measure the voltage between all phases on the low-voltage side for every tap position. b) To check phasing, measure volts: A to a, b and c B to a, b and c C to a, b and c Where A, B and C are the terminals of three phases on high- voltage side and a, b and c are the corresponding terminals on low-voltage side. c) Magnetic balance test. 5) Tripping tests a) High voltage. b) Low voltage. c) Inter-tripping tests. d) Winding temperature trips. 6) Calibrate earthing resistance --- 7) Buchholtz relays a) Tests for angle, air injection, etc. b) Check that there is no air in protector before commissioning. c) When energizing transformer, close in on ‘Trip’, etc. d) Check for stability when oil pumps are started: 1) at ambient temperature, 2) At a winding temperature of 80°C or above. 8) Alarm circuits a) Buchholtz relay | NOT VERIFIED | 415 V; 80°C | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 64 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0133 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | b) Oil and winding temperature thermo- meter. c) Cooling gear failure. 9) Fans and pumps a) Check that the oil valves are open in cooling circuit. b) Check the rotation of pumps, automatic starting overload | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | b) Oil and winding temperature thermo- meter. c) Cooling gear failure. 9) Fans and pumps a) Check that the oil valves are open in cooling circuit. b) Check the rotation of pumps, automatic starting overload | Distribution transformers | PDF p. 65 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0134 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | compensated voltages from the other transformer. 15) See that neutral earthing switches are closed before making alive. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 65 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0135 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 18) If necessary, arrange temporary protection for soaking and switching in, for example unrestricted earth fault, if soaking from low voltage side with 113 V and 213 V open | NOT COVERED | NOT VERIFIED | 113 V; 213 V | NOT COVERED | 18) If necessary, arrange temporary protection for soaking and switching in, for example unrestricted earth fault, if soaking from low voltage side with 113 V and 213 V open | Distribution transformers | PDF p. 65 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0136 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 20) Load tests a) Voltmeter, ammeters, etc., on both high and low voltage sides. b) Overcurrent. c) No spill in high voltage star point. d) No creeping of contacts on both high and low voltage earth fault relays e) Voltages on relays. f) Directional elements - low voltage, directional overcurrent and the earth- fault relays (if fitted). g) Voltage compensation. 21) Tap changing test on load over full range of taps | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 20) Load tests a) Voltmeter, ammeters, etc., on both high and low voltage sides. b) Overcurrent. c) No spill in high voltage star point. d) No creeping of contacts on both high and low voltage earth fault relays e) Voltages on relays. f) Directional elements - low voltage, directional overcurrent and the earth- fault relays (if fitted). g) Voltage compensation. 21) Tap changing test on load over full range of taps | Distribution transformers | PDF p. 66 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0137 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | moisture and dust. This subsequently deteriorates the oil quality and affects insulation of DT which further leads to failure of DT. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | moisture and dust. This subsequently deteriorates the oil quality and affects insulation of DT which further leads to failure of DT. | Distribution transformers | PDF p. 73 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0138 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | power factor, Oil temperature of the transformer, temperature of the internal part, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 75 | CHAPTER-6 | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0139 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | monitored regularly to prevent any potential faults. Failure of the DTs easily costs several Crore | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | monitored regularly to prevent any potential faults. Failure of the DTs easily costs several Crore | Distribution transformers | PDF p. 76 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0140 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | rupees for repair or replacement, and results in revenue losses and loss of service to customers | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 76 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0141 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Transformer burning / damage and Oil loss etc. Since these transformers are installed in Utilities in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 76 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0142 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | these DTs, mainly due to day to day operation and maintenance of AMR system of DT meters, mis- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0143 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | alignment or failure of modem, communication failures, non-restoration of DT metering system by | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | alignment or failure of modem, communication failures, non-restoration of DT metering system by | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0144 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Further, as the meter keeps record of different system parameters, transformer failure analysis | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Further, as the meter keeps record of different system parameters, transformer failure analysis | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0145 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | can be done; the cause of the transformer failure can be easily identified and analyzed before | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | can be done; the cause of the transformer failure can be easily identified and analyzed before | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0146 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | maintenance of AMR/AMI system of DT meters installed in urban areas may be outsourced, since | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0147 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Utility staff is mainly engaged in restoration of power supply and their maintenance. The scope | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0148 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Troubleshooting | General | TROUBLESHOOTING | and unbalanced loading of Distribution transformers for taking further corrective actions and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | and unbalanced loading of Distribution transformers for taking further corrective actions and | Distribution transformers | PDF p. 77 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0149 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | implemented two IT based Application modules (i.e. Asset and Maintenance management system), | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 78 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0150 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | The Maintenance Management System helps utility in better planning and co-ordination of various | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 78 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0151 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | maintenance activities; reduce breakdowns through preventive and predictive maintenance, to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | maintenance activities; reduce breakdowns through preventive and predictive maintenance, to | Distribution transformers | PDF p. 78 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0152 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | maintain maintenance history, to review and control maintenance costs and providing a feedback | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 78 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0153 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | • Coupled with Trouble call management system, it will keep track on maintenance work on each | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 78 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0154 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | meters, other critical parameters of distribution transformers like oil temperature, oil humidity, oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 79 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0155 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | center via some communication technology. The parameters like oil temperature, oil humidity, oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 79 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0156 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Condition Monitoring | General | CONDITION_MONITORING | existing meters to transmit these data to a Centralized Condition Monitoring Software. DTMU | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 79 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0157 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | In order to solve the oil leakages and oil theft problems with Distribution Transformers (DTs),, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 80 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0158 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The DIDO in smart meters, may be used for the oil level and temperature monitoring of the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 80 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0159 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | distribution transformers. Special sensors may be used for monitoring of oil level low and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 80 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0160 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | temperature rise of the oil which can be DIDO port of smart meters and may be communicated | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 80 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0161 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | dome shaped structure floats to a calibrated level when it is immersed in the oil and rests on a | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 80 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0162 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | OTI (Oil Temperature Indicator): It may be used for real-time monitoring of the temperature of oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 81 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0163 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | inside the DT. It may have a user configurable marking to set the permissible limits for the oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 81 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0164 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (shown in fig. 3). It may digitally signal through the cable attached to it, in case the oil- temperature | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 81 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0165 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | When someone tries to steal oil from the transformer or there is any oil-leakage, the oil-level in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 82 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0166 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | send an alert SMS to the concerned zonal staff about the oil- theft in DT, with the details of its | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 82 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0167 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | location (pre-fed at HES via Geographical Information System (GIS), as per the installed serial | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 82 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0168 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | can trigger based on the oil temperature rise. This low cost solution can help in mitigating the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 83 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0169 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | degrees. With alert message or email, the maintenance crew can be mobilized to check the | degrees. With alert message or email, the maintenance crew can be mobilized to check the | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 83 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D04-C0170 | D04 | Guidelines_for_OM_of_DTs.pdf | Guidelines for Operation & Maintenance of Distribution Transformers | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Design / Technical Reference | General | DESIGN_REFERENCE |  EASA guidelines for repair of power & distribution transformers (EASA-AR 200). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Distribution transformers | PDF p. 86 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0001 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Short title and commencement.- (1) These regulations niay be called the Centra·1 Electricity Authority.(Safety · Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Regulations, 2011. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Short title and commencement.- (1) These regulations niay be called the Centra·1 Electricity Authority.(Safety · Requirements for Construction, Operation and Maintenance of Electrical Plants and Electric Lines) Regulations, 2011. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 18 | THE GAZEITE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0002 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | (b) "contractor" means a person or an agency who undertakes to produce a given result, not merely su.pply of goods. or articles of manufacture but including civil works or erection of equipment or testing and commissioning of equipment or operation and maintenance of equipment and includes a sub-contractor; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 18 | THE GAZEITE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0003 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 4. Safety provisions relating to Owner.- (1) The Owner shall make safety an integral part of work processes to ensure safety for employees including employees of contractor, sub-contractor as well as visitors. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 4. Safety provisions relating to Owner.- (1) The Owner shall make safety an integral part of work processes to ensure safety for employees including employees of contractor, sub-contractor as well as visitors. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0004 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (4) The Owner shall set up a sound and scientific safety management system which shall include,- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (4) The Owner shall set up a sound and scientific safety management system which shall include,- | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0005 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (a) formulation of a written statement of policy in respect of safety and health of employees; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (a) formulation of a written statement of policy in respect of safety and health of employees; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0006 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (b) defining and documenting responsibilities for all levels of functionaries to carry out safety related activities including responsibilities of the contractors; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (b) defining and documenting responsibilities for all levels of functionaries to carry out safety related activities including responsibilities of the contractors; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0007 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (c) preparing detailed safety manual complying with the statutory requirements and manufacturers' recommendations; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (c) preparing detailed safety manual complying with the statutory requirements and manufacturers' recommendations; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0008 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (e) providing adequate human, physical and financial resources to implement the safety management system; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (e) providing adequate human, physical and financial resources to implement the safety management system; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 19 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0009 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (f) providing safe working environment and evolving framework for occupational safety and health; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (f) providing safe working environment and evolving framework for occupational safety and health; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0010 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (h) providing adequate training to all employees to keep them aware of safety related issues; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (h) providing adequate training to all employees to keep them aware of safety related issues; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0011 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | G) establishing system for proper communication, documentation and record management in relation to occupational safety and health; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | G) establishing system for proper communication, documentation and record management in relation to occupational safety and health; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0012 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (I) establishing methodology for internal and external audit of safety management system; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (I) establishing methodology for internal and external audit of safety management system; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0013 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (m) establishing system for periodic monitoring and review of the safety system by the management; | NOT COVERED | (m) establishing system for periodic monitoring and review of the safety system by the management; | NOT VERIFIED | (m) establishing system for periodic monitoring and review of the safety system by the management; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0014 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Installation | SAFETY | 5. Safety manual.- Safety manual referred to in clause (c) of sub-regulation (4) of regulation 4 shall be site specific but for similar installations, common safety manual may be prepared and made applicable to such installations and these safety manuals shall cover the matters identified in Schedule-I and Schedule-II annexed to these regulations. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 5. Safety manual.- Safety manual referred to in clause (c) of sub-regulation (4) of regulation 4 shall be site specific but for similar installations, common safety manual may be prepared and made applicable to such installations and these safety manuals shall cover the matters identified in Schedule-I and Schedule-II annexed to these regulations. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0015 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 6. Safety officer and safety committee.- (1) (a) The Owner shall appoint one qualified safety officer where the · number of employees, including contract workers, exceeds •five hundred and where the number of employees is less than five hundred, a suitable officer shall be designated as safety officer: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 6. Safety officer and safety committee.- (1) (a) The Owner shall appoint one qualified safety officer where the · number of employees, including contract workers, exceeds •five hundred and where the number of employees is less than five hundred, a suitable officer shall be designated as safety officer: | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0016 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Provided that where number of employees exceeds one thousand. one more safety officer shall be appointed for every additional one thousand employees. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Provided that where number of employees exceeds one thousand. one more safety officer shall be appointed for every additional one thousand employees. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0017 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (b) A person shall not be eligible for appointment as a safety officer unless he is qualified,- - | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (b) A person shall not be eligible for appointment as a safety officer unless he is qualified,- - | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 20 | 1HE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0018 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (c) (i) Where number of safety officers appointed exceeds one, one of them shall be designated as chief safety officer who shall have higher ranking than the. others and he shall be in-charge of the safety functions and the other safety officers shall work under his control. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (c) (i) Where number of safety officers appointed exceeds one, one of them shall be designated as chief safety officer who shall have higher ranking than the. others and he shall be in-charge of the safety functions and the other safety officers shall work under his control. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0019 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (ii) The chief safety officer or the safety officer, as the case may be, shall be given the status of a senior executive and he shall work directly under the control of the Chief Executive. ' | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (ii) The chief safety officer or the safety officer, as the case may be, shall be given the status of a senior executive and he shall work directly under the control of the Chief Executive. ' | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0020 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (d) The safety officer shall be appointed before start of construction activities and the safety set-up chart shali be prepared and properly displayed at a conspicuous place. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (d) The safety officer shall be appointed before start of construction activities and the safety set-up chart shali be prepared and properly displayed at a conspicuous place. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0021 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (e) The safety officer shall advise and assist the Owner in fulfillment of his responsibilities concerning prevention of personal injuries and maintaining a safe working environment. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (e) The safety officer shall advise and assist the Owner in fulfillment of his responsibilities concerning prevention of personal injuries and maintaining a safe working environment. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0022 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (f) The safety officer shall be auffiorised to stop the execution ofany work which in his judgment is unsafe and may result in injury to any person and he shall also have the power to remove the employees or contract workers from the site, if they are found not using personal protection equipment or in unsafe practice or procedure. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (f) The safety officer shall be auffiorised to stop the execution ofany work which in his judgment is unsafe and may result in injury to any person and he shall also have the power to remove the employees or contract workers from the site, if they are found not using personal protection equipment or in unsafe practice or procedure. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0023 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (g) The safety officer shall develop and organise safety training programmes at regular intervals in order to impart proper safety training and shall also create safety awareness among the employees. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (g) The safety officer shall develop and organise safety training programmes at regular intervals in order to impart proper safety training and shall also create safety awareness among the employees. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0024 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (2)(a) where the number-of employees, including contract workers exceeds two hundred and fifty, the Owner shall constitute a safety committee comprising of equal number of representatives of the management and the employees and during construction, the safety committee shall also include representatives of contractors and their employees with equal representation and the representatives of the management shall include the safety officer and medical officer: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (2)(a) where the number-of employees, including contract workers exceeds two hundred and fifty, the Owner shall constitute a safety committee comprising of equal number of representatives of the management and the employees and during construction, the safety committee shall also include representatives of contractors and their employees with equal representation and the representatives of the management shall include the safety officer and medical officer: | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 21 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0025 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Provided that where number of employees, including contract workers, is two hundred and fifty or less, the safety committee · shall be constituted by the Owner for a group of electrical plants or electric lines, as the case may be. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Provided that where number of employees, including contract workers, is two hundred and fifty or less, the safety committee · shall be constituted by the Owner for a group of electrical plants or electric lines, as the case may be. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0026 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (b) The safety committee shall promote co-operation between the workers and the management for maintaining proper safety and health at work place. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (b) The safety committee shall promote co-operation between the workers and the management for maintaining proper safety and health at work place. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0027 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (c) The safety committee shall meet at least once in a month during construction stage and once in three months_ during operation and maintenance of electrical plants and electric lines and the decisions and recommendations of the safety committee shall be complied with by the Owner within the time limit as decided by the safety committee. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (c) The safety committee shall meet at least once in a month during construction stage and once in three months_ during operation and maintenance of electrical plants and electric lines and the decisions and recommendations of the safety committee shall be complied with by the Owner within the time limit as decided by the safety committee. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0028 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 7. Safety provisions relating to contractor.- (1)The Owner shall incorporate the safety provisions in the contract document which are required to be complied by the contractor's employees during execution of the contract to facilitate safe working during execution of the work. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 7. Safety provisions relating to contractor.- (1)The Owner shall incorporate the safety provisions in the contract document which are required to be complied by the contractor's employees during execution of the contract to facilitate safe working during execution of the work. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0029 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (2) The contractor shall observe the safety requirements as laid down in the contract and in case of sub-contract, it shall be the responsibility of main contractor that all safety requirements are followed by the employees and staff of the sub- contractor. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (2) The contractor shall observe the safety requirements as laid down in the contract and in case of sub-contract, it shall be the responsibility of main contractor that all safety requirements are followed by the employees and staff of the sub- contractor. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0030 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | AIS | NOT VERIFIED | Safety | AIS | SAFETY | (3) The contractor employing two hundred employees or more, including contract workers, shall have a safety co-ordinator in order to ensure the implementation of safety requirements of the contract and a contractor with lesser number of employees, including contract workers, shall nominate one of his employees to act as safety co-ordinator who shall liaise with the safety officer on matters relating to safety and his name shall be displayed on the notice board at a prominent place at the work site. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (3) The contractor employing two hundred employees or more, including contract workers, shall have a safety co-ordinator in order to ensure the implementation of safety requirements of the contract and a contractor with lesser number of employees, including contract workers, shall nominate one of his employees to act as safety co-ordinator who shall liaise with the safety officer on matters relating to safety and his name shall be displayed on the notice board at a prominent place at the work site. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0031 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (4) The contractor shall be responsible for non-compliance of the safety measures, implications, injuries, fatalities and compensation arising out of such situations or incidents. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (4) The contractor shall be responsible for non-compliance of the safety measures, implications, injuries, fatalities and compensation arising out of such situations or incidents. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0032 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (5) In case of any accident, the contractor shall immediately submit a statement of the same to the Owner and the safety officer, containing the details of the accident, any injury or casualities, extent of property damage and remedial action taken to prevent recurrence and in addition, the contractor shall submit a monthly statement of the accidents to the Owner at the end of each month. | NOT COVERED | tion taken to prevent recurrence and in addition, the contractor shall submit a monthly statement of the accidents to the Owner at the end of each month | NOT VERIFIED | (5) In case of any accident, the contractor shall immediately submit a statement of the same to the Owner and the safety officer, containing the details of the accident, any injury or casualities, extent of property damage and remedial action taken to prevent recurrence and in addition, the contractor shall submit a monthly statement of the accidents to the Owner at the end of each month. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 22 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0033 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | 8. Reporting of accidents.- The cases of outage of an electrical plant or an electric line of following nominal rating due to any accident related to any equipment e.g. fire,· explosion of pressure piping or pressure vessel, implosion, emission of hazardous chemicals, collapse of transmission tower, flooding of power house area, shall be reported to the Authority within twenty four hours, whether or not any death or disablement is caused to any person,- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 23 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0034 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | 9. Emergency management plan.- (1) An on-site emergency management plan shall be formulated for thermal generating plant, hydro-electric generating plant, sub-station and group of electric lines for quickly and effectively dealing with probable emergencies like fire, explosion, gas leakages, landslides, floods, earthquakes, storms, cyclones, hurricanes, and crisis situations arising in the event of strikes, terrorist threats, attacks and sabotages, bomb threats and explosions and reducing response time. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 23 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0035 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | (2) The provisions to be made for the on-site emergency management plan shall conform to the Schedule -Ill annexed to these regulations. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 23 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0036 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | Provided that in case of construction of electrical plants and electric lines, emergency action plan shall be prepared, before commencement of construction activity, to handle emergencies like fire, explosion, collapse of lifting appliances and transport equipment, collapse of building or structures, gas leakages, land slides, floods, earthquakes, storms, cyclones, hurricanes and crisis situations arising in the event of strikes, terrorist threats, attacks arid sabotages, bomb threats and explosions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 23 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0037 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (d) information regarding type of hazardous chemicals and fuels at plant site,- (i) chemicals (quantities and toxicological data); (ii) fuels (quantities and storage method); (ii) material safety data sheets; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (d) information regarding type of hazardous chemicals and fuels at plant site,- (i) chemicals (quantities and toxicological data); (ii) fuels (quantities and storage method); (ii) material safety data sheets; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 24 | .TIIE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0038 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | (i) fire fighting equipment; (ii) details of diesel generating sets and dewatering facilities available; (iii) rescue equipment available; (iv) medical resources available; (v) type of vehicles, mobile cranes, dumpers etc.; (vi) list of contractors and details of resources available with them; (vii) list of private caterers providing canteen facility; (viii) list of emergency material suppliers like tents, pumps, diesel generating sets, tarpaulins etc.; (ix) waterresources available. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (i) fire fighting equipment; (ii) details of diesel generating sets and dewatering facilities available; (iii) rescue equipment available; (iv) medical resources available; (v) type of vehicles, mobile cranes, dumpers etc.; (vi) list of contractors and details of resources available with them; (vii) list of private caterers providing canteen facility; (viii) list of emergency material suppliers like tents, pumps, diesel generating sets, tarpaulins etc.; (ix) waterresources available. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 24 | .TIIE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0039 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Condition Monitoring | General | CONDITION_MONITORING | (i) an occupational health centre having the facilities for health examination, diagnosis, treatment and maintenance of health records; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 25 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0040 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | (3) The medical officer of occupational health center shall be involved in planning the emergency handling of large numberof injured employees in the event such as fire, explosion, natural· calamities and man-made. disasters and all the equipment required for providing immediate relief to the injured during emergencies shall always be kept in readiness in occupational health center. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 26 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0041 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | (5) The Owner shall put in place programme for periodic medical check- up of employees and at least the following periodic medical check-ups shall be carried out and records maintained, namely:- | NOT COVERED | (5) The Owner shall put in place programme for periodic medical check- up of employees and at least the following periodic medical check-ups shall be carri | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 26 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0042 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | (g) response in the event of emergencies including fire, flood, landslide, earthquake etc.; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 27 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0043 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | (2) The Owner shall ensure that adequate safety training is provided by the contractor to his employees. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (2) The Owner shall ensure that adequate safety training is provided by the contractor to his employees. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 27 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0044 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | (3) Safety promotional activities shall be organised periodically to create awareness and enthusiasm among the employees which shall include organising safety day, safety week, fire safety day,· fire safety week, safety competitions, posters, slogans, safety calendars and displays depicting possible consequences of unsafe acts and conditions in conspicuous locations in the plant. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (3) Safety promotional activities shall be organised periodically to create awareness and enthusiasm among the employees which shall include organising safety day, safety week, fire safety day,· fire safety week, safety competitions, posters, slogans, safety calendars and displays depicting possible consequences of unsafe acts and conditions in conspicuous locations in the plant. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 27 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0045 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 8. Safety while simultaneous working in different elevations or locations in hilly areas; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 8. Safety while simultaneous working in different elevations or locations in hilly areas; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 30 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0046 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 10. Suitable safety measures to minimise the effect of mishaps resulting on account of geological surprises. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 10. Suitable safety measures to minimise the effect of mishaps resulting on account of geological surprises. | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 30 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0047 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | The following safety features shall be additionally covered in 'Safety Manual for Operation and Maintenance' in addition to those covered in Schedule-1,- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The following safety features shall be additionally covered in 'Safety Manual for Operation and Maintenance' in addition to those covered in Schedule-1,- | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 30 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0048 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | 1. Procedure for obtaining permission to work for carrying out operations and maintenance of equipment; | 1. Procedure for obtaining permission to work for carrying out operations and maintenance of equipment; | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 30 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0049 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 2. Safety in operation and maintenance of various electro-mechanical equipment as per recommendations of manufacturers; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 2. Safety in operation and maintenance of various electro-mechanical equipment as per recommendations of manufacturers; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 30 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0050 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 10. Safety in washing of live insulators and testing of insulators on live lines; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 10. Safety in washing of live insulators and testing of insulators on live lines; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 32 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0051 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | (c) Major leakage in natural gas pipelines (e.g. full bore rupture of gas pipe line) resulting in unconfined natural ga.s leakage leading to vapour cloud explosion and fire; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 32 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0052 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | (d) Major hydrogen gas leakage from generator leading emergency situation that can lead to fire and explosion; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 32 | THE GAZETTE OF INDIA: EXTRAORDINARY | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0053 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (g) Large scale fire in fuel oil area, coal storage, naphtha or liquefied natural gas storage area. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 33 | [ 'WT III-= 4 J | Extracted from source page; verify surrounding context if using as a final answer.
D05-C0054 | D05 | reg_elec_plants_lines.pdf | Operation and Maintenance of Electrical Plants and Electric Lines Regulations, 2011 | Central Electricity Authority | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | U) Details of fire fighting and other facilities available to deal with emergency conditions; | NOT COVERED | NOT VERIFIED | NOT VERIFIED | U) Details of fire fighting and other facilities available to deal with emergency conditions; | NOT COVERED | Electrical plants/equipment and electric lines within document scope | PDF p. 33 | [ 'WT III-= 4 J | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0001 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | You are kindly aware that a Standing Committee of Experts was constituted vide CEA Letter No CEA/SETD/220-O/2012/1-80 dated 01.01.2013 under Section 73, Clause (1) of the Electricity Act, 2003 to investigate the failure of 220 kV and above Voltage class substation equipment and recommend remedial measures to avert failures in future. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | You are kindly aware that a Standing Committee of Experts was constituted vide CEA Letter No CEA/SETD/220-O/2012/1-80 dated 01.01.2013 under Section 73, Clause (1) of the Electricity Act, 2003 to investigate the failure of 220 kV and above Voltage class substation equipment and recommend remedial measures to avert failures in future. | 220 kV and above voltage class substation equipment | PDF p. 1 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0002 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 24.03.2025 and 25.03.2025 at CEA HQ, New Delhi in hybrid mode to discuss the cause of failures of the substation equipment reported by various utilities to CEA which had failed during the period from July 2023 to December 2024. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 24.03.2025 and 25.03.2025 at CEA HQ, New Delhi in hybrid mode to discuss the cause of failures of the substation equipment reported by various utilities to CEA which had failed during the period from July 2023 to December 2024. | 220 kV and above voltage class substation equipment | PDF p. 1 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0003 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Standing Committee for the failure of the Equipment that occurred during the period from July 2023 to December 2024 has been prepared and is enclosed herewith for kind information and necessary action please. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Standing Committee for the failure of the Equipment that occurred during the period from July 2023 to December 2024 has been prepared and is enclosed herewith for kind information and necessary action please. | 220 kV and above voltage class substation equipment | PDF p. 1 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0004 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | 4.8 Failures of Wave Trap, Coupling Capacitors (CC), Disconnectors/Isolators, GIS Bay, XLPE | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 4.8 Failures of Wave Trap, Coupling Capacitors (CC), Disconnectors/Isolators, GIS Bay, XLPE | 220 kV and above voltage class substation equipment | PDF p. 12 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0005 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 10. Failure report of 160 MVA, 220/132/33 kV Auto Transformer at Barwaha Substation of | NOT COVERED | NOT VERIFIED | 160 MVA; 33 kV | NOT COVERED | 10. Failure report of 160 MVA, 220/132/33 kV Auto Transformer at Barwaha Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0006 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 12. Failure report of 50 MVA, 220 kV Power Transformer at Hinjewadi-1 Substation of | NOT COVERED | NOT VERIFIED | 50 MVA; 220 kV | NOT COVERED | 12. Failure report of 50 MVA, 220 kV Power Transformer at Hinjewadi-1 Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0007 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 14. Failure report of 50 MVA, 220/33 kV, Power Transformer at Vankusawade Substation of | NOT COVERED | NOT VERIFIED | 50 MVA; 33 kV | NOT COVERED | 14. Failure report of 50 MVA, 220/33 kV, Power Transformer at Vankusawade Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0008 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 18. Failure Report of 50 MVA, 220/33 kV Power Transformer at Kurkumbh Substation of | NOT COVERED | NOT VERIFIED | 50 MVA; 33 kV | NOT COVERED | 18. Failure Report of 50 MVA, 220/33 kV Power Transformer at Kurkumbh Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0009 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 19. Failure Report of 25 MVA, 220/33 kV Power Transformer at Purti Substation of MSETCL..... 121 | NOT COVERED | NOT VERIFIED | 25 MVA; 33 kV | NOT COVERED | 19. Failure Report of 25 MVA, 220/33 kV Power Transformer at Purti Substation of MSETCL..... 121 | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0010 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 22. Failure report of 500 MVA, 400/220 kV ICT at Muzaffarnagar Substation of Powergrid......... 134 | NOT COVERED | NOT VERIFIED | 500 MVA; 220 kV | NOT COVERED | 22. Failure report of 500 MVA, 400/220 kV ICT at Muzaffarnagar Substation of Powergrid......... 134 | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0011 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 23. Failure report of 397 MVA, 400 kV Converter Transformer at HVDC Kaniha Substation of | NOT COVERED | NOT VERIFIED | 397 MVA; 400 kV | NOT COVERED | 23. Failure report of 397 MVA, 400 kV Converter Transformer at HVDC Kaniha Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0012 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 24. Failure report of 500 MVA, 400/220 kV ICT at Maharanibagh Substation of Powergrid......... 143 | NOT COVERED | NOT VERIFIED | 500 MVA; 220 kV | NOT COVERED | 24. Failure report of 500 MVA, 400/220 kV ICT at Maharanibagh Substation of Powergrid......... 143 | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0013 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 29. Failure report of 160 MVA, 220/132 kV, BHEL Make Auto Power Transformer at Bhiwadi | NOT COVERED | NOT VERIFIED | 160 MVA; 132 kV | NOT COVERED | 29. Failure report of 160 MVA, 220/132 kV, BHEL Make Auto Power Transformer at Bhiwadi | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0014 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 30. Failure Report of 50 MVA, 230/33 kV Power Transformer at Veeranam Substation of | NOT COVERED | NOT VERIFIED | 50 MVA; 33 kV | NOT COVERED | 30. Failure Report of 50 MVA, 230/33 kV Power Transformer at Veeranam Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0015 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 31. Failure report of 50 MVA, 230 kV Power Transformer at Udayathur Substation of | NOT COVERED | NOT VERIFIED | 50 MVA; 230 kV | NOT COVERED | 31. Failure report of 50 MVA, 230 kV Power Transformer at Udayathur Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0016 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 32. Failure report of 315 MVA, 400/ 230 kV of ICT at Alamathy Substation of TANTRANSCO...... 173 | NOT COVERED | NOT VERIFIED | 315 MVA; 230 kV | NOT COVERED | 32. Failure report of 315 MVA, 400/ 230 kV of ICT at Alamathy Substation of TANTRANSCO...... 173 | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0017 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 33. Failure report of 160 MVA, 3 Phase Auto-transformer at Faridpur Substation of UPPTCL...... 176 | NOT COVERED | NOT VERIFIED | 160 MVA | NOT COVERED | 33. Failure report of 160 MVA, 3 Phase Auto-transformer at Faridpur Substation of UPPTCL...... 176 | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0018 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 34. Failure report of 500 MVA, 400/220/33 kV, 3-Phase ICT at Rasara Substation of UPPTCL...... 179 | NOT COVERED | NOT VERIFIED | 500 MVA; 33 kV | NOT COVERED | 34. Failure report of 500 MVA, 400/220/33 kV, 3-Phase ICT at Rasara Substation of UPPTCL...... 179 | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0019 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 35. Failure report of 400/220/33 kV, 240 MVA 3 Phase ICT at Gorakhpur Substation of | NOT COVERED | NOT VERIFIED | 33 kV; 240 MVA | NOT COVERED | 35. Failure report of 400/220/33 kV, 240 MVA 3 Phase ICT at Gorakhpur Substation of | 220 kV and above voltage class substation equipment | PDF p. 13 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0020 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 36. Failure report of 100 MVA, 220/132 kV Auto Transformer at Bhartna Substation Etawah | NOT COVERED | NOT VERIFIED | 100 MVA; 132 kV | NOT COVERED | 36. Failure report of 100 MVA, 220/132 kV Auto Transformer at Bhartna Substation Etawah | 220 kV and above voltage class substation equipment | PDF p. 14 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0021 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, AIS, Substation | Bus Reactor | Failure / Failure Analysis | AIS | FAILURE_ANALYSIS | 40. Failure report of 50 MVAr, 400 kV Bus Reactor at Ramgarh Jaisalmer Substation of | NOT COVERED | NOT VERIFIED | 50 MVAr; 400 kV | NOT COVERED | 40. Failure report of 50 MVAr, 400 kV Bus Reactor at Ramgarh Jaisalmer Substation of | 220 kV and above voltage class substation equipment | PDF p. 14 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0022 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS, Substation | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | 157. Failure report of 220 kV GIS Disconnector at Saki Substation of Adani Electricity Mumbai | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 157. Failure report of 220 kV GIS Disconnector at Saki Substation of Adani Electricity Mumbai | 220 kV and above voltage class substation equipment | PDF p. 17 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0023 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation, Switchyard | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | As per its mandate to investigate the failure of 220 kV and above voltage class substation/ switchyard equipment and recommend measures to avert recurrence of such failures in future, the Stading Committee receives reports of failures of various substation/ switchyard equipment from various power utilities, which then investigates the failures, and brings out the report for the benefit of the Power Sector as a whole. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | As per its mandate to investigate the failure of 220 kV and above voltage class substation/ switchyard equipment and recommend measures to avert recurrence of such failures in future, the Stading Committee receives reports of failures of various substation/ switchyard equipment from various power utilities, which then investigates the failures, and brings out the report for the benefit of the Power Sector as a whole. | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0024 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Circuit Breaker, Surge Arrester, Substation | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | As part of this process, the failures of substation equipment that occurred during the period, 1st July 2023 - 31st December 2024, were analysed by the Committee in their meeting held on 24th March 2025 and 25th March 2025. Total 26 Utilities reported the failure incidences. A total of 162 failure incidences of Transformers, Reactors, Instrument Transformers, Surge Arresters, Circuit Breakers, Disconnectors, Wave Trap, Coupling Capacitors, Bay, Cable, and PASS Module of 220 kV and above voltage rating were reported between 1st July 2023 and 31st December 2024 to CEA. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | As part of this process, the failures of substation equipment that occurred during the period, 1st July 2023 - 31st December 2024, were analysed by the Committee in their meeting held on 24th March 2025 and 25th March 2025. Total 26 Utilities reported the failure incidences. A total of 162 failure incidences of Transformers, Reactors, Instrument Transformers, Surge Arresters, Circuit Breakers, Disconnectors, Wave Trap, Coupling Capacitors, Bay, Cable, and PASS Module of 220 kV and above voltage rating were reported between 1st July 2023 and 31st December 2024 to CEA. | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0025 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Out of these equipment failures, total 36 cases of Transformer failure were reported. These 36 Transformers consist of 12 Nos. of 400 kV class Transformers and 24 Nos. of 220 kV class Transformers, and none were of 765 kV class. W.r.t. Reactors, total 4 failures were reported during the period, out of which 1 were 765 kV class and 3 were 400 kV class. | NOT COVERED | NOT VERIFIED | 400 kV; 220 kV; 765 kV | NOT COVERED | Out of these equipment failures, total 36 cases of Transformer failure were reported. These 36 Transformers consist of 12 Nos. of 400 kV class Transformers and 24 Nos. of 220 kV class Transformers, and none were of 765 kV class. W.r.t. Reactors, total 4 failures were reported during the period, out of which 1 were 765 kV class and 3 were 400 kV class. | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0026 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker | NOT VERIFIED | Failure / Failure Analysis | Circuit Breaker | FAILURE_ANALYSIS | Total 42 No. of failure cases of Surge arrestors were reported out of which 35 were of 220 kV class, 7 were of 400 kV class and none were of 765 kV class. Failures of Circuit breakers which were reported to CEA were 10, out of which 6 were of 220 kV class, 4 were of 400 kV class and none were of 765 kV class. | NOT COVERED | NOT VERIFIED | 220 kV; 400 kV; 765 kV | NOT COVERED | Total 42 No. of failure cases of Surge arrestors were reported out of which 35 were of 220 kV class, 7 were of 400 kV class and none were of 765 kV class. Failures of Circuit breakers which were reported to CEA were 10, out of which 6 were of 220 kV class, 4 were of 400 kV class and none were of 765 kV class. | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0027 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | Other equipment for which failures were reported include 3 Nos. of Disconnector/Isolator, 3 Nos. of Coupling Capacitors, 4 Nos. of Wave Trap, 1 No. of GIS Bay, 1 No. of Cable and 1 No. of Pass Module. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Other equipment for which failures were reported include 3 Nos. of Disconnector/Isolator, 3 Nos. of Coupling Capacitors, 4 Nos. of Wave Trap, 1 No. of GIS Bay, 1 No. of Cable and 1 No. of Pass Module. | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0028 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Out of the total 162 failures of the equipment that occurred during the period, 22 Nos. of equipment failed within five years, 38 Nos of equipment failed in 5-10 years of period. 66 Nos of equipment failed during 10-20 years of their operation. 31 Nos of equipment failed had operation of more than 20 years. For five equipment, Utilities did not provide the commissioning date. | NOT COVERED | NOT VERIFIED | 5-10 years; 10-20 years; 20 years | NOT COVERED | Out of the total 162 failures of the equipment that occurred during the period, 22 Nos. of equipment failed within five years, 38 Nos of equipment failed in 5-10 years of period. 66 Nos of equipment failed during 10-20 years of their operation. 31 Nos of equipment failed had operation of more than 20 years. For five equipment, Utilities did not provide the commissioning date. | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0029 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | It has been suggested that to prevent the failure of the equipment especially Transformers and Reactors, the practice of Condition Based Monitoring using online modern diagnostic tools should be followed. In case Transformers/ Reactors are reaching their end of Service of life, then close monitoring of these equipment should be carried out. The frequency/ periodicity of measurement should be changed depending on the condition/ healthiness of the equipment in operation. The trend of test results should be monitored rather than the absolute values of test results. The regular cleaning of dust deposited on the housings of major equipment and bushings of transformer in Thermal Power Plant or area with heavy | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | It has been suggested that to prevent the failure of the equipment especially Transformers and Reactors, the practice of Condition Based Monitoring using online modern diagnostic tools should be followed. In case Transformers/ Reactors are reaching their end of Service of life, then close monitoring of these equipment should be carried out. The frequency/ periodicity of measurement should be changed depending on the condition/ healthiness of the equipment in operation. The trend of test results should be monitored rather than the absolute values of test results. The regular cleaning of dust deposited on the housings of major equipment and bushings of transformer in Thermal Power Plant or area with heavy | 220 kV and above voltage class substation equipment | PDF p. 18 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0030 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS, AIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | pollution are essential to avoid flash over across the insulators as frequent flashovers may lead to failure of the equipment. A centralized electrical asset monitoring system has been suggested to be implemented to monitor the condition of all Medium voltage and high voltage electrical assets like GIS, AIS, Breakers, Power Cables including Transformers. All FAT, SAT and Periodic testing data for all electrical equipment shall be stored in this system for performing health assessment. The system shall have advanced health index models that utilize analytics and threshold limits as prescribed by latest IEEE, IEC, and CIGRE standards / recommendations. This system shall also be capable of integrating online monitoring of sensors installed at electrical assets, and inspection records/ reports from the visual inspection of assets. | NOT COVERED | All FAT, SAT and Periodic testing data for all electrical equipment shall be stored in this system for performing health asse | NOT VERIFIED | NOT COVERED | pollution are essential to avoid flash over across the insulators as frequent flashovers may lead to failure of the equipment. A centralized electrical asset monitoring system has been suggested to be implemented to monitor the condition of all Medium voltage and high voltage electrical assets like GIS, AIS, Breakers, Power Cables including Transformers. All FAT, SAT and Periodic testing data for all electrical equipment shall be stored in this system for performing health assessment. The system shall have advanced health index models that utilize analytics and threshold limits as prescribed by latest IEEE, IEC, and CIGRE standards / recommendations. This system shall also be capable of integrating online monitoring of sensors installed at electrical assets, and inspection records/ reports from the visual inspection of assets. | 220 kV and above voltage class substation equipment | PDF p. 19 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0031 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Installation | DGA | INSTALLATION | It shall have the capabilities to monitor DGA, Partial discharge – Electrical & UHF, bushing, fan control, fiber optic monitoring and other monitoring parameters. This system shall be installed for transformers, including existing and new transformers; shall support cloud and on-premise installation and provide access to electrical asset health dashboards at engineer’s PC, Mobile, Laptops or tablets. | It shall have the capabilities to monitor DGA, Partial discharge – Electrical & UHF, bushing, fan control, fiber optic monitoring and other monitoring parameters. This system shall be installed for transformers, including existing and new transformers; shall support cloud and on-premise installation and provide access to electrical asset health dashboards at engineer’s PC, Mobile, Laptops or tablets. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 19 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0032 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker, Substation | NOT VERIFIED | Testing | Circuit Breaker | TESTING | In case of Surge Arrestor, 3rd harmonic resistive component of leakage current is a very good method for assessing healthiness of SA and therefore it should be regularly monitored. In case of Circuit breaker, Dynamic Contact Resistance Measurement (DCRM) test should be conducted once in two years. The necessity of having regular operation & maintenance of substation equipment has been emphasized, and the Utilities have been requested to align their practices in line with the model O& M guidelines issued by CEA in this regard. | In case of Surge Arrestor, 3rd harmonic resistive component of leakage current is a very good method for assessing healthiness of SA and therefore it should be regularly monitored. In case of Circuit breaker, Dynamic Contact Resistance Measurement (DCRM) test should be conducted once in two years. The necessity of having regular operation & maintenance of substation equipment has been emphasized, and the Utilities have been requested to align their practices in line with the model O& M guidelines issued by CEA in this regard. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 19 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0033 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Report of the Standing Committee of Experts on failure of 220 kV and above Voltage class Substation Equipment for the period: July, 2023 – December, 2024 | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | Report of the Standing Committee of Experts on failure of 220 kV and above Voltage class Substation Equipment for the period: July, 2023 – December, 2024 | 220 kV and above voltage class substation equipment | PDF p. 20 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0034 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Circuit Breaker, CT, PT, CVT, Surge Arrester, Substation, Switchyard | Current Transformer | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | Under Section 73, Clause (l) of the Electricity Act, 2003, CEA vide office order no: CEA/SETD/220-O/2012/1-80 dated 01.01.2013 (Annexure-V) constituted a Standing Committee of Experts in the field of design and operation of EHV Substations from CEA, various power utilities and research/academic institutes to investigate the failure of 220 kV and above voltage class substation/ switchyard equipment such as Power/Generator Transformer, Circuit Breaker (CB), Instrument Transformer [i.e. Current Transformer (CT), Potential Transformer (PT) and Capacitor Voltage Transformer (CVT)], Surge Arrester (SA), Isolator etc. and recommend measures to avert recurrence of such failures in future. As part of this activity, CEA has been receiving reports of failures of various substation/ switchyard equipment from power utilities. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | Under Section 73, Clause (l) of the Electricity Act, 2003, CEA vide office order no: CEA/SETD/220-O/2012/1-80 dated 01.01.2013 (Annexure-V) constituted a Standing Committee of Experts in the field of design and operation of EHV Substations from CEA, various power utilities and research/academic institutes to investigate the failure of 220 kV and above voltage class substation/ switchyard equipment such as Power/Generator Transformer, Circuit Breaker (CB), Instrument Transformer [i.e. Current Transformer (CT), Potential Transformer (PT) and Capacitor Voltage Transformer (CVT)], Surge Arrester (SA), Isolator etc. and recommend measures to avert recurrence of such failures in future. As part of this activity, CEA has been receiving reports of failures of various substation/ switchyard equipment from power utilities. | 220 kV and above voltage class substation equipment | PDF p. 20 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0035 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation, Switchyard | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | All the utilities are required to report any event of failure of substation equipment at the earliest in the specified format for reporting the incident (available on CEA website and attached as Annexure-IV) along with all the additional information [like Disturbance Recorder (DR)/ Event Logger (EL) report], SLD, Test reports, O&M history, photographs etc.) to be submitted by the utilities while reporting the incident. The objective of the Standing Committee was to investigate the causes of failures, deliberate the failures of various substation/ switchyard equipment of Power utilities, suggest remedial measures to prevent recurrence of such events in future and prepare a report which would serve as a repository of case studies of failures and suggested remedial measures for future. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | All the utilities are required to report any event of failure of substation equipment at the earliest in the specified format for reporting the incident (available on CEA website and attached as Annexure-IV) along with all the additional information [like Disturbance Recorder (DR)/ Event Logger (EL) report], SLD, Test reports, O&M history, photographs etc.) to be submitted by the utilities while reporting the incident. The objective of the Standing Committee was to investigate the causes of failures, deliberate the failures of various substation/ switchyard equipment of Power utilities, suggest remedial measures to prevent recurrence of such events in future and prepare a report which would serve as a repository of case studies of failures and suggested remedial measures for future. | 220 kV and above voltage class substation equipment | PDF p. 20 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0036 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | In this connection, a meeting of the Standing Committee of Experts to investigate the failure of 220 kV and above voltage Class Substation equipment for the period of July 2023 to December 2024 was held on 24.03.2025 and 25.03.2025 at CEA HQ, New Delhi in hybrid mode under the chairmanship of Chief Engineer, PSE&TD Division, CEA, and Chairman of the Standing Committee. List of participants is given at Annexure-I. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | In this connection, a meeting of the Standing Committee of Experts to investigate the failure of 220 kV and above voltage Class Substation equipment for the period of July 2023 to December 2024 was held on 24.03.2025 and 25.03.2025 at CEA HQ, New Delhi in hybrid mode under the chairmanship of Chief Engineer, PSE&TD Division, CEA, and Chairman of the Standing Committee. List of participants is given at Annexure-I. | 220 kV and above voltage class substation equipment | PDF p. 20 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0037 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Safety | Failure | SAFETY | It was informed that as per Regulation 48 (8) of CEA (Measures relating to Safety and Electric Supply) Regulations, failures of any 220 kV and above voltage level substation equipment shall be reported by the owner utility within 48 hours of occurrence of the failure, to the Authority, and the reasons for failure and measures to be taken to avoid recurrence of failure shall be sent to the Authority within one month of the occurrence as per stipulated formats, along | NOT COVERED | NOT VERIFIED | 220 kV; 48 hours | It was informed that as per Regulation 48 (8) of CEA (Measures relating to Safety and Electric Supply) Regulations, failures of any 220 kV and above voltage level substation equipment shall be reported by the owner utility within 48 hours of occurrence of the failure, to the Authority, and the reasons for failure and measures to be taken to avoid recurrence of failure shall be sent to the Authority within one month of the occurrence as per stipulated formats, along | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 20 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0038 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | with all the additional information (like Disturbance Recorder (DR)/ Event Logger (EL) report], SLD, Test Reports, O&M history, Photographs etc.). He requested all utilities to adhere to these timelines strictly. | with all the additional information (like Disturbance Recorder (DR)/ Event Logger (EL) report], SLD, Test Reports, O&M history, Photographs etc.). He requested all utilities to adhere to these timelines strictly. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 21 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0039 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Circuit Breaker, CT, CVT, Surge Arrester, GIS, Substation | Current Transformer | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | It was informed that for the period of July 2023 to December 2024, a total of 170 incidents of failure of substation equipment were reported to CEA by 27 Utilities (Aptransco, AEGCL, Adani, BBMB, CSPTCL, DTL, DVC, IndiGrid, KPTCL, KSEB, MSETCL, MPPTCL, MSPGCL, NEEPCO, NHPC, NPCIL, NTPC, OPTCL, Powergrid, RRVUNL, RVPNL, TANTRANSCO, Torrent Power Ltd, TVNL, UPPTCL, WBPDCL, GETCO). Failure of forty Transformers, four Reactors, forty seven Current Transformer, thirteen PTs/CVTs, forty four Surge Arresters/LA, nine Circuit Breakers, three Disconnectors/Isolators, four Wave Trap, three Coupling Capacitor, one GIS Bay, one Cable Fault and one PASS (Plug and Switch System) Module (Hybrid Switchgear) were reported. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | It was informed that for the period of July 2023 to December 2024, a total of 170 incidents of failure of substation equipment were reported to CEA by 27 Utilities (Aptransco, AEGCL, Adani, BBMB, CSPTCL, DTL, DVC, IndiGrid, KPTCL, KSEB, MSETCL, MPPTCL, MSPGCL, NEEPCO, NHPC, NPCIL, NTPC, OPTCL, Powergrid, RRVUNL, RVPNL, TANTRANSCO, Torrent Power Ltd, TVNL, UPPTCL, WBPDCL, GETCO). Failure of forty Transformers, four Reactors, forty seven Current Transformer, thirteen PTs/CVTs, forty four Surge Arresters/LA, nine Circuit Breakers, three Disconnectors/Isolators, four Wave Trap, three Coupling Capacitor, one GIS Bay, one Cable Fault and one PASS (Plug and Switch System) Module (Hybrid Switchgear) were reported. | 220 kV and above voltage class substation equipment | PDF p. 21 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0040 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | AIS | NOT VERIFIED | Failure / Failure Analysis | AIS | FAILURE_ANALYSIS | In this connection, he also raised concern w.r.t. non-participation of the Utilities, who have reported failure incidences, in the meeting. It was noted that out of the 27 Utilities who have reported failures, representatives from only 17 Utilities attended the Standing Committee meeting. No representative from CSPTCL, KPTCL, MSPGCL, NEEPCO, NPCIL, RRVUNL, TANTRANSCO, Torrent Power Ltd, TVNL, WBPDCL attended the meeting. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | In this connection, he also raised concern w.r.t. non-participation of the Utilities, who have reported failure incidences, in the meeting. It was noted that out of the 27 Utilities who have reported failures, representatives from only 17 Utilities attended the Standing Committee meeting. No representative from CSPTCL, KPTCL, MSPGCL, NEEPCO, NPCIL, RRVUNL, TANTRANSCO, Torrent Power Ltd, TVNL, WBPDCL attended the meeting. | 220 kV and above voltage class substation equipment | PDF p. 21 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0041 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Circuit Breaker, CVT, Surge Arrester, Substation | NOT VERIFIED | Maintenance Schedule | Surge Arrester | SCHEDULE | He requested all the utilities to furnish a brief on the action taken by various utilities w.r.t. recommendations given by the standing committee in their past meetings such as centralized asset monitoring system, condition based monitoring, etc. He also emphasized on the need to for undertaking regular O&M of substation equipment, and requested utilities to present a brief on O&M practices being followed by them for various substation equipment such as Transformer, Reactors, Circuit Breaker, CT, PT/CVT, Isolator/Disconnector, Surge Arrester/LA etc. covering various aspects like the tests conducted on the equipment, periodicity of testing and permissible limits/acceptable range of test results. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 21 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0042 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Thereafter presentations by Utilities for their respective failure incidents were held. The failure incidents and their subsequent findings were deliberated upon by the members of the committee. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Thereafter presentations by Utilities for their respective failure incidents were held. The failure incidents and their subsequent findings were deliberated upon by the members of the committee. | 220 kV and above voltage class substation equipment | PDF p. 21 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0043 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 1. A total of 162 failure incidence of Transformer, Reactors, Instrument Transformers, Surge | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 1. A total of 162 failure incidence of Transformer, Reactors, Instrument Transformers, Surge | 220 kV and above voltage class substation equipment | PDF p. 21 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0044 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 2. Representative of Adani Transmission Ltd presented 3 Nos. of failures covering failure of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 2. Representative of Adani Transmission Ltd presented 3 Nos. of failures covering failure of | 220 kV and above voltage class substation equipment | PDF p. 22 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0045 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | CT at Mundra S/s, GIS Isolator at Saki S/s and Cable at Aarey S/s. Representative from M/s Adani Transmission stated that in case of the failure of CT, the CT was sent to OEM and it was found that the rupture disc was operated, minor burning marks were observed on the primary conductor, flashover observed on one side of HV spacer on active part and grading was found to be removed from the Aluminum mantel which fell down inside the insulator. Root cause Analysis could not be done due to substantial damage to CT, however, the probable cause is due to minor welding cracks in grading and loose contact between HV spacer & Active part. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | CT at Mundra S/s, GIS Isolator at Saki S/s and Cable at Aarey S/s. Representative from M/s Adani Transmission stated that in case of the failure of CT, the CT was sent to OEM and it was found that the rupture disc was operated, minor burning marks were observed on the primary conductor, flashover observed on one side of HV spacer on active part and grading was found to be removed from the Aluminum mantel which fell down inside the insulator. Root cause Analysis could not be done due to substantial damage to CT, however, the probable cause is due to minor welding cracks in grading and loose contact between HV spacer & Active part. | 220 kV and above voltage class substation equipment | PDF p. 22 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0046 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Surge Arrester, GIS | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | For the case of failure of GIS Isolator at Saki S/s, ATL representative stated that heavy contamination of gas was observed in Y phase chamber of Bus Isolator module of Bay-8 (Bus Coupler). The absorbent bag from top of inspection window fell due to broken absorbent cage. The installation in the similar network was inspected and absorbent cage was replaced. The Committee recommended to change the cage material, if required. For the case of failure of Cable at Aarey S/s, ATL representative mentioned that as per the report of the patrolling personnel, the cable got damaged due to excessive vertical pressure during heavy material movement of Metro Works. CE (PSE&TD), CEA recommended to find the actual root cause of the fault after consultation with the OEM and requested to increase the patrolling frequency of such critical sites. 3. Representative of OPTCL presented failure of three Surge Arrester and one CT. OPTCL | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | For the case of failure of GIS Isolator at Saki S/s, ATL representative stated that heavy contamination of gas was observed in Y phase chamber of Bus Isolator module of Bay-8 (Bus Coupler). The absorbent bag from top of inspection window fell due to broken absorbent cage. The installation in the similar network was inspected and absorbent cage was replaced. The Committee recommended to change the cage material, if required. For the case of failure of Cable at Aarey S/s, ATL representative mentioned that as per the report of the patrolling personnel, the cable got damaged due to excessive vertical pressure during heavy material movement of Metro Works. CE (PSE&TD), CEA recommended to find the actual root cause of the fault after consultation with the OEM and requested to increase the patrolling frequency of such critical sites. 3. Representative of OPTCL presented failure of three Surge Arrester and one CT. OPTCL | 220 kV and above voltage class substation equipment | PDF p. 22 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0047 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Surge Arrester | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | representative stated that two number of Surge Arrester had served for more than 25 years. He further stated that one Surge Arrester served only for two years. The reason of failure Surge Arrester within two years could not be identified. This one faulty Surge Arrester was beyond repair and was replaced with the Surge Arrester of same make. CE (PSE&TD), CEA requested to keep the replaced Surge Arrester under monitoring as there may be design issue with Surge Arrestor. Further, the committee recommended to monitor the leakage current of Surge Arrester at the time of commissioning and in every 2 years thereafter. | NOT COVERED | NOT VERIFIED | 25 years; 2 years | NOT COVERED | representative stated that two number of Surge Arrester had served for more than 25 years. He further stated that one Surge Arrester served only for two years. The reason of failure Surge Arrester within two years could not be identified. This one faulty Surge Arrester was beyond repair and was replaced with the Surge Arrester of same make. CE (PSE&TD), CEA requested to keep the replaced Surge Arrester under monitoring as there may be design issue with Surge Arrestor. Further, the committee recommended to monitor the leakage current of Surge Arrester at the time of commissioning and in every 2 years thereafter. | 220 kV and above voltage class substation equipment | PDF p. 22 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0048 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Surge Arrester | NOT VERIFIED | Failure / Failure Analysis | Tan Delta | FAILURE_ANALYSIS | Representative of M/s Adani Transmission was of view that Switching Impulse Protection Level (SIPL) and Lightning Impulse Protection Level (LIPL) should be defined instead of Switching Impulse withstand Level (SIWL) and Lightening Impulse withstand Level (LIWL) to prevent the failure of Surge Arresters. For the reported CT failure, OPTCL representative informed that oil leakage could be the reason of failure of CT. CE (PSE&TD), CEA remarked that since the CT has served for only 6 years, detailed reason should be found out for the failure. OPTCL representative informed that Tan delta of CT is being measured regularly and if the measured value of Tan delta of the CTs are found to be high, they are kept under observation and depending on the abnormality of the results they are replaced with good ones. | NOT COVERED | NOT VERIFIED | 6 years | NOT COVERED | Representative of M/s Adani Transmission was of view that Switching Impulse Protection Level (SIPL) and Lightning Impulse Protection Level (LIPL) should be defined instead of Switching Impulse withstand Level (SIWL) and Lightening Impulse withstand Level (LIWL) to prevent the failure of Surge Arresters. For the reported CT failure, OPTCL representative informed that oil leakage could be the reason of failure of CT. CE (PSE&TD), CEA remarked that since the CT has served for only 6 years, detailed reason should be found out for the failure. OPTCL representative informed that Tan delta of CT is being measured regularly and if the measured value of Tan delta of the CTs are found to be high, they are kept under observation and depending on the abnormality of the results they are replaced with good ones. | 220 kV and above voltage class substation equipment | PDF p. 22 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0049 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Troubleshooting | General | TROUBLESHOOTING | The committee recommended regular thermos-vision scanning of clamps and connectors for detection of hotspots and taking remedial measures thereof. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The committee recommended regular thermos-vision scanning of clamps and connectors for detection of hotspots and taking remedial measures thereof. | 220 kV and above voltage class substation equipment | PDF p. 22 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0050 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 4. Representative of BBMB presented failure of one auto-transformer at Panipat and three | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 4. Representative of BBMB presented failure of one auto-transformer at Panipat and three | 220 kV and above voltage class substation equipment | PDF p. 23 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0051 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Surge Arrester | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | Surge Arrester. BBMB representative informed that the internal inspection of auto- transformer was carried out and it was found that there was complete burning of transformer windings. The auto-transformer is thus found to be beyond repair. The transformer has served around 45 years after commissioning. He further stated that they have adopted the measure of condition-based monitoring for replacement of old transformer. For the failure of Surge Arresters, BBMB representative informed that the damage seems to have occurred due to transient voltage surge/dielectric breakdown or degradation of ZnO blocks due to their ageing factors. The committee recommended to monitor the leakage current before and after monsoon to ascertain the effect of moisture. 5. Representative of Powergrid presented the failure of three Transformers occurred at | NOT COVERED | NOT VERIFIED | 45 years | NOT COVERED | Surge Arrester. BBMB representative informed that the internal inspection of auto- transformer was carried out and it was found that there was complete burning of transformer windings. The auto-transformer is thus found to be beyond repair. The transformer has served around 45 years after commissioning. He further stated that they have adopted the measure of condition-based monitoring for replacement of old transformer. For the failure of Surge Arresters, BBMB representative informed that the damage seems to have occurred due to transient voltage surge/dielectric breakdown or degradation of ZnO blocks due to their ageing factors. The committee recommended to monitor the leakage current before and after monsoon to ascertain the effect of moisture. 5. Representative of Powergrid presented the failure of three Transformers occurred at | 220 kV and above voltage class substation equipment | PDF p. 23 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0052 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | HVDC Talcher, Muzaffarnagar and Maharanibag and one Reactor occurred during July 2023 to December 2023. For the failure of converter transformer at HVDC Talcher, Powergrid representative informed that fault may have occurred inside the Star winding which might have led to observance of carbonization and burnt paper pieces inside snout and take off lead of Y1 bushing. Deviations in magnetization current and voltage ratio during post failure LV test results also indicate that there is a fault in the secondary star winding. Based on LV test results and internal inspection observations, it is inferred that the said converter transformer failed due to insulation failure of secondary star winding. Further, it was also informed that the Talcher area has high ambient temperature and the Converter Transformer is continuously on overload condition at 1.25 p.u. (1250 MW). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | HVDC Talcher, Muzaffarnagar and Maharanibag and one Reactor occurred during July 2023 to December 2023. For the failure of converter transformer at HVDC Talcher, Powergrid representative informed that fault may have occurred inside the Star winding which might have led to observance of carbonization and burnt paper pieces inside snout and take off lead of Y1 bushing. Deviations in magnetization current and voltage ratio during post failure LV test results also indicate that there is a fault in the secondary star winding. Based on LV test results and internal inspection observations, it is inferred that the said converter transformer failed due to insulation failure of secondary star winding. Further, it was also informed that the Talcher area has high ambient temperature and the Converter Transformer is continuously on overload condition at 1.25 p.u. (1250 MW). | 220 kV and above voltage class substation equipment | PDF p. 23 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0053 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, GIS, Substation | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | This might have led to the failure of Converter Transformer. OEM i.e. M/s Siemens has enhanced the pump capacity in 2007 considering the generally overload condition found at Talcher. However, OEM has not taken any action to improve the design to address the high ambient temperature at Talcher end. Powergrid representative stated that to avoid the reoccurrence of such failure, RLDC has been communicated to reduce the load to 1 p.u. For the other two transformers i.e. 400/220 kV, 315 MVA Muzaffarnagar Substation, 400/220 kV, 500 MVA at Maharanibag GIS Substation, the main tank got burst at the bottom bell joint. As it was found that main tank got burst, the committee recommended to improve the tank design, if required. For the failure of Reactor at Balipara S/s, from the LV test results and internal inspection, it was observed that the Y-Phase winding at lead take-off got damaged. | NOT COVERED | NOT VERIFIED | 220 kV; 315 MVA; 500 MVA | NOT COVERED | This might have led to the failure of Converter Transformer. OEM i.e. M/s Siemens has enhanced the pump capacity in 2007 considering the generally overload condition found at Talcher. However, OEM has not taken any action to improve the design to address the high ambient temperature at Talcher end. Powergrid representative stated that to avoid the reoccurrence of such failure, RLDC has been communicated to reduce the load to 1 p.u. For the other two transformers i.e. 400/220 kV, 315 MVA Muzaffarnagar Substation, 400/220 kV, 500 MVA at Maharanibag GIS Substation, the main tank got burst at the bottom bell joint. As it was found that main tank got burst, the committee recommended to improve the tank design, if required. For the failure of Reactor at Balipara S/s, from the LV test results and internal inspection, it was observed that the Y-Phase winding at lead take-off got damaged. | 220 kV and above voltage class substation equipment | PDF p. 23 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0054 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Substation | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | It was suspected that said Reactor failed due to failure of the inter- turn insulation of the of the Y-Phase winding. Further, Powergrid representative presented the failure of four Transformers and one Reactor during the period of January 2024 to December 2024. For the failure of Transformer at Kaithal Substation, it was informed that there is a history of occurrence of frequent through faults in 220 kV side feeder. From the LV test report, DGA history, physical and internal inspection of the failed ICT, it was inferred that there was dielectric | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | It was suspected that said Reactor failed due to failure of the inter- turn insulation of the of the Y-Phase winding. Further, Powergrid representative presented the failure of four Transformers and one Reactor during the period of January 2024 to December 2024. For the failure of Transformer at Kaithal Substation, it was informed that there is a history of occurrence of frequent through faults in 220 kV side feeder. From the LV test report, DGA history, physical and internal inspection of the failed ICT, it was inferred that there was dielectric | 220 kV and above voltage class substation equipment | PDF p. 23 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0055 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | failure of B phase series winding during through fault in associated 220 kV transmission line. Director (PSE&TD), CEA requested to review the design of the ICT after consultation with OEM because the Transformers are generally designed to bear such through faults. CE (PSE&TD), CEA recommended to reduce the Earth resistance to substation wherever it is higher than 0.5 ohm. ICT at Munirabad failed due to dielectric failure of B-Phase series winding. For the case of ICT failure at Kala substation, from the Disturbance recorder, DGA history, Physical and internal inspection of the failed ICT, it was inferred that there is flashover between Tap winding of B phase bottom to main tank. For the failure of ICT at Birpara substation, Powergrid representative stated that the line connecting to Bhutan from Birpara Substation is having too many faults. | NOT COVERED | NOT VERIFIED | 220 kV; 0.5 ohm | NOT COVERED | failure of B phase series winding during through fault in associated 220 kV transmission line. Director (PSE&TD), CEA requested to review the design of the ICT after consultation with OEM because the Transformers are generally designed to bear such through faults. CE (PSE&TD), CEA recommended to reduce the Earth resistance to substation wherever it is higher than 0.5 ohm. ICT at Munirabad failed due to dielectric failure of B-Phase series winding. For the case of ICT failure at Kala substation, from the Disturbance recorder, DGA history, Physical and internal inspection of the failed ICT, it was inferred that there is flashover between Tap winding of B phase bottom to main tank. For the failure of ICT at Birpara substation, Powergrid representative stated that the line connecting to Bhutan from Birpara Substation is having too many faults. | 220 kV and above voltage class substation equipment | PDF p. 24 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0056 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC, Substation | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | These faults led to weakening of the Transformer. In the present case of failure of ICT at Birpara Substation, it was inferred that there was flash over in the Y-Phase OLTC selector switch. CE (PSE&TD), CEA requested that the proper maintenance practices should be followed where OLTC is required with ICTs. The reactor failed suddenly during charging of the reactor due to flashover/ arcing across the winding in bottom part. During the flashover/ arcing, high fault current (approx. 9 kA) has flown in the reactor. The committee recommended that the failure event which occur within 10 years of services is a matter of concern, therefore such matters should be got thoroughly investigated by utilities with the help of OEM for improving the product design. 6. Representative of AEGCL presented the failure of one Auto-Transformer at Namrup GSS. | NOT COVERED | NOT VERIFIED | 10 years | NOT COVERED | These faults led to weakening of the Transformer. In the present case of failure of ICT at Birpara Substation, it was inferred that there was flash over in the Y-Phase OLTC selector switch. CE (PSE&TD), CEA requested that the proper maintenance practices should be followed where OLTC is required with ICTs. The reactor failed suddenly during charging of the reactor due to flashover/ arcing across the winding in bottom part. During the flashover/ arcing, high fault current (approx. 9 kA) has flown in the reactor. The committee recommended that the failure event which occur within 10 years of services is a matter of concern, therefore such matters should be got thoroughly investigated by utilities with the help of OEM for improving the product design. 6. Representative of AEGCL presented the failure of one Auto-Transformer at Namrup GSS. | 220 kV and above voltage class substation equipment | PDF p. 24 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0057 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | He briefed that the transformer was of CGL make and served for around 44 years, therefore, ageing could be the reason of failure. He stated that the failed 220/132 kV, 50 MVA Transformer was replaced with the 220/132 kV, 100 MVA transformer of same make. 7. Representative of DVC presented the failure of one Auto-Transformer and two Lightning | NOT COVERED | NOT VERIFIED | 44 years; 132 kV; 50 MVA; 100 MVA | NOT COVERED | He briefed that the transformer was of CGL make and served for around 44 years, therefore, ageing could be the reason of failure. He stated that the failed 220/132 kV, 50 MVA Transformer was replaced with the 220/132 kV, 100 MVA transformer of same make. 7. Representative of DVC presented the failure of one Auto-Transformer and two Lightning | 220 kV and above voltage class substation equipment | PDF p. 24 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0058 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Bushing | NOT VERIFIED | Failure / Failure Analysis | Tan Delta | FAILURE_ANALYSIS | Arresters. He stated that in case of failure of Auto-Transformer at Barjora S/s, it was found during internal inspection that the Y phase HV winding failed and heavy gas generated inside tank & OLTC of Auto-Transformer. The transformer is of BHEL make and served for around 30 years. During the previous routine maintenance before fault, abnormal values of Tan delta of R-phase bushing were observed. DVC has written the letter to OEM to quote the price for repairing of failed Auto-Transformer. | NOT COVERED | NOT VERIFIED | 30 years | NOT COVERED | Arresters. He stated that in case of failure of Auto-Transformer at Barjora S/s, it was found during internal inspection that the Y phase HV winding failed and heavy gas generated inside tank & OLTC of Auto-Transformer. The transformer is of BHEL make and served for around 30 years. During the previous routine maintenance before fault, abnormal values of Tan delta of R-phase bushing were observed. DVC has written the letter to OEM to quote the price for repairing of failed Auto-Transformer. | 220 kV and above voltage class substation equipment | PDF p. 24 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0059 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | For the failure of LA at Purulia Substation, he informed that LA had served for around 30 years, therefore aging could be the reason of the failure. In case of failure of LA at Barjora Substation, he informed that LA had served for around 18 years, therefore, ageing could be the reason of failure in case of LA failure at Barjora S/s. Both the faulty LAs at Paulia S/s and at Barjora S/s were beyond repair. 8. Representative of MPPTCL presented the failure of one Auto-Transformer at Barwaha | NOT COVERED | NOT VERIFIED | 30 years; 18 years | NOT COVERED | For the failure of LA at Purulia Substation, he informed that LA had served for around 30 years, therefore aging could be the reason of the failure. In case of failure of LA at Barjora Substation, he informed that LA had served for around 18 years, therefore, ageing could be the reason of failure in case of LA failure at Barjora S/s. Both the faulty LAs at Paulia S/s and at Barjora S/s were beyond repair. 8. Representative of MPPTCL presented the failure of one Auto-Transformer at Barwaha | 220 kV and above voltage class substation equipment | PDF p. 24 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0060 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Substation | NOT VERIFIED | Safety | OLTC | SAFETY | scheduled shut down on line-II for testing different condition of interlocks between CB/Isolators at their end. This line-II was earthed at both ends, however, line-I was charged. As per information from METRO substation during testing some wrong operation happened and line-I supply extended to line-II through METRO 132 kV Bus, therefore, leading to creation of a dead 3 phase earthed line fault. The line was tripped in time from both ends. This fault was fed by above Transformer from 220 kV Substation Bhopal. The transformer has served only for 5 years. Root Cause of Transformer failure could not be identified as the transformer got burnt completely. NIFPS system operated but could not save the Transformer as main tank OLTC diverter switch cover blasted therefore no nitrogen blanket could be maintained. | NOT COVERED | NOT VERIFIED | 132 kV; 220 kV; 5 years | scheduled shut down on line-II for testing different condition of interlocks between CB/Isolators at their end. This line-II was earthed at both ends, however, line-I was charged. As per information from METRO substation during testing some wrong operation happened and line-I supply extended to line-II through METRO 132 kV Bus, therefore, leading to creation of a dead 3 phase earthed line fault. The line was tripped in time from both ends. This fault was fed by above Transformer from 220 kV Substation Bhopal. The transformer has served only for 5 years. Root Cause of Transformer failure could not be identified as the transformer got burnt completely. NIFPS system operated but could not save the Transformer as main tank OLTC diverter switch cover blasted therefore no nitrogen blanket could be maintained. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 25 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0061 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, CVT, Surge Arrester | Current Transformer | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | Other than Transformer, MPPTCL reported failure of two Current Transformers, one CVT, six Surge Arresters and three Wave Traps. MPPTCL representative informed that they are replacing the SCT make CTs as they have the high rate of failure. Representative of MPPTCL informed that LA at Chichli S/s is of the rating 66 kV, 10 kA MOCV 56 kV. As the Committee is to discuss the failure of 220 kV and above equipment, therefore the LA may be removed from the Agenda. Committee noted the same. 9. Representative of GETCO presented the failure of one Transformers at Jambuva S/s and | NOT COVERED | NOT VERIFIED | 66 kV; 56 kV; 220 kV | NOT COVERED | Other than Transformer, MPPTCL reported failure of two Current Transformers, one CVT, six Surge Arresters and three Wave Traps. MPPTCL representative informed that they are replacing the SCT make CTs as they have the high rate of failure. Representative of MPPTCL informed that LA at Chichli S/s is of the rating 66 kV, 10 kA MOCV 56 kV. As the Committee is to discuss the failure of 220 kV and above equipment, therefore the LA may be removed from the Agenda. Committee noted the same. 9. Representative of GETCO presented the failure of one Transformers at Jambuva S/s and | 220 kV and above voltage class substation equipment | PDF p. 25 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0062 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Safety | Failure | SAFETY | one Transformer at Morbi S/s. Both the Transformers have served for around 6 years. For the Transformer Failure at Morbi substation, GETCO representative informed that the high intensity Phase to Ground fault took place in 66 kV line which was cleared by protective system of 66 kV line. Subsequently, fault developed in transformer and the Transformer tripped in differential and buchholz relay. It seems that after the clearance of UG cable line fault well within time, transformer LV winding could not withstand recovery voltage which lead to damage to LV winding insulation. CE (PSE&TD), CEA requested to provide the proper distance protection at 66 kV lines or provide suitable back-up protection to the transformer. | NOT COVERED | NOT VERIFIED | 6 years; 66 kV | one Transformer at Morbi S/s. Both the Transformers have served for around 6 years. For the Transformer Failure at Morbi substation, GETCO representative informed that the high intensity Phase to Ground fault took place in 66 kV line which was cleared by protective system of 66 kV line. Subsequently, fault developed in transformer and the Transformer tripped in differential and buchholz relay. It seems that after the clearance of UG cable line fault well within time, transformer LV winding could not withstand recovery voltage which lead to damage to LV winding insulation. CE (PSE&TD), CEA requested to provide the proper distance protection at 66 kV lines or provide suitable back-up protection to the transformer. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 25 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0063 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | For the transformer failure at Jambuva Substation, GETCO representative informed that a monkey got electrocuted on 66 kV Jambuva B – Dabhoi line bus Isolators which caused tripping of transformer. The committee recommended to contact OEM regarding improvement in the design of the transformer, if required, since the transformers have failed within 6 years of service only. 10. Representative of MSETCL from Pune Zone presented the failure of three Transformers | NOT COVERED | NOT VERIFIED | 66 kV; 6 years | NOT COVERED | For the transformer failure at Jambuva Substation, GETCO representative informed that a monkey got electrocuted on 66 kV Jambuva B – Dabhoi line bus Isolators which caused tripping of transformer. The committee recommended to contact OEM regarding improvement in the design of the transformer, if required, since the transformers have failed within 6 years of service only. 10. Representative of MSETCL from Pune Zone presented the failure of three Transformers | 220 kV and above voltage class substation equipment | PDF p. 25 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0064 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Substation | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | at Kurkumbh, Alephta and Chinchwad Substation. For the failure of Transformer at Kurkumbh Substation, he intimated that the 33 kV side feeder fault might have created the axial force which could not be sustained by the transformer HV/LV winding. The HV R-ph and B-ph winding might have got their inter-turn shorted. For the failure of ICT at Alephta, MSETCL representative informed that flashover took place on OLTC driver shaft between Y and B phase due to failure of dielectric strength. The transformer had been repaired at site itself by replacing the driver shaft. | NOT COVERED | NOT VERIFIED | 33 kV | NOT COVERED | at Kurkumbh, Alephta and Chinchwad Substation. For the failure of Transformer at Kurkumbh Substation, he intimated that the 33 kV side feeder fault might have created the axial force which could not be sustained by the transformer HV/LV winding. The HV R-ph and B-ph winding might have got their inter-turn shorted. For the failure of ICT at Alephta, MSETCL representative informed that flashover took place on OLTC driver shaft between Y and B phase due to failure of dielectric strength. The transformer had been repaired at site itself by replacing the driver shaft. | 220 kV and above voltage class substation equipment | PDF p. 25 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0065 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | For the failure of ICT at Chinchwad substation, he informed that ICT got failed due to inter-turn shorting of Y-phase series winding. CE (PSE&TD), CEA enquired about non-operation of differential protection even after inter-turn fault was present. MSETCL representative replied that the fault current was very low. The committee recommended to check the setting of the differential relay. The committee also recommended to discuss with the Discom regarding the issue of failure of Transformer due to frequent downstream feeder faults to prevent such failure. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | For the failure of ICT at Chinchwad substation, he informed that ICT got failed due to inter-turn shorting of Y-phase series winding. CE (PSE&TD), CEA enquired about non-operation of differential protection even after inter-turn fault was present. MSETCL representative replied that the fault current was very low. The committee recommended to check the setting of the differential relay. The committee also recommended to discuss with the Discom regarding the issue of failure of Transformer due to frequent downstream feeder faults to prevent such failure. | 220 kV and above voltage class substation equipment | PDF p. 26 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0066 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | MSETCL representative intimated that MSETCL has formed a committee regarding transformer repair, the committee has conducted detailed study on the transformer failure and it has been observed that major cause of failure of Power Transformer is that the LV windings are not mechanically strong to bear the frequent distribution side outgoing feeder faults. He further suggested that wherever there is an issue of failure of Power Transformer due to frequent feeder faults, NGR is being used in LV neutral. This led to bringing the fault current level down and therefore, low axial forces on the transformer winding. Representative of MSETCL from Nagpur Zone presented the failure of one Transformer at Purti Substation and one current transformer. For the failure of Power Transformer at Purti Substation, he informed that station AC supply got failed due to 33 kV feeder fault. | NOT COVERED | NOT VERIFIED | 33 kV | NOT COVERED | MSETCL representative intimated that MSETCL has formed a committee regarding transformer repair, the committee has conducted detailed study on the transformer failure and it has been observed that major cause of failure of Power Transformer is that the LV windings are not mechanically strong to bear the frequent distribution side outgoing feeder faults. He further suggested that wherever there is an issue of failure of Power Transformer due to frequent feeder faults, NGR is being used in LV neutral. This led to bringing the fault current level down and therefore, low axial forces on the transformer winding. Representative of MSETCL from Nagpur Zone presented the failure of one Transformer at Purti Substation and one current transformer. For the failure of Power Transformer at Purti Substation, he informed that station AC supply got failed due to 33 kV feeder fault. | 220 kV and above voltage class substation equipment | PDF p. 26 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0067 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Circuit Breaker, Bushing, Substation | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | This led to station DC supply failure because of weak VRLA battery set. It was observed that Oil spilled out from PRV and flashover was observed on Transformer bushing. No protection operated and fault was eventually cleared by remote end Circuit breaker. It was informed that only one set of battery is available with the substation. CE (PSE&TD), CEA requested to follow CEA Regulations with respect to the requirement of providing Battery sets and Chargers. MSETCL also representative informed that frequent failure have been observed on 220/33 kV transformers because the windings of these transformers are not mechanically strong and frequent fault have been observed on 33 kV side feeder which feeds distribution Network. 11. Representative of NHPC presented the failure of one Transformer at Dhauliganga, one | NOT COVERED | NOT VERIFIED | 33 kV | NOT COVERED | This led to station DC supply failure because of weak VRLA battery set. It was observed that Oil spilled out from PRV and flashover was observed on Transformer bushing. No protection operated and fault was eventually cleared by remote end Circuit breaker. It was informed that only one set of battery is available with the substation. CE (PSE&TD), CEA requested to follow CEA Regulations with respect to the requirement of providing Battery sets and Chargers. MSETCL also representative informed that frequent failure have been observed on 220/33 kV transformers because the windings of these transformers are not mechanically strong and frequent fault have been observed on 33 kV side feeder which feeds distribution Network. 11. Representative of NHPC presented the failure of one Transformer at Dhauliganga, one | 220 kV and above voltage class substation equipment | PDF p. 26 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0068 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Circuit Breaker, CVT | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | CVT at Chamera Power Station and one Circuit Breaker at Dhauliganga. NHPC representative informed that the transformer of rating 11/400/√ 3, 48.33 MVA, 1 phase at Dulhasti Power Station did not actually fail. During the DGA test on transformer as a preventive measure, increasing amount of gases were found. As per the recommendation of OEM, the transformer was replaced with the spare. The committee has recommended to conduct the periodic DGA to assess the healthiness of transformer. Further the Committee also noted that since the Transformer did not get failed and was taken out of service as a preventive measure, the instant case shall not be considered as ICT failure, hence should be removed from the list of Transformers failures. | NOT COVERED | The committee has recommended to conduct the periodic DGA to assess the healthiness of transformer | 48.33 MVA | NOT COVERED | CVT at Chamera Power Station and one Circuit Breaker at Dhauliganga. NHPC representative informed that the transformer of rating 11/400/√ 3, 48.33 MVA, 1 phase at Dulhasti Power Station did not actually fail. During the DGA test on transformer as a preventive measure, increasing amount of gases were found. As per the recommendation of OEM, the transformer was replaced with the spare. The committee has recommended to conduct the periodic DGA to assess the healthiness of transformer. Further the Committee also noted that since the Transformer did not get failed and was taken out of service as a preventive measure, the instant case shall not be considered as ICT failure, hence should be removed from the list of Transformers failures. | 220 kV and above voltage class substation equipment | PDF p. 26 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0069 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker, CVT | NOT VERIFIED | Failure / Failure Analysis | Circuit Breaker | FAILURE_ANALYSIS | In case of CVT failure, NHPC representative informed that the CVT had served for around 29 years, therefore, ageing of equipment could be the reason of failure of CVT. In case of failure of Circuit Breaker at Dhauliganga, NHPC representative informed that number of operations are high for Circuit Breaker at Dhauliganga Power Station. Due to frequent operations, the Circuit Breaker got failed. | NOT COVERED | NOT VERIFIED | 29 years | NOT COVERED | In case of CVT failure, NHPC representative informed that the CVT had served for around 29 years, therefore, ageing of equipment could be the reason of failure of CVT. In case of failure of Circuit Breaker at Dhauliganga, NHPC representative informed that number of operations are high for Circuit Breaker at Dhauliganga Power Station. Due to frequent operations, the Circuit Breaker got failed. | 220 kV and above voltage class substation equipment | PDF p. 26 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0070 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 12. Representative of DTL presented the failure of one Transformer at Pappankalan-I S/s and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 12. Representative of DTL presented the failure of one Transformer at Pappankalan-I S/s and | 220 kV and above voltage class substation equipment | PDF p. 27 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0071 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Surge Arrester | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | two Surge Arrester at Mehrauli and Okhla S/s. For the failure of Transformer, DTL representative informed that internal inspection was carried out before fault and CFT (Core, Frame and Tank Insulation Resistance) test was not normal. Earlier, the Transformer showed high values of Acetylene during routine PMS (Preventive Maintenance Schedule) maintenance. Filtration of the Oil was carried out and after the filtration of the Oil, DGA results were found normal before taking the Transformer into service. It was intimated that this transformer served DTL for about 31 years and the deterioration of insulation due to ageing and frequent fault at 66 kV level may have resulted in failure of the transformer. For the failure of Surge Arresters, it was intimated that both the SAs had completed their life as per the preventive maintenance schedule. 13. Representative of KSEBL presented the failure of one Auto-Transformer of 66.67 MVA at | NOT COVERED | NOT VERIFIED | 31 years; 66 kV; 66.67 MVA | NOT COVERED | two Surge Arrester at Mehrauli and Okhla S/s. For the failure of Transformer, DTL representative informed that internal inspection was carried out before fault and CFT (Core, Frame and Tank Insulation Resistance) test was not normal. Earlier, the Transformer showed high values of Acetylene during routine PMS (Preventive Maintenance Schedule) maintenance. Filtration of the Oil was carried out and after the filtration of the Oil, DGA results were found normal before taking the Transformer into service. It was intimated that this transformer served DTL for about 31 years and the deterioration of insulation due to ageing and frequent fault at 66 kV level may have resulted in failure of the transformer. For the failure of Surge Arresters, it was intimated that both the SAs had completed their life as per the preventive maintenance schedule. 13. Representative of KSEBL presented the failure of one Auto-Transformer of 66.67 MVA at | 220 kV and above voltage class substation equipment | PDF p. 27 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0072 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, GIS, Substation | Current Transformer | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | Edappon Substation and one GIS bay at Ettumanoor Substation. For the failure of Auto- Transformer, KSEBL representative informed that two squirrels climbed on to the tertiary bus bar thereby causing a dead short circuit between the live part of the tertiary bus bar and earth. The tertiary winding of the transformer got completely damaged and required to be replaced. CE (PSE&TD), CEA suggested to KSEBL representative to get the relay settings checked as long time taken to isolate the fault might have led to damage of tertiary winding. For the failure of GIS bay, KSEBL representative mentioned that the flash occurred at gas barrier insulation. Gas purity test was conducted after failure and high SO2 levels in the CB and Line isolator compartments were detected indicating occurrence of flashover. Committee recommended to take the opinion of the OEM for failure of the Gas barrier insulation. 14. Representative of NTPC presented the failure of two Current Transformers at Sipat Power | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Edappon Substation and one GIS bay at Ettumanoor Substation. For the failure of Auto- Transformer, KSEBL representative informed that two squirrels climbed on to the tertiary bus bar thereby causing a dead short circuit between the live part of the tertiary bus bar and earth. The tertiary winding of the transformer got completely damaged and required to be replaced. CE (PSE&TD), CEA suggested to KSEBL representative to get the relay settings checked as long time taken to isolate the fault might have led to damage of tertiary winding. For the failure of GIS bay, KSEBL representative mentioned that the flash occurred at gas barrier insulation. Gas purity test was conducted after failure and high SO2 levels in the CB and Line isolator compartments were detected indicating occurrence of flashover. Committee recommended to take the opinion of the OEM for failure of the Gas barrier insulation. 14. Representative of NTPC presented the failure of two Current Transformers at Sipat Power | 220 kV and above voltage class substation equipment | PDF p. 27 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0073 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | Station. It was informed that the routine DGA test of oil sample was conducted for both the CTs and high concentration of H2 was found. Both the CTs did not fail but replaced as a preventive measure. Further, it was intimated by the NTPC representative that NTPC has now adopted the policy of replacing CTs after 20 years of service since CTs become more prone to failure after 20 years of life. Committee noted that since the CTs did not get failed and were taken out of service as a preventive measure, therefore, these failure shall be removed from the list of CT failures. 15. Representative of IndiGrid presented the failure of one ICT at Kabulpur S/s, one Reactor | NOT COVERED | NOT VERIFIED | 20 years | NOT COVERED | Station. It was informed that the routine DGA test of oil sample was conducted for both the CTs and high concentration of H2 was found. Both the CTs did not fail but replaced as a preventive measure. Further, it was intimated by the NTPC representative that NTPC has now adopted the policy of replacing CTs after 20 years of service since CTs become more prone to failure after 20 years of life. Committee noted that since the CTs did not get failed and were taken out of service as a preventive measure, therefore, these failure shall be removed from the list of CT failures. 15. Representative of IndiGrid presented the failure of one ICT at Kabulpur S/s, one Reactor | 220 kV and above voltage class substation equipment | PDF p. 27 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0074 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Kadarpur S/s and one Lightning Arrester at Bari S/s. He briefed that one ICT at 400/220/132kV Grid S/S, Kabulpur failed during earth fault in 220 kV line. During the fault, Transformer winding might have experienced forces and weak insulation of the winding might have got damaged leading to short circuit in the winding. The failure of ICT was due to inter-turn shorting of winding conductor caused by weakening of insulation. He further informed that the ICT was repaired in 2014 due to through faults at 220 kV side and after repairing, the ICT was working satisfactorily. The committee observed that | NOT COVERED | NOT VERIFIED | 132kV; 220 kV | NOT COVERED | Kadarpur S/s and one Lightning Arrester at Bari S/s. He briefed that one ICT at 400/220/132kV Grid S/S, Kabulpur failed during earth fault in 220 kV line. During the fault, Transformer winding might have experienced forces and weak insulation of the winding might have got damaged leading to short circuit in the winding. The failure of ICT was due to inter-turn shorting of winding conductor caused by weakening of insulation. He further informed that the ICT was repaired in 2014 due to through faults at 220 kV side and after repairing, the ICT was working satisfactorily. The committee observed that | 220 kV and above voltage class substation equipment | PDF p. 27 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0075 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Substation | Bus Reactor | Safety | Transformer Oil | SAFETY | proper coordination should be established between downstream network protection system and substation equipment protection system. In view of this Committee recommended IndiGrid to check the protection provided in downstream network. For the Bus Reactor failure at Kadarpur S/s, IndiGrid representative briefed that the Bus Reactor got tripped while taking the Bus Reactor into service. The switching transient might have caused flashover in the B-phase winding and resulted in tripping of the Bus Reactor. It was observed that NIFPES system operated and oil was drained. OEM has visited the site and declared the Reactor unrepairable. M/s IndiGird was in the process of procuring new Reactor. The committee suggested that OEM be requested to provide the reason for the failure of Reactor and get suitable recommendations. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | proper coordination should be established between downstream network protection system and substation equipment protection system. In view of this Committee recommended IndiGrid to check the protection provided in downstream network. For the Bus Reactor failure at Kadarpur S/s, IndiGrid representative briefed that the Bus Reactor got tripped while taking the Bus Reactor into service. The switching transient might have caused flashover in the B-phase winding and resulted in tripping of the Bus Reactor. It was observed that NIFPES system operated and oil was drained. OEM has visited the site and declared the Reactor unrepairable. M/s IndiGird was in the process of procuring new Reactor. The committee suggested that OEM be requested to provide the reason for the failure of Reactor and get suitable recommendations. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 28 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0076 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Further, IndiGrid informed that LA at Bari S/s did not get failed however, due to heavy rain the foundation got tilted and the LA got damaged. After this incident, foundation of all the LAs have been checked and strengthened to avoid such incidents in future. The committee observed that the LA did not get fail and was damaged due to foundation, the same shall be removed from the list of LA failures. 16. Representative of RRVPNL presented the failure of one Transformer at Bhiwadi S/s, one | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Further, IndiGrid informed that LA at Bari S/s did not get failed however, due to heavy rain the foundation got tilted and the LA got damaged. After this incident, foundation of all the LAs have been checked and strengthened to avoid such incidents in future. The committee observed that the LA did not get fail and was damaged due to foundation, the same shall be removed from the list of LA failures. 16. Representative of RRVPNL presented the failure of one Transformer at Bhiwadi S/s, one | 220 kV and above voltage class substation equipment | PDF p. 28 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0077 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Circuit Breaker, CT, Surge Arrester, Substation, Fire Protection | Current Transformer | Safety | Fire Protection | SAFETY | Reactors at Ramgarh S/s, five Current Transformers, two Circuit Breakers and two Surge Arresters. For the failure of Transformer, RRVPNL representative informed that fault occurred on the 220/132 kV, 160 MVA Transformer-II. The Y-phase Circuit Breaker pole on Transformer-II got stuck while clearing the fault, and the LBB command was triggered. As a result, all 220 kV Circuit Breakers at the Bhiwadi substation tripped on the LBB command, except for the 220 kV Bhiwadi (PG)-II Circuit Breaker, which failed to operate because its Y-phase pole was stuck. The line was then tripped from the remote end using Zone-2 protection. The Transformer-II caught fire and NIFPES system could not operate due to damaged cable in the yard. CE (PSE&TD), CEA requested to RVPNL to contact OEM and submit complete report since transformer got failed within 10 years of service only. | NOT COVERED | NOT VERIFIED | 132 kV; 160 MVA; 220 kV; 10 years | Reactors at Ramgarh S/s, five Current Transformers, two Circuit Breakers and two Surge Arresters. For the failure of Transformer, RRVPNL representative informed that fault occurred on the 220/132 kV, 160 MVA Transformer-II. The Y-phase Circuit Breaker pole on Transformer-II got stuck while clearing the fault, and the LBB command was triggered. As a result, all 220 kV Circuit Breakers at the Bhiwadi substation tripped on the LBB command, except for the 220 kV Bhiwadi (PG)-II Circuit Breaker, which failed to operate because its Y-phase pole was stuck. The line was then tripped from the remote end using Zone-2 protection. The Transformer-II caught fire and NIFPES system could not operate due to damaged cable in the yard. CE (PSE&TD), CEA requested to RVPNL to contact OEM and submit complete report since transformer got failed within 10 years of service only. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 28 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0078 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | For the failure of Reactor, RRVPNL representative mentioned that all the bushing and winding of the reactor got completely damaged. In such condition, the testing of said reactor was not possible and therefore could not be carried out. He further mentioned that Disturbance Recorder (DR) could not be able to record this event due to some internal issue. CE (PSE&TD), CEA stated that it might be possible that DR has not been particularly configured to record that event or DR has been configured to record unwanted events also causing overloading of DR, and rectify the same. The committee recommended to RRVPNL to take up the matter with OEM since the reactor got failed within 7 years of service only. For the failure of CT of 33 kV, 1000/1 A, 4 core at Sri Ganganagar, representative of RRVPNL stated that the rating of the CT is 33 kV. | NOT COVERED | NOT VERIFIED | 7 years; 33 kV; 1 A | NOT COVERED | For the failure of Reactor, RRVPNL representative mentioned that all the bushing and winding of the reactor got completely damaged. In such condition, the testing of said reactor was not possible and therefore could not be carried out. He further mentioned that Disturbance Recorder (DR) could not be able to record this event due to some internal issue. CE (PSE&TD), CEA stated that it might be possible that DR has not been particularly configured to record that event or DR has been configured to record unwanted events also causing overloading of DR, and rectify the same. The committee recommended to RRVPNL to take up the matter with OEM since the reactor got failed within 7 years of service only. For the failure of CT of 33 kV, 1000/1 A, 4 core at Sri Ganganagar, representative of RRVPNL stated that the rating of the CT is 33 kV. | 220 kV and above voltage class substation equipment | PDF p. 28 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0079 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | The mandate of the Committee is to investigate the failure of Substation equipment of 220 kV and above, therefore the same may be removed from the list of failures. The committee noted it. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | The mandate of the Committee is to investigate the failure of Substation equipment of 220 kV and above, therefore the same may be removed from the list of failures. The committee noted it. | 220 kV and above voltage class substation equipment | PDF p. 28 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0080 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT | Current Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 17. Representative of KPTCL presented the failure of one Current Transformer. He stated that | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 17. Representative of KPTCL presented the failure of one Current Transformer. He stated that | 220 kV and above voltage class substation equipment | PDF p. 29 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0081 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CVT | NOT VERIFIED | Safety | Transformer Oil | SAFETY | heavy arcing was observed at P1 terminal of ‘Y’ phase CT of 220 kV Doni line – 2 bay which tripped on overcurrent relay. During this incident, due to heavy arcing at P1 terminal of CT, Oil tank got damaged and resulted in small holes on the top of CT and oil spill-over. The CT has served for around 25 years. However, it can be repaired and put in service again. 18. UPPTCL reported the failure of six Transformers, twenty four CTs, four PT/CVTs, four | NOT COVERED | NOT VERIFIED | 220 kV; 25 years | heavy arcing was observed at P1 terminal of ‘Y’ phase CT of 220 kV Doni line – 2 bay which tripped on overcurrent relay. During this incident, due to heavy arcing at P1 terminal of CT, Oil tank got damaged and resulted in small holes on the top of CT and oil spill-over. The CT has served for around 25 years. However, it can be repaired and put in service again. 18. UPPTCL reported the failure of six Transformers, twenty four CTs, four PT/CVTs, four | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 29 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0082 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Then UPPTCL representative presented only two transformers failure report. UPPTCL representative presented the case of failure of 315 MVA, 440/220/33 kV ICT at Rasara Substation. He informed that during the inspection it was observed that flashover occurred in tertiary winding due to insulation failure. The transformer was failed during warranty period. On-site inspection of transformer was done by OEM. However, OEM decided to conduct further testing and repairing at their works. For the failure of ICT at Sarnath, UPPTCL representative informed that the Transformer did not fail and it was taken out of service as a preventive measure due to observed increasing trend of Acetylene in transformer oil. Therefore, this may not be considered as a transformer failure. Accordingly, the mentioned Transformer may be removed from the list of the failures of the Transformers. The committee noted same. 19. Representatives of AP Transco, RRVUNL, TANTRANSCO, Torrent Power Limited, | NOT COVERED | NOT VERIFIED | 315 MVA; 33 kV | NOT COVERED | Then UPPTCL representative presented only two transformers failure report. UPPTCL representative presented the case of failure of 315 MVA, 440/220/33 kV ICT at Rasara Substation. He informed that during the inspection it was observed that flashover occurred in tertiary winding due to insulation failure. The transformer was failed during warranty period. On-site inspection of transformer was done by OEM. However, OEM decided to conduct further testing and repairing at their works. For the failure of ICT at Sarnath, UPPTCL representative informed that the Transformer did not fail and it was taken out of service as a preventive measure due to observed increasing trend of Acetylene in transformer oil. Therefore, this may not be considered as a transformer failure. Accordingly, the mentioned Transformer may be removed from the list of the failures of the Transformers. The committee noted same. 19. Representatives of AP Transco, RRVUNL, TANTRANSCO, Torrent Power Limited, | 220 kV and above voltage class substation equipment | PDF p. 29 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0083 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | CSPTCL, TVNL, NPCIL, NEEPCO, MSPGCL, WBPDCL and TTC did not attend the meeting. Therefore, failure events reported by these Utilities could not be discussed. 20. The Chief Engineer (PSE&TD), CEA concluded the deliberations with the following | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | CSPTCL, TVNL, NPCIL, NEEPCO, MSPGCL, WBPDCL and TTC did not attend the meeting. Therefore, failure events reported by these Utilities could not be discussed. 20. The Chief Engineer (PSE&TD), CEA concluded the deliberations with the following | 220 kV and above voltage class substation equipment | PDF p. 29 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0084 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | a. Each Utility is required to intimate each incidence of failure of equipment to | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | a. Each Utility is required to intimate each incidence of failure of equipment to | 220 kV and above voltage class substation equipment | PDF p. 29 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0085 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Chairperson of the Standing Committee within 48 hours of occurrence of the failure. Further, each Utility shall submit the detailed report of equipment failure within one month of occurrence of failure as per the format available on CEA website along with all the relevant information such as test reports, photographs, OEM recommendation etc. This will help not only in analysing the failure events, but also enable the Committee members to undertake site visit in time, if required. | NOT COVERED | NOT VERIFIED | 48 hours | NOT COVERED | Chairperson of the Standing Committee within 48 hours of occurrence of the failure. Further, each Utility shall submit the detailed report of equipment failure within one month of occurrence of failure as per the format available on CEA website along with all the relevant information such as test reports, photographs, OEM recommendation etc. This will help not only in analysing the failure events, but also enable the Committee members to undertake site visit in time, if required. | 220 kV and above voltage class substation equipment | PDF p. 29 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0086 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Substation | Current Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | MPPTCL, 1one GT of rating 1/400/√ 3, 48.33 MVA, 1 phase GT at Dulhasti Power Station of NHPC, two Current Transformers at Sipat Power Station of NTPC, one CT of rating 33 kV, 1000/1 A, 4 core at Sri Ganganagar S/s of RRVPNL, one LA at Bari S/s of IndiGrid, one 315 MVA, 440/220/33 kV ICT at Rasara Substation would be removed from the list of failures as they are not actual failures, but taken out of service for maintenance purposes. | NOT COVERED | NOT VERIFIED | 48.33 MVA; 33 kV; 1 A; 315 MVA | NOT COVERED | MPPTCL, 1one GT of rating 1/400/√ 3, 48.33 MVA, 1 phase GT at Dulhasti Power Station of NHPC, two Current Transformers at Sipat Power Station of NTPC, one CT of rating 33 kV, 1000/1 A, 4 core at Sri Ganganagar S/s of RRVPNL, one LA at Bari S/s of IndiGrid, one 315 MVA, 440/220/33 kV ICT at Rasara Substation would be removed from the list of failures as they are not actual failures, but taken out of service for maintenance purposes. | 220 kV and above voltage class substation equipment | PDF p. 30 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0087 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Circuit Breaker, Surge Arrester, GIS | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | The Committee investigates failures of 220 kV and above voltage class equipment only. A total of 162 failure incidences of Transformers, Reactors, Instrument Transformers, Surge Arresters, Circuit Breakers, Disconnectors, Wave Trap, Coupling Capacitors, GIS Bay, Cable and PASS Module of 220 kV and above voltage rating were reported between 1st July 2023 and 31st December 2024 to CEA. The voltage wise quantity of each equipment has been indicated in the Table-1 below: | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | The Committee investigates failures of 220 kV and above voltage class equipment only. A total of 162 failure incidences of Transformers, Reactors, Instrument Transformers, Surge Arresters, Circuit Breakers, Disconnectors, Wave Trap, Coupling Capacitors, GIS Bay, Cable and PASS Module of 220 kV and above voltage rating were reported between 1st July 2023 and 31st December 2024 to CEA. The voltage wise quantity of each equipment has been indicated in the Table-1 below: | 220 kV and above voltage class substation equipment | PDF p. 31 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0088 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | re-Commissioning (after repairing of the equipment) and failure date. (ii) For the 5 case of equipment failures, date of commissioning was not provided by | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | re-Commissioning (after repairing of the equipment) and failure date. (ii) For the 5 case of equipment failures, date of commissioning was not provided by | 220 kV and above voltage class substation equipment | PDF p. 32 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0089 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | TVNL ER - - 1 - - - - - - 1 UPPTCL NR 4 24 4 11 4 1 1 1 50 WBPDCL ER - - - - 1 - - - - 1 Total 36 4 42 15 42 10 4 6 3 162 Complete details of all the above-mentioned equipment failures is provided in Annexure-II. The probable cause of failure is based on information, data, and reports furnished by the utility. The type of equipment wise analysis of failures is presented in ensuing paras. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | TVNL ER - - 1 - - - - - - 1 UPPTCL NR 4 24 4 11 4 1 1 1 50 WBPDCL ER - - - - 1 - - - - 1 Total 36 4 42 15 42 10 4 6 3 162 Complete details of all the above-mentioned equipment failures is provided in Annexure-II. The probable cause of failure is based on information, data, and reports furnished by the utility. The type of equipment wise analysis of failures is presented in ensuing paras. | 220 kV and above voltage class substation equipment | PDF p. 33 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0090 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | Transformer of CSPTCL at Khedamara S/s has failed on the day of commissioning itself. ii. Summary of Inter Connecting Transformers/Generator Transformers (GTs) reported to CEA that have failed between 1st July 2023 and 31st Dec 2024 is detailed below (Table 5): | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Transformer of CSPTCL at Khedamara S/s has failed on the day of commissioning itself. ii. Summary of Inter Connecting Transformers/Generator Transformers (GTs) reported to CEA that have failed between 1st July 2023 and 31st Dec 2024 is detailed below (Table 5): | 220 kV and above voltage class substation equipment | PDF p. 34 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0091 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Note: The probable cause of failure is based on information, data, and reports furnished by the utility. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Note: The probable cause of failure is based on information, data, and reports furnished by the utility. | 220 kV and above voltage class substation equipment | PDF p. 37 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0092 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | iii. As can be seen from Table 5 above, thirty six (36) transformer failure cases from July 2023 to December 2024 have been reported by fourteen (14) Utilities to CEA. It is highlighted that a large number of transformer failure cases remain unreported as many of power utilities [State Transmission Utilities, Private Utilities/Licensees, Central Transmission Utilities, Public Sector Power Utilities] in the Country have not reported the failures. iv. Out of total 36 failures of the Transformers occurred, 24 were of 220 kV class, 12 of 400 kV class and none of 765 class. 10 Nos. of Transformers failed within five years, 4 Nos. of Transformers failed in 5-10 years of period. 19 Nos. of Transformers failed during 10-20 years of their operation. 3 Nos. of Transformers failed who had operation of more than 20 years. The transformers failures that occurred between 1st July 2023 and 31st December 2024 from the commissioning of the equipment is as per the below graph below: | NOT COVERED | NOT VERIFIED | 220 kV; 400 kV; 5-10 years; 10-20 years; 20 years | NOT COVERED | iii. As can be seen from Table 5 above, thirty six (36) transformer failure cases from July 2023 to December 2024 have been reported by fourteen (14) Utilities to CEA. It is highlighted that a large number of transformer failure cases remain unreported as many of power utilities [State Transmission Utilities, Private Utilities/Licensees, Central Transmission Utilities, Public Sector Power Utilities] in the Country have not reported the failures. iv. Out of total 36 failures of the Transformers occurred, 24 were of 220 kV class, 12 of 400 kV class and none of 765 class. 10 Nos. of Transformers failed within five years, 4 Nos. of Transformers failed in 5-10 years of period. 19 Nos. of Transformers failed during 10-20 years of their operation. 3 Nos. of Transformers failed who had operation of more than 20 years. The transformers failures that occurred between 1st July 2023 and 31st December 2024 from the commissioning of the equipment is as per the below graph below: | 220 kV and above voltage class substation equipment | PDF p. 37 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0093 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | i. Failure of the following Reactors have been reported to CEA during the period from July 2023 and December 2024 by three (3) utilities. Cause of failure is based on information, data and reports furnished by the utility. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | i. Failure of the following Reactors have been reported to CEA during the period from July 2023 and December 2024 by three (3) utilities. Cause of failure is based on information, data and reports furnished by the utility. | 220 kV and above voltage class substation equipment | PDF p. 39 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0094 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | i. Summary of failure of CTs between July 2023 and December 2024 as reported to CEA is detailed below (Table 7): Table 7: Summary of failure of CTs | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | i. Summary of failure of CTs between July 2023 and December 2024 as reported to CEA is detailed below (Table 7): Table 7: Summary of failure of CTs | 220 kV and above voltage class substation equipment | PDF p. 40 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0095 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT | Current Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | ii. It is observed that forty two (42) Nos. of cases of Current Transformers failure that occurred during the period from July 2023 to December 2024 have been reported to CEA by eleven (11) utilities out which 34 were of 220 kV class, 5 were of 400 kV class and 3 were of 765 kV class. iii. Out of total 42 failures of the Current Transformers occurred, 3 Nos. of Current Transformers failed within five years, 20 Nos. of Current Transformers failed in 5- 10 years of period. 13 Nos. of Current Transformers failed during 10-20 years of their operation. 4 Nos. of Current Transformers failed which had operation of more than 20 years. For 2 Nos of Current Transformers, Utility has not given commissioning date, therefore analysis could not be carried out. The Current Transformers failures occurred between 1st July 2023 to 31st December 2024 from the commissioning of the equipment is as per the below graph below: | NOT COVERED | NOT VERIFIED | 220 kV; 400 kV; 765 kV; 5- 10 years; 10-20 years; 20 years | NOT COVERED | ii. It is observed that forty two (42) Nos. of cases of Current Transformers failure that occurred during the period from July 2023 to December 2024 have been reported to CEA by eleven (11) utilities out which 34 were of 220 kV class, 5 were of 400 kV class and 3 were of 765 kV class. iii. Out of total 42 failures of the Current Transformers occurred, 3 Nos. of Current Transformers failed within five years, 20 Nos. of Current Transformers failed in 5- 10 years of period. 13 Nos. of Current Transformers failed during 10-20 years of their operation. 4 Nos. of Current Transformers failed which had operation of more than 20 years. For 2 Nos of Current Transformers, Utility has not given commissioning date, therefore analysis could not be carried out. The Current Transformers failures occurred between 1st July 2023 to 31st December 2024 from the commissioning of the equipment is as per the below graph below: | 220 kV and above voltage class substation equipment | PDF p. 43 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0096 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | CVT | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | iv. Summary of failure of PTs/ CVTs, between July 2023 and December 2024 as reported to CEA is detailed below (Table 8): | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | iv. Summary of failure of PTs/ CVTs, between July 2023 and December 2024 as reported to CEA is detailed below (Table 8): | 220 kV and above voltage class substation equipment | PDF p. 43 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0097 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | CVT | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | v. It is observed that fifteen (15) Nos. of cases of PTs/CVTs failure that occurred during the period from July 2023 to December 2024 have been reported to CEA by eleven (11) utilities out which 12 were of 220 kV class, 3 were of 400 kV class and none were of 765 kV class. vi. Out of total 15 failures of the PTs/CVTs occurred, 1 Nos. of PTs/CVTs failed within five years, 4 Nos. of PTs/CVTs failed in 5-10 years of period. 2 Nos. of PTs/CVTs failed during 10-20 years of their operation. 8 Nos. of PTs/CVTs failed which had operation of more than 20 years. The PTs/CVTs failures occurred between 1st July 2023 to 31st December 2024 from the commissioning of the equipment is as per the below graph below: | NOT COVERED | NOT VERIFIED | 220 kV; 400 kV; 765 kV; 5-10 years; 10-20 years; 20 years | NOT COVERED | v. It is observed that fifteen (15) Nos. of cases of PTs/CVTs failure that occurred during the period from July 2023 to December 2024 have been reported to CEA by eleven (11) utilities out which 12 were of 220 kV class, 3 were of 400 kV class and none were of 765 kV class. vi. Out of total 15 failures of the PTs/CVTs occurred, 1 Nos. of PTs/CVTs failed within five years, 4 Nos. of PTs/CVTs failed in 5-10 years of period. 2 Nos. of PTs/CVTs failed during 10-20 years of their operation. 8 Nos. of PTs/CVTs failed which had operation of more than 20 years. The PTs/CVTs failures occurred between 1st July 2023 to 31st December 2024 from the commissioning of the equipment is as per the below graph below: | 220 kV and above voltage class substation equipment | PDF p. 44 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0098 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CVT, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Analysis of failures vii. In the case of Instrument Transformer, fifty seven (57) Nos. of failure occurred during the period from July 2023 to December 2024 have been reported to CEA by thirteen (13) Utilities. However, it may be noted that due to only a handful of utilities reporting the failure, it is not possible to successfully capture the statistics of service life of key electrical equipment in the substations across various utilities in India. viii. In most of the cases of failure of CT/ CVT/ PT, the equipment had blasted or flashed over. In such cases, it becomes difficult to pin point the cause of failure. However, such failures may be attributed to deterioration of internal insulation and moisture ingress. Some of the failures of equipment could be due to ageing. ix. The number of different PT/CVT failures as reported in last 7 years to CEA has been shown in the graph below: | NOT COVERED | NOT VERIFIED | 7 years | NOT COVERED | Analysis of failures vii. In the case of Instrument Transformer, fifty seven (57) Nos. of failure occurred during the period from July 2023 to December 2024 have been reported to CEA by thirteen (13) Utilities. However, it may be noted that due to only a handful of utilities reporting the failure, it is not possible to successfully capture the statistics of service life of key electrical equipment in the substations across various utilities in India. viii. In most of the cases of failure of CT/ CVT/ PT, the equipment had blasted or flashed over. In such cases, it becomes difficult to pin point the cause of failure. However, such failures may be attributed to deterioration of internal insulation and moisture ingress. Some of the failures of equipment could be due to ageing. ix. The number of different PT/CVT failures as reported in last 7 years to CEA has been shown in the graph below: | 220 kV and above voltage class substation equipment | PDF p. 45 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0099 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker | NOT VERIFIED | Failure / Failure Analysis | Circuit Breaker | FAILURE_ANALYSIS | ii. It is observed that ten (10) Nos. of cases of CBs failure that occurred during the period from July 2023 to December 2024 have been reported to CEA by five (5) utilities out which 6 were of 220 kV class, 4 were of 400 kV class and none were of 765 kV class. However, it may be noted that due to a handful of utilities reporting the failure, it is not possible to successfully capture the statistics of service life iii. The Circuit breakers failures occurred between July 2023 and December 2024 from the commissioning of the equipment is as per the below graph below: | NOT COVERED | NOT VERIFIED | 220 kV; 400 kV; 765 kV | NOT COVERED | ii. It is observed that ten (10) Nos. of cases of CBs failure that occurred during the period from July 2023 to December 2024 have been reported to CEA by five (5) utilities out which 6 were of 220 kV class, 4 were of 400 kV class and none were of 765 kV class. However, it may be noted that due to a handful of utilities reporting the failure, it is not possible to successfully capture the statistics of service life iii. The Circuit breakers failures occurred between July 2023 and December 2024 from the commissioning of the equipment is as per the below graph below: | 220 kV and above voltage class substation equipment | PDF p. 46 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0100 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | i. Total forty two (42) Nos. of cases of SA/LA failure that occurred between July 2023 to December 2024 were reported to CEA by twelve (12) utilities. Summary of failure of Surge Arrestors is as below (Table-10): | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | i. Total forty two (42) Nos. of cases of SA/LA failure that occurred between July 2023 to December 2024 were reported to CEA by twelve (12) utilities. Summary of failure of Surge Arrestors is as below (Table-10): | 220 kV and above voltage class substation equipment | PDF p. 47 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0101 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | ii. Out of these, fourty two (42) Nos. of SAs failures reported to CEA, 35 are of 220 kV class, seven (7) Nos. of SAs are of 400 kV class. iii. Out of total 42 failures of the Surge Arrestors occurred, 3 Nos. of Surge Arrestors failed within five years, 4 Nos. of Surge Arrestors failed in 5-10 years of period. 24 Nos. of Surge Arrestors failed during 10-20 years of their operation. 8 Nos. of Surge Arrestors failed which had operation of more than 20 years. For three equipment Utilities did not provide the commissioning date, therefore analysis could not be carried out. | NOT COVERED | NOT VERIFIED | 220 kV; 400 kV; 5-10 years; 10-20 years; 20 years | NOT COVERED | ii. Out of these, fourty two (42) Nos. of SAs failures reported to CEA, 35 are of 220 kV class, seven (7) Nos. of SAs are of 400 kV class. iii. Out of total 42 failures of the Surge Arrestors occurred, 3 Nos. of Surge Arrestors failed within five years, 4 Nos. of Surge Arrestors failed in 5-10 years of period. 24 Nos. of Surge Arrestors failed during 10-20 years of their operation. 8 Nos. of Surge Arrestors failed which had operation of more than 20 years. For three equipment Utilities did not provide the commissioning date, therefore analysis could not be carried out. | 220 kV and above voltage class substation equipment | PDF p. 49 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0102 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | iv. The number of Surge Arrestors failures occurred between July 2023 and December 2024 from the commissioning of the equipment is as per the below graph below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | iv. The number of Surge Arrestors failures occurred between July 2023 and December 2024 from the commissioning of the equipment is as per the below graph below: | 220 kV and above voltage class substation equipment | PDF p. 49 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0103 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | 4.8 Failures of Wave Trap, Coupling Capacitors (CC), Disconnectors/Isolators, GIS Bay, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 4.8 Failures of Wave Trap, Coupling Capacitors (CC), Disconnectors/Isolators, GIS Bay, | 220 kV and above voltage class substation equipment | PDF p. 50 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0104 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | i. As reported to CEA total 4 Nos. of Wave Trap, 3 Nos. of Coupling Capacitor, 3 Nos. of Disconnector/Isolator, 1 No. of GIS Bay, 1 No. of Cable and 1 No. of PASS Module failed between July 2023 to December 2024. Summary of failures of these equipment is as below (Table-11). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | i. As reported to CEA total 4 Nos. of Wave Trap, 3 Nos. of Coupling Capacitor, 3 Nos. of Disconnector/Isolator, 1 No. of GIS Bay, 1 No. of Cable and 1 No. of PASS Module failed between July 2023 to December 2024. Summary of failures of these equipment is as below (Table-11). | 220 kV and above voltage class substation equipment | PDF p. 50 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0105 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, CVT, Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | i. It is observed that reported failures are primarily due to the following reasons: a) Normal Ageing b) Improper Erection c) Failure of Insulation system for CB/CT/PT/CVT/SA. d) Failure of Insulation system & Bushing for Transformers & Reactors. e) Lack of prudent maintenance practices f) Frequent System Faults and transient over voltages generated by the system. ii. In most of the failure cases of CT/PT/CVT/SA, equipment blasted or got completely damaged making it impossible to carry out any test after failure. Without tests, internal condition of the failed equipment cannot be assessed and cause of failure cannot be determined. However, in most of the cases it is assumed that degradation of insulation due to ingress of moisture and transient system voltages might be the reason of failure of these equipment. iii. As the utilities have been intimating failure events to CEA with extended delay times, the required site visits could not be undertaken by the Committee. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | i. It is observed that reported failures are primarily due to the following reasons: a) Normal Ageing b) Improper Erection c) Failure of Insulation system for CB/CT/PT/CVT/SA. d) Failure of Insulation system & Bushing for Transformers & Reactors. e) Lack of prudent maintenance practices f) Frequent System Faults and transient over voltages generated by the system. ii. In most of the failure cases of CT/PT/CVT/SA, equipment blasted or got completely damaged making it impossible to carry out any test after failure. Without tests, internal condition of the failed equipment cannot be assessed and cause of failure cannot be determined. However, in most of the cases it is assumed that degradation of insulation due to ingress of moisture and transient system voltages might be the reason of failure of these equipment. iii. As the utilities have been intimating failure events to CEA with extended delay times, the required site visits could not be undertaken by the Committee. | 220 kV and above voltage class substation equipment | PDF p. 51 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0106 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | iv. Condition Based Maintenance (CBM) Practices using modern diagnostic tools is yet to be adopted in large scale by many utilities, and in general, periodic Time Based Maintenance (TBM) is still being practiced. Adequate modern Diagnostic tools are also not available with most of the State Utilities. | NOT COVERED | ic tools is yet to be adopted in large scale by many utilities, and in general, periodic Time Based Maintenance (TBM) is still being practiced | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 51 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0107 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | v. Sometimes due to unavailability of shut down, maintenance of equipment is deferred which affects the efficient functioning of the equipment and further deteriorate the health of equipment. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 51 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0108 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | vi. In most cases of the failures, utilities do not furnish factory test reports, pre-commissioning test reports, history of O&M & repairs, relay settings, environmental & system conditions at the time of failure etc. which makes it very difficult to analyze the cause of failure. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. In most cases of the failures, utilities do not furnish factory test reports, pre-commissioning test reports, history of O&M & repairs, relay settings, environmental & system conditions at the time of failure etc. which makes it very difficult to analyze the cause of failure. | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0109 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | vii. In case of failure of transformers and reactors, report of detailed internal inspection carried out by the Original Equipment Manufacturer (OEM) at site or at its works are not provided. 6 Recommendations | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vii. In case of failure of transformers and reactors, report of detailed internal inspection carried out by the Original Equipment Manufacturer (OEM) at site or at its works are not provided. 6 Recommendations | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0110 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 1) All the utilities should furnish preliminary information of failure of substation | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 1) All the utilities should furnish preliminary information of failure of substation | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0111 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | equipment of 220 kV and above voltage class within 48 hours of the occurrence of the failure and detailed report within a Month in the prescribed format available at Annexure-IV and also on CEA website. The report should accompany tests carried out after failure, test reports and details of previous maintenance, pre-commissioning test reports, and photographs of the failed equipment. | NOT COVERED | NOT VERIFIED | 220 kV; 48 hours | NOT COVERED | equipment of 220 kV and above voltage class within 48 hours of the occurrence of the failure and detailed report within a Month in the prescribed format available at Annexure-IV and also on CEA website. The report should accompany tests carried out after failure, test reports and details of previous maintenance, pre-commissioning test reports, and photographs of the failed equipment. | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0112 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | the failure of equipment, even if the warranty has expired, which may help the manufacturers to take corrective action for improving the product design. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | the failure of equipment, even if the warranty has expired, which may help the manufacturers to take corrective action for improving the product design. | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0113 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | tools should be followed instead of conventional Periodic / Time-Based Maintenance. A list of diagnostic tools is given in CEA Grid Standard regulation which can be used for one substation or a pool of substations depending upon requirement. | NOT COVERED | tools should be followed instead of conventional Periodic / Time-Based Maintenance | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0114 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS, AIS | NOT VERIFIED | Maintenance Schedule | GIS | SCHEDULE | Medium voltage and high voltage electrical assets like GIS, AIS, Breakers, Power Cables including Transformers for condition based maintenance. All FAT, SAT and Periodic testing data for all electrical equipment shall be stored in this system for performing health assessment. The system shall have advanced health index models that utilizes analytics and threshold limits as prescribed by latest IEEE, IEC, and CIGRE standards / recommendations. This system shall also be capable of integrating online monitoring of sensors installed at electrical | NOT COVERED | All FAT, SAT and Periodic testing data for all electrical equipment shall be stored in this system for performing health asse | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 52 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0115 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Installation | DGA | INSTALLATION | assets, and inspection records/reports from the visual inspection of assets. It shall have the capabilities to monitor DGA, Partial discharge – Electrical & UHF, bushing, fan control, fiber optic monitoring and other monitoring parameters. This system shall support cloud and on-premise installation and provide access to electrical asset health dashboards at engineer’s PC, Mobile, Laptops or tablets. 6) Condition monitoring as mentioned in Standard specifications and technical | assets, and inspection records/reports from the visual inspection of assets. It shall have the capabilities to monitor DGA, Partial discharge – Electrical & UHF, bushing, fan control, fiber optic monitoring and other monitoring parameters. This system shall support cloud and on-premise installation and provide access to electrical asset health dashboards at engineer’s PC, Mobile, Laptops or tablets. 6) Condition monitoring as mentioned in Standard specifications and technical | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0116 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | parameters for transformers and reactors (66 kV & above voltage class) CEA standard shall be adopted. 7) The frequency/ periodicity of measurement should be changed depending on | NOT COVERED | NOT VERIFIED | 66 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0117 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | the condition/ healthiness of the equipment in operation. The trend of test results should be monitored rather than the absolute values of test results. | the condition/ healthiness of the equipment in operation. The trend of test results should be monitored rather than the absolute values of test results. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0118 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | 8) Utilities should follow the best practices for maintenance of each equipment. | 8) Utilities should follow the best practices for maintenance of each equipment. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0119 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Installation | Installation | INSTALLATION | electrical equipment at sites one or two months prior to expiry of warranty period of respective equipment so that any abnormality observed in test results can be discussed with OEM for taking up further necessary action within warranty period. 10) The utilities must be careful during installation of transformers at site and long | electrical equipment at sites one or two months prior to expiry of warranty period of respective equipment so that any abnormality observed in test results can be discussed with OEM for taking up further necessary action within warranty period. 10) The utilities must be careful during installation of transformers at site and long | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0120 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | transformer uncharged in the yard for long time before putting in to service. The OEM’s recommendation for storage should be followed strictly. Spare equipment should be periodically tested as per OEM’s recommendation. 12) Utilities should take appropriate actions for repair/ replacement of concerned | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0121 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | equipment as soon as some abnormality is observed through visual inspection or diagnostic tests. 13) Frequent failures of equipment of any particular make should be thoroughly | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | equipment as soon as some abnormality is observed through visual inspection or diagnostic tests. 13) Frequent failures of equipment of any particular make should be thoroughly | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0122 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | operation & maintenance of sub-station equipment. The manpower should be strengthened for efficient operation & maintenance. 15) The regular cleaning of dust deposited on the housings of major equipment and | operation & maintenance of sub-station equipment. The manpower should be strengthened for efficient operation & maintenance. 15) The regular cleaning of dust deposited on the housings of major equipment and | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 53 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0123 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, CVT, Bushing, Substation | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | across the insulators, as such frequent flashover across the bushing / housing of equipment (due to operation in such dusty environment) may lead to failure of equipment. Wherever feasible, the porcelain housings of major equipment (CB/LA/CT/CVT) and bushings of transformer may be protected by providing Room Temperature Vulcanisation (RTV) coating. RTV coating over porcelain housing of equipment (CB/LA/CT/CVT) / bushings of transformer & reactors may also be considered by utilities for substation equipment installed in pollution prone areas. 16) Utilities should create and maintain complete database of equipment/transformers including previous test reports (reports of factory tests/pre-commissioning tests/tests during O&M etc.), operation & maintenance history of equipment with make, model & year of commissioning etc. for proper evaluation, interpretation of test results and for taking Run-Refurbish-Replacement decision. 17) However, merely maintaining the history of O&M is not sufficient. Test results | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | across the insulators, as such frequent flashover across the bushing / housing of equipment (due to operation in such dusty environment) may lead to failure of equipment. Wherever feasible, the porcelain housings of major equipment (CB/LA/CT/CVT) and bushings of transformer may be protected by providing Room Temperature Vulcanisation (RTV) coating. RTV coating over porcelain housing of equipment (CB/LA/CT/CVT) / bushings of transformer & reactors may also be considered by utilities for substation equipment installed in pollution prone areas. 16) Utilities should create and maintain complete database of equipment/transformers including previous test reports (reports of factory tests/pre-commissioning tests/tests during O&M etc.), operation & maintenance history of equipment with make, model & year of commissioning etc. for proper evaluation, interpretation of test results and for taking Run-Refurbish-Replacement decision. 17) However, merely maintaining the history of O&M is not sufficient. Test results | 220 kV and above voltage class substation equipment | PDF p. 54 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0124 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Installation | INSTALLATION | are not useful if correct method of testing is not followed. All tests and maintenance should be carried out as per best practices. The method of testing as well as the conditions while conducting the tests should be consistent / identical to previous testing condition as far as possible. For example, test voltage, tap position at which test is conducted, etc., should be maintained while measuring IR or Turns Ratio, or conducting SFRA and other similar tests. Details of test kits, should be maintained so that the test results can be compared with subsequent test results. For variation in temperature, required correction factors could be incorporated. Calibration of the testing instruments should be ensured for reliability of the assessment. 18) Utilities should explore the possibility of installation of CCTV cameras in the | are not useful if correct method of testing is not followed. All tests and maintenance should be carried out as per best practices. The method of testing as well as the conditions while conducting the tests should be consistent / identical to previous testing condition as far as possible. For example, test voltage, tap position at which test is conducted, etc., should be maintained while measuring IR or Turns Ratio, or conducting SFRA and other similar tests. Details of test kits, should be maintained so that the test results can be compared with subsequent test results. For variation in temperature, required correction factors could be incorporated. Calibration of the testing instruments should be ensured for reliability of the assessment. 18) Utilities should explore the possibility of installation of CCTV cameras in the | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 54 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0125 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation, Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | substation, covering transformer area so that transformers could be monitored from the control room and any mishap with the transformer could be recorded for further analysis. It would also help to determine the point of initiation and actual cause in case of fire in transformer. 19) If any damaged equipment is sent to the manufacturer’s works for repair, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 54 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0126 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | detailed investigation report including probable causes of failure should be submitted to the Standing Committee for benefit of the other utilities. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | detailed investigation report including probable causes of failure should be submitted to the Standing Committee for benefit of the other utilities. | 220 kV and above voltage class substation equipment | PDF p. 54 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0127 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | Commissioning | SCHEDULE | commissioning of the transformers/ reactors, proper care must be taken to ensure satisfactory operation of transformer/ reactor. Storage and periodic testing of transformer/ reactor should be done as per manufacturer’s recommendations. 5) Transformer/ reactors should not be kept for more than three (3) months | NOT COVERED | Storage and periodic testing of transformer/ reactor should be done as per manufacturer’s recommendations | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0128 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | with dry air/inert gas (Nitrogen) filling and all throughout the period, required pressure needs to be maintained in order to avoid the exposure of active part to atmosphere. After three (3) months, transformer/ reactor should be filled with oil under vacuum and it should be provided with oil conservator including oil level indicator and breather. The oil parameters need to be monitored regularly. 6) As far as possible the transformer/ reactor should be transported filled with | with dry air/inert gas (Nitrogen) filling and all throughout the period, required pressure needs to be maintained in order to avoid the exposure of active part to atmosphere. After three (3) months, transformer/ reactor should be filled with oil under vacuum and it should be provided with oil conservator including oil level indicator and breather. The oil parameters need to be monitored regularly. 6) As far as possible the transformer/ reactor should be transported filled with | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0129 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | dry air. Use of nitrogen for this purpose should be avoided. 7) The height of the fire wall between two transformers/reactors should be at | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0130 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | least 600 mm above the highest point of the transformer and fire wall should be rated for four-hour fire rating so that fire in one transformer/reactor does not affect adjacent transformers/ reactor. 8) Whenever there is movement of transformer either from manufacturing | NOT COVERED | NOT VERIFIED | 600 mm | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0131 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | works or from one station to other, Sweep frequency response analysis (SFRA) should be carried out before movement and after shifting to new location and in case of any discrepancy, OEM may be contacted. SFRA signature would provide valuable information about deformation in winding /core during transportation. 9) On Load Tap Changer (OLTC) is one of the contributors to the failure of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | works or from one station to other, Sweep frequency response analysis (SFRA) should be carried out before movement and after shifting to new location and in case of any discrepancy, OEM may be contacted. SFRA signature would provide valuable information about deformation in winding /core during transportation. 9) On Load Tap Changer (OLTC) is one of the contributors to the failure of | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0132 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | transformer. Possibility of eliminating OLTC from 400 kV & 765 kV class transformer should be considered (based on system studies) in consultation with Regional Power Committee (RPC) and Regional Load Despatch Centre (RLDC)/Grid-India and CEA. The reduction in in number of taps/steps can also be considered in case of OLTC of 220 kV and below voltage class transformers. The removal of OLTC will simplify the design and manufacturing of transformers. 10) Tertiary winding should be avoided, wherever feasible, as it increases the | NOT COVERED | NOT VERIFIED | 400 kV; 765 kV; 220 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0133 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | probability of failure of the transformer. Tertiary terminals of transformer prone to short circuiting by external element such as bird or animal may be suitably insulated. 11) Transformer should be subjected to short circuit withstand test as per | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | probability of failure of the transformer. Tertiary terminals of transformer prone to short circuiting by external element such as bird or animal may be suitably insulated. 11) Transformer should be subjected to short circuit withstand test as per | 220 kV and above voltage class substation equipment | PDF p. 55 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0134 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Inspection | FAILURE_ANALYSIS | Lines), 2022 Regulations, to verify its capability to withstand dynamic effect of short circuit. The design review of the transformers should be carried out properly before commencement of manufacturing. Stage inspection should also be carried out to check manufacturing process as well as quality of material used in subsequent transformers. 12) An internal inspection of the failed transformer on-site is warranted at times | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Lines), 2022 Regulations, to verify its capability to withstand dynamic effect of short circuit. The design review of the transformers should be carried out properly before commencement of manufacturing. Stage inspection should also be carried out to check manufacturing process as well as quality of material used in subsequent transformers. 12) An internal inspection of the failed transformer on-site is warranted at times | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0135 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Inspection | SAFETY | to locate fault inside the transformer and to assess the extent of damage. As far as possible, internal inspection should be carried out in association with OEM / in presence of representative of OEM. All safety precautions must be observed at all times. Internal inspection must be performed by experienced staff with proper training. The internal inspection should not cause any further damage to the transformer and precaution should be taken to prevent ingress of moisture and any foreign material into the transformer and hence internal inspection should be meticulously planned. 13) As far as possible, LV test and SFRA should be conducted after through fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | to locate fault inside the transformer and to assess the extent of damage. As far as possible, internal inspection should be carried out in association with OEM / in presence of representative of OEM. All safety precautions must be observed at all times. Internal inspection must be performed by experienced staff with proper training. The internal inspection should not cause any further damage to the transformer and precaution should be taken to prevent ingress of moisture and any foreign material into the transformer and hence internal inspection should be meticulously planned. 13) As far as possible, LV test and SFRA should be conducted after through fault | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0136 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | to check the integrity of the transformer. 14) The capacitance and tan delta measurement of transformer bushing at | to check the integrity of the transformer. 14) The capacitance and tan delta measurement of transformer bushing at | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0137 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | variable frequency and Dissolved gas analysis (DGA) of bushing oil should be carried out for health assessment of bushings as this has been proved to be very effective in assessing the condition of in-service bushings. 15) Residual Life Assessment (RLA) should be conducted for old and aged | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0138 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | transformers (approaching end of service life) for proper planning to replace them in stages. 16) Periodic oil testing including DGA (wherever feasible) in the case of | NOT COVERED | 16) Periodic oil testing including DGA (wherever feasible) in the case of | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0139 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CVT, Bushing | NOT VERIFIED | Maintenance Schedule | Tan Delta | SCHEDULE | instrument transformers are recommended. Health of gaskets and bellows needs to be checked periodically for CTs. Thermo-vision scanning of CTs, CVTs and PTs should also be carried out regularly as a good maintenance practice. 17) While measuring tan delta of transformer bushing/CT/PT/CVT, apart from | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0140 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | CVT | NOT VERIFIED | Maintenance Schedule | Tan Delta | SCHEDULE | absolute value, rate of rise of tan delta should also be monitored and it should not be more than 0.1% per year. Frequency of measurement should be increased in case tan delta value is approaching 0.7%. Following tables can be referred while measuring tan δ and capacitance of CVTs: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 56 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0141 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | CVT | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | bellows, the oil should be present up to the top of the bellows for proper functioning. The oil leakage needs to be checked periodically. Bellows level should be closely watched. The level of bellows of all CTs in one bay should be same at any point of time. Different bellows level may be an indicator of oil leakage, gassing or fault. Similarly, Capacitor units & EMU of CVTs in one bay should have same oil level indication at any point of time. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | bellows, the oil should be present up to the top of the bellows for proper functioning. The oil leakage needs to be checked periodically. Bellows level should be closely watched. The level of bellows of all CTs in one bay should be same at any point of time. Different bellows level may be an indicator of oil leakage, gassing or fault. Similarly, Capacitor units & EMU of CVTs in one bay should have same oil level indication at any point of time. | 220 kV and above voltage class substation equipment | PDF p. 57 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0142 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | suitable corrective measures such as splitting of bus or employment of fault limiting devices should be adopted. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | suitable corrective measures such as splitting of bus or employment of fault limiting devices should be adopted. | 220 kV and above voltage class substation equipment | PDF p. 58 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0143 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Insulation Resistance | TESTING | a very good method for assessing healthiness of SA. If 3rd harmonic component of resistive current is more than 150 µA, then Insulation Resistance (IR) value test should also be conducted and if current exceeds 350 µA, then SA should be removed from service and replaced. The measurement of leakage current before and after the monsoon should be carried out so as to ascertain the effect of moisture. | a very good method for assessing healthiness of SA. If 3rd harmonic component of resistive current is more than 150 µA, then Insulation Resistance (IR) value test should also be conducted and if current exceeds 350 µA, then SA should be removed from service and replaced. The measurement of leakage current before and after the monsoon should be carried out so as to ascertain the effect of moisture. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 58 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0144 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Surge Arrester | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | should be ensured that there is no damage during erection. If SA is kept on an uneven surface, it is likely to damage the pressure relief diaphragm. Any damage to this thin & sensitive material while handling & erecting will result into moisture entry into Surge Arrester, which will lead to its failure. 3) Thermal scanning is another simple on-line check often used on SAs to locate | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | should be ensured that there is no damage during erection. If SA is kept on an uneven surface, it is likely to damage the pressure relief diaphragm. Any damage to this thin & sensitive material while handling & erecting will result into moisture entry into Surge Arrester, which will lead to its failure. 3) Thermal scanning is another simple on-line check often used on SAs to locate | 220 kV and above voltage class substation equipment | PDF p. 58 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0145 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker, Substation | NOT VERIFIED | Testing | Circuit Breaker | TESTING | important tool to assess the healthiness of circuit breaker. This test may be carried out once in two years. Moreover, while formulating the specification for procurement of CB for new substation, provision for procurement of Operational Analyzer along with Dynamic Contact Resistance Measurement (DCRM) test kit should be included for one substation or a group of nearby substations depending upon the requirement. | important tool to assess the healthiness of circuit breaker. This test may be carried out once in two years. Moreover, while formulating the specification for procurement of CB for new substation, provision for procurement of Operational Analyzer along with Dynamic Contact Resistance Measurement (DCRM) test kit should be included for one substation or a group of nearby substations depending upon the requirement. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 58 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0146 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: 24242 vii. Date and time of occurrence of fault: 25-05-2024 at 20:12 Hrs, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: 24242 vii. Date and time of occurrence of fault: 25-05-2024 at 20:12 Hrs, | 220 kV and above voltage class substation equipment | PDF p. 73 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0147 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: 140020-1 vii. Date and time of occurrence of fault: 28-03-2024 at 05:24 Hrs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: 140020-1 vii. Date and time of occurrence of fault: 28-03-2024 at 05:24 Hrs. | 220 kV and above voltage class substation equipment | PDF p. 76 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0148 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | ix. Year of Manufacturing: 1977 x. Date of Commissioning: 19.09.1979 xi. Sequence of events/Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ix. Year of Manufacturing: 1977 x. Date of Commissioning: 19.09.1979 xi. Sequence of events/Description of fault | 220 kV and above voltage class substation equipment | PDF p. 76 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0149 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | Tertiary Bushing and Neutral Bushing with Neutral CT and Tertiary Bus, Upper gantry with Disc Insulators and conductor were damaged completely. Due to severe heat the gaskets also got damaged. Also, the control cables entering the cabinets of unit 2, unit 1 and unit 3 were also burnt. The inner side photographs of the transformer T-2 taken after opening of inspection window shows | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Tertiary Bushing and Neutral Bushing with Neutral CT and Tertiary Bus, Upper gantry with Disc Insulators and conductor were damaged completely. Due to severe heat the gaskets also got damaged. Also, the control cables entering the cabinets of unit 2, unit 1 and unit 3 were also burnt. The inner side photographs of the transformer T-2 taken after opening of inspection window shows | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 76 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0150 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | complete burning of transformer winding of T/F T-2. Hence this T/F T-2 got completely brunt/damaged and is found to be non- repairable /re-usable. The healthiness of the T/F windings of the partially damaged unit T- I was checked after cooling down of T/F T-2 and found in order. Hence decision was taken to revive the ICT bank-1 by repairing 150 MVA T/F T-1 and the revival work is under progress and is likely to be completed by 27.04.2024. In place of damaged T/F T-2, spare unit T/F T- 7 will be used as yellow phase after isolating damaged T/F T-2. xii. Details of Tests done after failure | NOT COVERED | NOT VERIFIED | 150 MVA | NOT COVERED | complete burning of transformer winding of T/F T-2. Hence this T/F T-2 got completely brunt/damaged and is found to be non- repairable /re-usable. The healthiness of the T/F windings of the partially damaged unit T- I was checked after cooling down of T/F T-2 and found in order. Hence decision was taken to revive the ICT bank-1 by repairing 150 MVA T/F T-1 and the revival work is under progress and is likely to be completed by 27.04.2024. In place of damaged T/F T-2, spare unit T/F T- 7 will be used as yellow phase after isolating damaged T/F T-2. xii. Details of Tests done after failure | 220 kV and above voltage class substation equipment | PDF p. 77 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0151 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | equipment or visited the site after failure, their remarks, MoM etc. may be attached | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | equipment or visited the site after failure, their remarks, MoM etc. may be attached | 220 kV and above voltage class substation equipment | PDF p. 77 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0152 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | tripping and damaged/brunt completely and is not repairable/reusable. xvii. (a) Details of previous maintenance | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 77 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0153 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | these tests. If yes, attach the test reports. (c) What steps were taken to address the | these tests. If yes, attach the test reports. (c) What steps were taken to address the | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 77 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0154 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 3. Failure report of 105 MVA, 400/220/33 kV Auto Transformer at 400 kV Khedamara, S/s of CSPTCL | NOT COVERED | NOT VERIFIED | 105 MVA; 33 kV; 400 kV | NOT COVERED | 3. Failure report of 105 MVA, 400/220/33 kV Auto Transformer at 400 kV Khedamara, S/s of CSPTCL | 220 kV and above voltage class substation equipment | PDF p. 80 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0155 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | ix. Year of Manufacturing: 2022-2023 x. Date of Commissioning: 11.05.2024 xi. Sequence of events/ Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ix. Year of Manufacturing: 2022-2023 x. Date of Commissioning: 11.05.2024 xi. Sequence of events/ Description of fault | 220 kV and above voltage class substation equipment | PDF p. 80 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0156 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 1. Main 1 Differential Protection Operated 2. Main 2 Differential Protection Operated 3. REF Protection Operated 4. Main Buchholz B phase 5. PRV trip B phase 6. OTI trip B phase 7. WTI trip B phase xii. Details of test done after failure (What test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 1. Main 1 Differential Protection Operated 2. Main 2 Differential Protection Operated 3. REF Protection Operated 4. Main Buchholz B phase 5. PRV trip B phase 6. OTI trip B phase 7. WTI trip B phase xii. Details of test done after failure (What test | 220 kV and above voltage class substation equipment | PDF p. 80 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0157 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | were conducted after discovery of failure. If no tests were conducted, reason for the same may be stated) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | were conducted after discovery of failure. If no tests were conducted, reason for the same may be stated) | 220 kV and above voltage class substation equipment | PDF p. 80 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0158 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | OLTC Drive Mechanism Box were damaged by fire. 7. Drive mechanism box was fire-damaged. 8. Oil drained from bell cover joints. 9. Pipe lines of the High Velocity Water | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 81 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0159 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Spray System (Emulsifier system) were damaged by porcelain debris from the bushing burst. 10. Pipe lines of the NIFPS system were | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 81 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0160 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | 6008143) showed heavy pitting and flashover marks on the HV bushing's stress shield, metallic pipe structure, and wood structure supporting the HV lead. This indicated a breakdown of insulation, causing a phase-to-ground fault. 12. Photographs of HV lead and assembly | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 6008143) showed heavy pitting and flashover marks on the HV bushing's stress shield, metallic pipe structure, and wood structure supporting the HV lead. This indicated a breakdown of insulation, causing a phase-to-ground fault. 12. Photographs of HV lead and assembly | 220 kV and above voltage class substation equipment | PDF p. 81 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0161 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | during pre-erection showed a metallic pipe structure in Unit-1 but not in Units- 2 and -3. Additional haft paper and insulation sheets were observed on Unit- l's HV lead. 13. HV lead was disconnected from the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 81 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0162 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | copper bar inside the bushing without burnt marks on copper strands. 14. Heavy burnt mark & damage observed | NOT COVERED | NOT VERIFIED | NOT VERIFIED | copper bar inside the bushing without burnt marks on copper strands. 14. Heavy burnt mark & damage observed | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 81 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0163 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | on HV lead takeoff point from winding. xiv. Probable cause of failure: Flashover between HV line lead and its metallic pipe transport support leading to bursting of 400 kV bushing ROOT CAUSE ANALYSIS OF FAILURE Post failure inspection of transformer carried out at site and at BHEL Bhopal works. It was found that active part of the transformer is intact. No deformation / damage observed in core and windings of the transformer. Tapping lead connection also found in order. Various low voltage tests carried out at BHEL works were found satisfactorily. Transformer has failed on occurrence of phase to ground fault which took place due to | NOT COVERED | NOT VERIFIED | 400 kV | NOT COVERED | on HV lead takeoff point from winding. xiv. Probable cause of failure: Flashover between HV line lead and its metallic pipe transport support leading to bursting of 400 kV bushing ROOT CAUSE ANALYSIS OF FAILURE Post failure inspection of transformer carried out at site and at BHEL Bhopal works. It was found that active part of the transformer is intact. No deformation / damage observed in core and windings of the transformer. Tapping lead connection also found in order. Various low voltage tests carried out at BHEL works were found satisfactorily. Transformer has failed on occurrence of phase to ground fault which took place due to | 220 kV and above voltage class substation equipment | PDF p. 81 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0164 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | flashover between HV line lead and its metallic pipe transport support. Due to arcing in oil, pressure buildup inside the transformer and causing welding cracks of tank and damage of HV line lead. Generally metallic support structure is used to secure HV lead during transportation which was supposed to be removed during erection. However, this support was remained unnoticed & left inadvertently after erection of bushing. xv. Present condition of equipment (Whether | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 82 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0165 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | (Activities carried out in previous maintenance including the tests conducted, periodicity of the maintenance activities) b) Whether any abnormality observed in these tests. If yes attach the test reports c) What steps were taken to address the abnormality? | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 82 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0166 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | xxvi. Past record of Operation of OLTC: NA - New equipment xxvii. Tap Range: Tap 1 to Tap 17 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 82 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0167 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Tan Delta | SCHEDULE | Oil sample (22.08.2024) b) Capacitance and Tan delta (24.08.2024) c) Frequency Response analysis (SFRA), 24.08.2024) d) Magnetic balance & Magnetizing current | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 84 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0168 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | xxvi. Tap position OLTC at the time of failure: 5 (Normal Tap) xxvii. Past record of Operation of OLTC | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxvi. Tap position OLTC at the time of failure: 5 (Normal Tap) xxvii. Past record of Operation of OLTC | 220 kV and above voltage class substation equipment | PDF p. 85 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0169 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | xxxviii. Whether short circuits test carried out on this transformer or same design transformer or short circuit withstand capability was verified on the basis of calculation | xxxviii. Whether short circuits test carried out on this transformer or same design transformer or short circuit withstand capability was verified on the basis of calculation | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 86 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0170 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Insulation Resistance | TESTING | Post tripping various tests has been carried out. Observations are as under:- DC Winding Resistance Test:- These results are in permissible range. INSULATION RESISTANCE TEST: IR Test conducted at 5 kV Insulation Tester. The IR Value between HV and MV winding observed in Giga Ohm with PI of 1.52. | Post tripping various tests has been carried out. Observations are as under:- DC Winding Resistance Test:- These results are in permissible range. INSULATION RESISTANCE TEST: IR Test conducted at 5 kV Insulation Tester. The IR Value between HV and MV winding observed in Giga Ohm with PI of 1.52. | NOT VERIFIED | 5 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 86 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0171 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | The IR Value between HV and Earth observed in Mega Ohm with PI of 1.38. The IR Value between MV and LV observed in Mega Ohm only with PI of 1.70 The IR Value between MV and Earth observed in Gega Ohm with PI of 1.41 The IR Value between LV and Earth observed in Mega Ohm only with PI of 1.70 The IR Value between LV and HV observed in Gega Ohm with PI of 1.43 DGA Test:- Post tripping results of DGA done on 22.08.2024 has shown Acetylene (C2H2 ) of the order of 58.1 ppm as compared to 0.5 ppm of 1st prior results done on 24.06.2024. | The IR Value between HV and Earth observed in Mega Ohm with PI of 1.38. The IR Value between MV and LV observed in Mega Ohm only with PI of 1.70 The IR Value between MV and Earth observed in Gega Ohm with PI of 1.41 The IR Value between LV and Earth observed in Mega Ohm only with PI of 1.70 The IR Value between LV and HV observed in Gega Ohm with PI of 1.43 DGA Test:- Post tripping results of DGA done on 22.08.2024 has shown Acetylene (C2H2 ) of the order of 58.1 ppm as compared to 0.5 ppm of 1st prior results done on 24.06.2024. | NOT VERIFIED | 58.1 ppm; 0.5 ppm | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 87 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0172 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Hydrogen increased from 09 ppm (24.06.24) to 1058 ppm (22.08.2024) Carbon Mono-oxide CO increased from 62 ppm (24.06.24) to 184 ppm (22.08.2024) Magnetising Current and balance:- It has been noticed that magnetising current of B phase is in the order of Ampere whereas magnetising current of R and Y-Ph winding is in the order of mili-ampere and when tested from HV side also, LV side magnetic balance showing similar results. No induction in B-phase when R and Y phases is energized. Magnetic balance of tertiary winding also showing abnormal results as complete voltage is not building when excited between Y-B phases. TTR Test:- Slightly Deviation observed in TTR at various taps in B- Ph (220 kV-66 kV) and No deviation observed in (220 kV-11 kV) windings of the transformer. | Hydrogen increased from 09 ppm (24.06.24) to 1058 ppm (22.08.2024) Carbon Mono-oxide CO increased from 62 ppm (24.06.24) to 184 ppm (22.08.2024) Magnetising Current and balance:- It has been noticed that magnetising current of B phase is in the order of Ampere whereas magnetising current of R and Y-Ph winding is in the order of mili-ampere and when tested from HV side also, LV side magnetic balance showing similar results. No induction in B-phase when R and Y phases is energized. Magnetic balance of tertiary winding also showing abnormal results as complete voltage is not building when excited between Y-B phases. TTR Test:- Slightly Deviation observed in TTR at various taps in B- Ph (220 kV-66 kV) and No deviation observed in (220 kV-11 kV) windings of the transformer. | NOT VERIFIED | 09 ppm; 1058 ppm; 62 ppm; 184 ppm; 220 kV; 66 kV; 11 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 87 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0173 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Safety | Tan Delta | SAFETY | Capacitance and Tan Delta test:- No major noticeable change in Winding / Bushing Tan Delta / Capacitance values has been observed within permissible limits. Tan Delta kit tripped for B-phase when Excitation current measured at 10 kV to 500 V on HV side. At the time of Testing Oil in Tank was at normal level. | NOT COVERED | NOT VERIFIED | 10 kV; 500 V | Capacitance and Tan Delta test:- No major noticeable change in Winding / Bushing Tan Delta / Capacitance values has been observed within permissible limits. Tan Delta kit tripped for B-phase when Excitation current measured at 10 kV to 500 V on HV side. At the time of Testing Oil in Tank was at normal level. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 87 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0174 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Bushing | NOT VERIFIED | Inspection | OLTC | INSPECTION | SFRA Test:- The graphs are mismatching to that of previous test results. Physical internal inspection was carried out by O&M team on 26 September 2024 Internal inspection of the transformer carried out and inspected all the power circuit area like OLTC Tap leads, Bushing leads, outside of the windings and core areas. However, nowhere blackish, burnt type things have been noticed. Bushing connections have been found to be ok. The insulation applied on the lead (tap) and connections leads of bushing found to be brownish due to ageing | SFRA Test:- The graphs are mismatching to that of previous test results. Physical internal inspection was carried out by O&M team on 26 September 2024 Internal inspection of the transformer carried out and inspected all the power circuit area like OLTC Tap leads, Bushing leads, outside of the windings and core areas. However, nowhere blackish, burnt type things have been noticed. Bushing connections have been found to be ok. The insulation applied on the lead (tap) and connections leads of bushing found to be brownish due to ageing | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 88 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0175 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 5. Failure report of 150 MVA, 220/132/33 kV Auto Transformer at Barjora S/s of DVC | NOT COVERED | NOT VERIFIED | 150 MVA; 33 kV | NOT COVERED | 5. Failure report of 150 MVA, 220/132/33 kV Auto Transformer at Barjora S/s of DVC | 220 kV and above voltage class substation equipment | PDF p. 89 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0176 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 1. During the magnetic balance test when voltage applied in Y-Phase the voltage induced in R & B- | 1. During the magnetic balance test when voltage applied in Y-Phase the voltage induced in R & B- | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 89 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0177 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Winding Resistance | TESTING | phase should be 50% of voltage applied in Y-Phase and sum of induced voltage of R & B should be equal to applied voltage in Y-Phase. But test report shows that when 233.1 volts applied on Y-phase, voltage induced in R & B-phases are very small (approximately 4.76% in R-phase and 3.72 % in B- Phase) and also sum so induced voltages in R & B-phases are 19.78 V which is very less than the applied voltage in Y-phase. Current drawn in Y-phase is very less compared to R & B-phase. 2. Magnetizing current drawn in Y-Phase (HV side) is very less compared to R & B-phase. 3. Y-Phase winding resistance is very low compared to R & B-Phases (% deviation in winding resistance | phase should be 50% of voltage applied in Y-Phase and sum of induced voltage of R & B should be equal to applied voltage in Y-Phase. But test report shows that when 233.1 volts applied on Y-phase, voltage induced in R & B-phases are very small (approximately 4.76% in R-phase and 3.72 % in B- Phase) and also sum so induced voltages in R & B-phases are 19.78 V which is very less than the applied voltage in Y-phase. Current drawn in Y-phase is very less compared to R & B-phase. 2. Magnetizing current drawn in Y-Phase (HV side) is very less compared to R & B-phase. 3. Y-Phase winding resistance is very low compared to R & B-Phases (% deviation in winding resistance | NOT VERIFIED | 19.78 V | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 89 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0178 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | between R & Y-phase=974.57% & between Y & B-phase is 974.47%). 4. No continuity in HV side between Y-Phase to R-Phase, Y-Phase to B-Phase & Y-Phase to Neutral. 5. The fault current in Y-Phase at the time of tripping was 22.27 kA. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | between R & Y-phase=974.57% & between Y & B-phase is 974.47%). 4. No continuity in HV side between Y-Phase to R-Phase, Y-Phase to B-Phase & Y-Phase to Neutral. 5. The fault current in Y-Phase at the time of tripping was 22.27 kA. | 220 kV and above voltage class substation equipment | PDF p. 89 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0179 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. Probable cause of failure: Internal fault xv. If OEM representative had inspected the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. Probable cause of failure: Internal fault xv. If OEM representative had inspected the | 220 kV and above voltage class substation equipment | PDF p. 90 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0180 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | xxvi. Tap position of OLTC at the time of failure: 9B th position ( Normal Position) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxvi. Tap position of OLTC at the time of failure: 9B th position ( Normal Position) | 220 kV and above voltage class substation equipment | PDF p. 91 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0181 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 6. Failure report of MVA2 20/66 kV Power Transformer at Morbi Substation of GETCO | NOT COVERED | NOT VERIFIED | 66 kV | NOT COVERED | 6. Failure report of MVA2 20/66 kV Power Transformer at Morbi Substation of GETCO | 220 kV and above voltage class substation equipment | PDF p. 93 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0182 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: PT-8011 vii. Date and time of occurrence of fault: 31.07.2024 23:52 Hrs | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: PT-8011 vii. Date and time of occurrence of fault: 31.07.2024 23:52 Hrs | 220 kV and above voltage class substation equipment | PDF p. 93 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0183 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | General | SAFETY | Transformer tripped after the clearance of 66 kV Morbi – Bela line 3 (UG cable) fault. High intensity Ph-G fault took place in 66 kV line which was cleared by protective system of 66 kV line | NOT COVERED | NOT VERIFIED | 66 kV | Transformer tripped after the clearance of 66 kV Morbi – Bela line 3 (UG cable) fault. High intensity Ph-G fault took place in 66 kV line which was cleared by protective system of 66 kV line | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 94 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0184 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | General | SAFETY | After above incident, fault developed in transformer and tripped in differential and buchholz trip. It seems that after the clearance of UG cable line fault well within time, transformer LV winding could not withstand recovery voltage which lead to damage to LV winding insulation. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | After above incident, fault developed in transformer and tripped in differential and buchholz trip. It seems that after the clearance of UG cable line fault well within time, transformer LV winding could not withstand recovery voltage which lead to damage to LV winding insulation. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 94 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0185 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 7. Failure report of 160 MVA 220/66 kV Power Transformer at Jambuva Substation of GETCO | NOT COVERED | NOT VERIFIED | 160 MVA; 66 kV | NOT COVERED | 7. Failure report of 160 MVA 220/66 kV Power Transformer at Jambuva Substation of GETCO | 220 kV and above voltage class substation equipment | PDF p. 97 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0186 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 8. Failure report of 315 MVA, 400/220/132 kV ICT at Kabulpur of Jhajjar KT Transco Pvt. Ltd (IndiGrid) | NOT COVERED | NOT VERIFIED | 315 MVA; 132 kV | NOT COVERED | 8. Failure report of 315 MVA, 400/220/132 kV ICT at Kabulpur of Jhajjar KT Transco Pvt. Ltd (IndiGrid) | 220 kV and above voltage class substation equipment | PDF p. 100 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0187 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | delayed directional over-current and earth fault relay (67 HV) of ICT 1 picked up. 3 Transformer differential protection relay | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | delayed directional over-current and earth fault relay (67 HV) of ICT 1 picked up. 3 Transformer differential protection relay | 220 kV and above voltage class substation equipment | PDF p. 100 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0188 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Circuit Breaker | NOT VERIFIED | Safety | Circuit Breaker | SAFETY | tripped the transformer ICT1. 6 ICT-1 400 kV side Circuit breaker opened. 7 ICT-1 220 kV side Circuit breaker opened. 8 B and R phase OSR and Main tank | NOT COVERED | NOT VERIFIED | 400 kV; 220 kV | tripped the transformer ICT1. 6 ICT-1 400 kV side Circuit breaker opened. 7 ICT-1 220 kV side Circuit breaker opened. 8 B and R phase OSR and Main tank | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 100 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0189 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | MVA ICT-1 is due to inter-turn shorting of winding conductor caused by weakening of insulation. • During earth fault in 220 kV line, | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | MVA ICT-1 is due to inter-turn shorting of winding conductor caused by weakening of insulation. • During earth fault in 220 kV line, | 220 kV and above voltage class substation equipment | PDF p. 101 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0190 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Transformer winding would have experienced forces and weak insulation of winding is damaged leading to short circuit in the winding. • Above failure was caused by excessive | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Transformer winding would have experienced forces and weak insulation of winding is damaged leading to short circuit in the winding. • Above failure was caused by excessive | 220 kV and above voltage class substation equipment | PDF p. 101 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0191 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | xxvi. Tap position of OLTC at the time of failure: Tap position – 10 xxvii. Past record of Operation of OLTC: 25-October-2016 (9b to 10) xxviii. Tap Range: 1 to 17 xxix. Details of Protection provided for ICT/ GT/ | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxvi. Tap position of OLTC at the time of failure: Tap position – 10 xxvii. Past record of Operation of OLTC: 25-October-2016 (9b to 10) xxviii. Tap Range: 1 to 17 xxix. Details of Protection provided for ICT/ GT/ | 220 kV and above voltage class substation equipment | PDF p. 102 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0192 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | Harmonic, and Earth fault, over current, Buchholz, PRV, OSR and WTI & OTI. xxx. Details of Protection operated: • 87 R - Differential protection Operated | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Harmonic, and Earth fault, over current, Buchholz, PRV, OSR and WTI & OTI. xxx. Details of Protection operated: • 87 R - Differential protection Operated | 220 kV and above voltage class substation equipment | PDF p. 102 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0193 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | • 64R- Restricted Earth fault relay protection Operated • PRV Operated • OSR Operated • Buchholz Relay Operated xxxi. Whether equipment is properly earthed: Yes xxxii. Earth Resistance of Substation and date of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | • 64R- Restricted Earth fault relay protection Operated • PRV Operated • OSR Operated • Buchholz Relay Operated xxxi. Whether equipment is properly earthed: Yes xxxii. Earth Resistance of Substation and date of | 220 kV and above voltage class substation equipment | PDF p. 102 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0194 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 9. Failure Report of 66.67 MVA, 220/110/33 kV Single phase Auto Transformer at Edappon substation | NOT COVERED | NOT VERIFIED | 66.67 MVA; 33 kV | NOT COVERED | 9. Failure Report of 66.67 MVA, 220/110/33 kV Single phase Auto Transformer at Edappon substation | 220 kV and above voltage class substation equipment | PDF p. 105 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0195 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 10. Failure report of 160 MVA, 220/132/33 kV Auto Transformer at Barwaha Substation of MPPTCL | NOT COVERED | NOT VERIFIED | 160 MVA; 33 kV | NOT COVERED | 10. Failure report of 160 MVA, 220/132/33 kV Auto Transformer at Barwaha Substation of MPPTCL | 220 kV and above voltage class substation equipment | PDF p. 108 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0196 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | ix. Year of Manufacturing: 2018 x. Date of Commissioning: 23-12-2018 xi. Sequence of events/ Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ix. Year of Manufacturing: 2018 x. Date of Commissioning: 23-12-2018 xi. Sequence of events/ Description of fault | 220 kV and above voltage class substation equipment | PDF p. 108 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0197 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | equipment or visited the site after failure their remarks, MoM etc. may be attached | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | equipment or visited the site after failure their remarks, MoM etc. may be attached | 220 kV and above voltage class substation equipment | PDF p. 108 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0198 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | a) Period of storage b) Idle charged or uncharged c) Dry air filled /Nitrogen filled / oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 110 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0199 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 11. Failure report of 50 MVA, 220/22 kV Power Transformer at Chinchwad-1 of MSETCL | NOT COVERED | NOT VERIFIED | 50 MVA; 22 kV | NOT COVERED | 11. Failure report of 50 MVA, 220/22 kV Power Transformer at Chinchwad-1 of MSETCL | 220 kV and above voltage class substation equipment | PDF p. 111 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0200 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 220 kV Bapgoan S/s under Vashi Zone & then transported to M/s Mahati Industries for repair. Again, the Transformer was failed at 220 kV Hinjewadi-2 S/s on dated 01/12/2021 & same was repaired by M/s Mahati Industries Ltd under GP & after repairs again commissioned at 220 kV Chinchwad-1 S/s on dated 12/09/2022. xix. Is tertiary winding provided (Yes/No): No | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 220 kV Bapgoan S/s under Vashi Zone & then transported to M/s Mahati Industries for repair. Again, the Transformer was failed at 220 kV Hinjewadi-2 S/s on dated 01/12/2021 & same was repaired by M/s Mahati Industries Ltd under GP & after repairs again commissioned at 220 kV Chinchwad-1 S/s on dated 12/09/2022. xix. Is tertiary winding provided (Yes/No): No | 220 kV and above voltage class substation equipment | PDF p. 112 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0201 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (d) Period of storage (e) Idle charged or uncharged (f) Dry air filled/Nitrogen filled/ Oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 113 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0202 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 12. Failure report of 50 MVA, 220 kV Power Transformer at Hinjewadi-1 Substation of MSETCL | NOT COVERED | NOT VERIFIED | 50 MVA; 220 kV | NOT COVERED | 12. Failure report of 50 MVA, 220 kV Power Transformer at Hinjewadi-1 Substation of MSETCL | 220 kV and above voltage class substation equipment | PDF p. 115 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0203 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | before commissioning:(a) Period of storage(b) Idle charged or uncharged(c) Dry air filled/Nitrogen filled/ Oil filled | before commissioning:(a) Period of storage(b) Idle charged or uncharged(c) Dry air filled/Nitrogen filled/ Oil filled | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 122 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0204 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 14. Failure report of 50 MVA, 220/33 kV, Power Transformer at Vankusawade Substation of MSETCL | NOT COVERED | NOT VERIFIED | 50 MVA; 33 kV | NOT COVERED | 14. Failure report of 50 MVA, 220/33 kV, Power Transformer at Vankusawade Substation of MSETCL | 220 kV and above voltage class substation equipment | PDF p. 122 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0205 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Safety | General | SAFETY | burst, both the power Transformers 1 & 3 tripped on LV backup protection. After isolating the faulty 33 kV Vankusawade Feeder-10, Transformers - 3 charged successfully whereas the 50 MVA Power Transformers -1 was again tripped with Relay indication- Buchholz Alarm & Trip. (Within 15 seconds of charging). However, it appears that there has been internal fault in the Transformer. | NOT COVERED | NOT VERIFIED | 33 kV; 50 MVA | burst, both the power Transformers 1 & 3 tripped on LV backup protection. After isolating the faulty 33 kV Vankusawade Feeder-10, Transformers - 3 charged successfully whereas the 50 MVA Power Transformers -1 was again tripped with Relay indication- Buchholz Alarm & Trip. (Within 15 seconds of charging). However, it appears that there has been internal fault in the Transformer. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 123 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0206 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 1. Internal Fault 2. Main Buchholz Alarm Relay Indication:- 3.Main Buchholz Trip 4. Main Buchholz Alarm | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 1. Internal Fault 2. Main Buchholz Alarm Relay Indication:- 3.Main Buchholz Trip 4. Main Buchholz Alarm | 220 kV and above voltage class substation equipment | PDF p. 124 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0207 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 15. Failure report of 100 MVA, 220/33 kV Power Transformer at Bothe S/s of MSETCL | NOT COVERED | NOT VERIFIED | 100 MVA; 33 kV | NOT COVERED | 15. Failure report of 100 MVA, 220/33 kV Power Transformer at Bothe S/s of MSETCL | 220 kV and above voltage class substation equipment | PDF p. 126 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0208 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: 610041 vii. Date and time of occurrence of fault: 04.06.2024 at 14:07 Hrs | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: 610041 vii. Date and time of occurrence of fault: 04.06.2024 at 14:07 Hrs | 220 kV and above voltage class substation equipment | PDF p. 126 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0209 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Safety | Failure | SAFETY | xiv. Probable cause of failure: Tripping of 33 kV Feeder-1 on OC because of heavy lightning on 33 kV Feeder-1 conductor and fault location is very near to substation. However, it appears that there has been internal fault in the Transformer. | NOT COVERED | NOT VERIFIED | 33 kV | xiv. Probable cause of failure: Tripping of 33 kV Feeder-1 on OC because of heavy lightning on 33 kV Feeder-1 conductor and fault location is very near to substation. However, it appears that there has been internal fault in the Transformer. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 126 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0210 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/ Nitrogen filled/ Oil filled | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 128 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0211 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 1. Differential Protection Operated 2. T/F internal fault. 3. Main Buchholz alarm. 4. Trip ckt faulty LV Bkr. 5. Problem in LV Bkr. 6. Master trip realy 86G.1 7. Auxiliary RCY for Trafo FUNCS(30AB) R/I:- LED- Differential Optd. Buchholz trip off Diff. trip B Diff Cur:- I diff -2148A Restr Cur:- I res - 3555A 729ms per Diff. Trip C Diff Cur:- I diff - 2148A Restr Cur:-I res- 2422A Buchholz alarm On CTR:- 1. Differential relay trip 2. T/F trip. xxvii. Whether equipment is properly earthed: Yes | NOT COVERED | NOT VERIFIED | 2148A; 3555A; 2422A | NOT COVERED | 1. Differential Protection Operated 2. T/F internal fault. 3. Main Buchholz alarm. 4. Trip ckt faulty LV Bkr. 5. Problem in LV Bkr. 6. Master trip realy 86G.1 7. Auxiliary RCY for Trafo FUNCS(30AB) R/I:- LED- Differential Optd. Buchholz trip off Diff. trip B Diff Cur:- I diff -2148A Restr Cur:- I res - 3555A 729ms per Diff. Trip C Diff Cur:- I diff - 2148A Restr Cur:-I res- 2422A Buchholz alarm On CTR:- 1. Differential relay trip 2. T/F trip. xxvii. Whether equipment is properly earthed: Yes | 220 kV and above voltage class substation equipment | PDF p. 131 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0212 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | ix. Year of Manufacturing: 2007-2008 (Repaired by M/s Mahati Industries Ltd in year 2024) x. Date of Commissioning: 28.06.2024 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 133 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0213 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. Probable cause of failure: Transformer internal fault. B phase fault current observed in DR is 20 kA at the time of fault. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. Probable cause of failure: Transformer internal fault. B phase fault current observed in DR is 20 kA at the time of fault. | 220 kV and above voltage class substation equipment | PDF p. 134 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0214 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | 1) Tripped on R Ph Fault current: Ia:2586.4 A 2) H/H tripped on R PH Ia: 2566.8 (Since then, feeder is under permit till date) | NOT COVERED | NOT VERIFIED | 2586.4 A | 1) Tripped on R Ph Fault current: Ia:2586.4 A 2) H/H tripped on R PH Ia: 2566.8 (Since then, feeder is under permit till date) | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 135 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0215 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 18. Failure Report of 50 MVA, 220/33 kV Power Transformer at Kurkumbh Substation of MSETCL | NOT COVERED | NOT VERIFIED | 50 MVA; 33 kV | NOT COVERED | 18. Failure Report of 50 MVA, 220/33 kV Power Transformer at Kurkumbh Substation of MSETCL | 220 kV and above voltage class substation equipment | PDF p. 136 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0216 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING | 1. IR test carried out; the results found in order. 2. Tan Delta & Capacitance test for winding carried out, all the results found in order. 3. In 10 kV Excitation tests, The R ph and B ph currents found doubled compared to previous results. | 1. IR test carried out; the results found in order. 2. Tan Delta & Capacitance test for winding carried out, all the results found in order. 3. In 10 kV Excitation tests, The R ph and B ph currents found doubled compared to previous results. | NOT VERIFIED | 10 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 136 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0217 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | For HV Y ph, kit tripped beyond 1.5 kV (190 mA). For LV Y ph, kit tripped beyond 25 V (185 mA) 4. Low voltage test carried out at tap No. 9. During the single phase magnetizing current | NOT COVERED | NOT VERIFIED | 1.5 kV; 190 mA; 25 V; 185 mA | For HV Y ph, kit tripped beyond 1.5 kV (190 mA). For LV Y ph, kit tripped beyond 25 V (185 mA) 4. Low voltage test carried out at tap No. 9. During the single phase magnetizing current | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 136 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0218 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | measurement test, High current observed for HV Y ph and LV Y ph. 5. The Magnetic balance test found disturbed. 6. Deviation observed in voltages measured during vector group tests. 7. DGA reports received on 21.08.2024 indicated presence of acetylene. | measurement test, High current observed for HV Y ph and LV Y ph. 5. The Magnetic balance test found disturbed. 6. Deviation observed in voltages measured during vector group tests. 7. DGA reports received on 21.08.2024 indicated presence of acetylene. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 136 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0219 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | a) For HV R ph and B ph HV open circuit test, the deviation observed below 3 kHz. b) For LV R ph and B ph open circuit test, the deviation observed below 3 kHz. c) For HV Y Ph open circuit test, the deviation observed below 1 kHz. d) For HV Y Ph open circuit test, the deviation observed below 1 kHz and from range 200 kHz to 1 MHz. As per the test results and observations, The Transformer declared as a faulty. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | a) For HV R ph and B ph HV open circuit test, the deviation observed below 3 kHz. b) For LV R ph and B ph open circuit test, the deviation observed below 3 kHz. c) For HV Y Ph open circuit test, the deviation observed below 1 kHz. d) For HV Y Ph open circuit test, the deviation observed below 1 kHz and from range 200 kHz to 1 MHz. As per the test results and observations, The Transformer declared as a faulty. | 220 kV and above voltage class substation equipment | PDF p. 137 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0220 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | tripped along with the 33 kV Shirsuphal feeder fault. The flame test carried out but could not conclusive as the small amount of gases had accumulated in the Buchholz. The differential Relay protection has operated correctly within time, no other protection operated. xxxi. Whether equipment is properly earthed: Yes | NOT COVERED | NOT VERIFIED | 33 kV | tripped along with the 33 kV Shirsuphal feeder fault. The flame test carried out but could not conclusive as the small amount of gases had accumulated in the Buchholz. The differential Relay protection has operated correctly within time, no other protection operated. xxxi. Whether equipment is properly earthed: Yes | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 138 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0221 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 19. Failure Report of 25 MVA, 220/33 kV Power Transformer at Purti Substation of MSETCL | NOT COVERED | NOT VERIFIED | 25 MVA; 33 kV | NOT COVERED | 19. Failure Report of 25 MVA, 220/33 kV Power Transformer at Purti Substation of MSETCL | 220 kV and above voltage class substation equipment | PDF p. 140 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0222 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | xxiv. Past record of operation of OLTC: Tap change operation was carried out as per | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 142 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0223 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Due to 100 MVA, 220/132 kV EMCO MAKE ICT 1, (Sr no. HT-1456/11937) tripped on Buchholz, PRV and Internal Fault, Also ICT body stiffener partially found cracked and Oil drain Out. 5) W/I: For ICT 1 Transformer Internal Fault, | NOT COVERED | NOT VERIFIED | 100 MVA; 132 kV | Due to 100 MVA, 220/132 kV EMCO MAKE ICT 1, (Sr no. HT-1456/11937) tripped on Buchholz, PRV and Internal Fault, Also ICT body stiffener partially found cracked and Oil drain Out. 5) W/I: For ICT 1 Transformer Internal Fault, | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 144 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0224 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | spread from bottom Bell Hardware and gasket from 132 kV Side & Minor from 220 kV Side. Internal Observation Of ICT: 1. Flash over on Bakelite OLTC drive shaft | NOT COVERED | NOT VERIFIED | 132 kV; 220 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 145 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0225 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | between Y and B phase due to failure of dielectric strength. 2. Drive shaft between R phase to Y Phase | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | between Y and B phase due to failure of dielectric strength. 2. Drive shaft between R phase to Y Phase | 220 kV and above voltage class substation equipment | PDF p. 145 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0226 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | arrangement found healthy, No flashover Observed on winding It Indicates winding seems to be healthy 6. Other than diverter switch, Inspection | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 145 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0227 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | Done found healthy xiv. Probable cause of failure: 1. Flash over on Bakelite OLTC drive shaft | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Done found healthy xiv. Probable cause of failure: 1. Flash over on Bakelite OLTC drive shaft | 220 kV and above voltage class substation equipment | PDF p. 145 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0228 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | 220 kV Ranjangaon substation. Removed from services from 220 kV Ranjangaon S/s in Augmentation scheme on dated 25.05.2010 2nd commissioning: On dated 31.07.2010 at 220 kV Alephata S/s. xix. Is tertiary winding provided (Yes/No): Yes | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 146 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0229 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | OSR relay, REF, Trip Circuit Supervision Relay, 86 master trip protection, PRV, CTR (N2 fire protection), Timer for 50 LBB, Auxiliary relay For Trans Non Trip, Auxiliary relay for Trans Trip, Auxiliary relay for CB Supervision relay LV: Trip Circuit supervision relay, LV Backup Relay, Stuck Breaker Protection Relay, Voltage Selection Relay, Master trip 86 Relay, Timer for 50 LBB, Colt Multi. Relay, DC supervision Relay, Auxiliary Relay. xxx. Details of Protection operated: Differential relay, Buchholz relay, PVR relay | NOT COVERED | NOT VERIFIED | NOT VERIFIED | OSR relay, REF, Trip Circuit Supervision Relay, 86 master trip protection, PRV, CTR (N2 fire protection), Timer for 50 LBB, Auxiliary relay For Trans Non Trip, Auxiliary relay for Trans Trip, Auxiliary relay for CB Supervision relay LV: Trip Circuit supervision relay, LV Backup Relay, Stuck Breaker Protection Relay, Voltage Selection Relay, Master trip 86 Relay, Timer for 50 LBB, Colt Multi. Relay, DC supervision Relay, Auxiliary Relay. xxx. Details of Protection operated: Differential relay, Buchholz relay, PVR relay | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 147 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0230 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Winding Resistance | TESTING | ppm acetylene which indicated arcing/flash-over in the tank. • The winding resistance for 1V-2V found | NOT COVERED | NOT VERIFIED | 1V; 2V | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 149 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0231 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | on higher side but the 2V-N test results show the results match with the previous, which indicates inter-turn shorting in the series winding of Y ph, i.e. between 1V-2V. • Magnetic Balance test shows unbalance. | on higher side but the 2V-N test results show the results match with the previous, which indicates inter-turn shorting in the series winding of Y ph, i.e. between 1V-2V. • Magnetic Balance test shows unbalance. | NOT VERIFIED | 2V; 1V | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 149 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0232 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | and 2V-N open circuit show shorting in Y ph winding. • Short circuit test shows rise in current | and 2V-N open circuit show shorting in Y ph winding. • Short circuit test shows rise in current | NOT VERIFIED | 2V | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 150 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0233 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Capacitance | TESTING | of Y-ph. Excitation test showed abnormally high current for HV Y-ph. • However, Tan-delta and capacitance | of Y-ph. Excitation test showed abnormally high current for HV Y-ph. • However, Tan-delta and capacitance | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 150 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0234 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | GAS/Oil Actuated Relay (Buchholz Relay), NIFPS, Over Temperature Prototection( HV & LV Winding, Oil), High Oil Pressure Release (PRV), OSR xxx. Details of Protection operated: Buchholz Relay | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 151 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0235 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 22. Failure report of 500 MVA, 400/220 kV ICT at Muzaffarnagar Substation of Powergrid | NOT COVERED | NOT VERIFIED | 500 MVA; 220 kV | NOT COVERED | 22. Failure report of 500 MVA, 400/220 kV ICT at Muzaffarnagar Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 153 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0236 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | towards 220 kV side. (v) 220 kV B & Y phase OLTC chamber i.e. diverter & tap selector assembly fell on bottom of ICT | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 153 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0237 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Fire Protection | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | tank. (vi) Severe mechanical damage has been observed in B phase OLTC. (vii) Burning and heavy fire related damages have been observed in Y phase bottom winding, Y- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 153 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0238 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Failure / Failure Analysis | Fire Protection | FAILURE_ANALYSIS | (viii) Marshalling box of the ICT mounted on 220 kV side was also damaged due to failure impact (ix) Due to fault, ICT caught fire towards 220kV side and same was extinguished with emulsifier, | NOT COVERED | NOT VERIFIED | 220 kV; 220kV | EXPLICIT IN SOURCE | (viii) Marshalling box of the ICT mounted on 220 kV side was also damaged due to failure impact (ix) Due to fault, ICT caught fire towards 220kV side and same was extinguished with emulsifier, | 220 kV and above voltage class substation equipment | PDF p. 154 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0239 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | hydrant system and rain. (x) All Oil spilled to sump pit from heavy opening mentioned at point no1. The main tank & OLTC | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 154 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0240 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | conservator oil level was NIL. (xi) All 220 kV Bushings, 400kV B phase bushing, 33kV Y & B phase bushings got damaged during | NOT COVERED | NOT VERIFIED | 220 kV; 400kV; 33kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 154 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0241 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | incidence. xiv. Probable cause of failure: 220 kV side winding dielectric failure. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | incidence. xiv. Probable cause of failure: 220 kV side winding dielectric failure. | 220 kV and above voltage class substation equipment | PDF p. 154 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0242 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | xxxiv. Lightning Impulse and Switching Impulse Withstand Voltage of the bushing of all voltage level | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 155 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0243 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/ Nitrogen filled/ Oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 155 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0244 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 23. Failure report of 397 MVA, 400 kV Converter Transformer at HVDC Kaniha Substation of Powergrid | NOT COVERED | NOT VERIFIED | 397 MVA; 400 kV | NOT COVERED | 23. Failure report of 397 MVA, 400 kV Converter Transformer at HVDC Kaniha Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 157 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0245 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | Deviations were noticed in magnetization current in all 3 windings i.e. Primary, secondary star and secondary delta of this failed converter transformer. 3. Voltage Ratio Test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Deviations were noticed in magnetization current in all 3 windings i.e. Primary, secondary star and secondary delta of this failed converter transformer. 3. Voltage Ratio Test | 220 kV and above voltage class substation equipment | PDF p. 158 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0246 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | xiii. Observations (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment/ Material etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 158 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0247 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | core laminations. 7) Burnt paper/carbon particles were found on top Perma wood ring near star winding Y1 bushing. 8) Bushing connection & lead take-out area of star winding Y1 checked after dismantling the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 159 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0248 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | bushing; many burnt paper & carbon traces found on Star winding Y1 Bushing BCT, snout area, winding lead takeout area inside snout. xiv. Probable cause of failure: Based on LV test results and internal | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | bushing; many burnt paper & carbon traces found on Star winding Y1 Bushing BCT, snout area, winding lead takeout area inside snout. xiv. Probable cause of failure: Based on LV test results and internal | 220 kV and above voltage class substation equipment | PDF p. 159 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0249 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 24. Failure report of 500 MVA, 400/220 kV ICT at Maharanibagh Substation of Powergrid | NOT COVERED | NOT VERIFIED | 500 MVA; 220 kV | NOT COVERED | 24. Failure report of 500 MVA, 400/220 kV ICT at Maharanibagh Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 162 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0250 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xii. Details of Tests done after failure (What tests were conducted after the discovery of failure. If no test were conducted, reason for the same may be stated) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xii. Details of Tests done after failure (What tests were conducted after the discovery of failure. If no test were conducted, reason for the same may be stated) | 220 kV and above voltage class substation equipment | PDF p. 162 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0251 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | In SFRA Signature (HV-IV open circuit), B phase open circuit signature is flat. xiii. Observations (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment/ Material etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 163 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0252 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Inspection | FAILURE_ANALYSIS | Based on the physical and internal inspection of the failed ICT & LV test report, following are the observations: 1) The main tank of ICT busted from 400 kV Y & B phase bottom bell joint. The main tank opened | NOT COVERED | NOT VERIFIED | 400 kV | NOT COVERED | Based on the physical and internal inspection of the failed ICT & LV test report, following are the observations: 1) The main tank of ICT busted from 400 kV Y & B phase bottom bell joint. The main tank opened | 220 kV and above voltage class substation equipment | PDF p. 163 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0253 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | around 100 mm from bottom joint on HV side with huge bulging. 2) The bell tank joint bolts were found sheared with impact & spread over 10-20 meters from ICT. 3) All Oil spilled to sump pit from heavy opening mentioned at point no1. The main tank & OLTC | NOT COVERED | NOT VERIFIED | 100 mm | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 163 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0254 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | conservator oil level was found NIL. 4) The 400 kV, 220 kV & 33 kV Bushings were found healthy, and no major impact of fault was seen | NOT COVERED | NOT VERIFIED | 400 kV; 220 kV; 33 kV | NOT COVERED | conservator oil level was found NIL. 4) The 400 kV, 220 kV & 33 kV Bushings were found healthy, and no major impact of fault was seen | 220 kV and above voltage class substation equipment | PDF p. 163 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0255 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Bushing, Fire Protection | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | on bushings. 5) Severe mechanical damage has been observed in Y & B phase OLTC. 6) Burning and heavy fire related damages have been observed in Y phase & B Phase Series winding. 7) Permawood and insulation materials were also found shattered outside the main tank towards 400 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 163 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0256 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 25. Failure report of 315 MVA, 400/220 kV ICT-1 at Kaithal Substation of Powergrid | NOT COVERED | NOT VERIFIED | 315 MVA; 220 kV | NOT COVERED | 25. Failure report of 315 MVA, 400/220 kV ICT-1 at Kaithal Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 166 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0257 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Date H2 CH4 C2H2 C2H4 C2H6 11.05.2024 1364 974 1928 2235 174 LV test Results (Post Failure) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Date H2 CH4 C2H2 C2H4 C2H6 11.05.2024 1364 974 1928 2235 174 LV test Results (Post Failure) | 220 kV and above voltage class substation equipment | PDF p. 166 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0258 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | From the LV test report, DGA history, Physical and internal inspection of the failed ICT, it is suspected that there is dielectric failure of B phase series winding during through fault in associated 220 kV transmission line. Due to fault in series winding, high fault current (approx. 23 kA) flown from HV side which results in development of high mechanical forces in the ICT. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | From the LV test report, DGA history, Physical and internal inspection of the failed ICT, it is suspected that there is dielectric failure of B phase series winding during through fault in associated 220 kV transmission line. Due to fault in series winding, high fault current (approx. 23 kA) flown from HV side which results in development of high mechanical forces in the ICT. | 220 kV and above voltage class substation equipment | PDF p. 167 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0259 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Bushing | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | transformer during the fault. Minor cracks on HV bushing flange were also observed. 4) B-Phase winding geometry has changed. The top and bottom clamping ring dislocated. 5) B-Phase IV side outer cylinder found broken. HV lead connecting to OLTC lead no-3 dislodged from | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | transformer during the fault. Minor cracks on HV bushing flange were also observed. 4) B-Phase winding geometry has changed. The top and bottom clamping ring dislocated. 5) B-Phase IV side outer cylinder found broken. HV lead connecting to OLTC lead no-3 dislodged from | 220 kV and above voltage class substation equipment | PDF p. 167 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0260 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | its original position. Copper conductor came out along with HV lead from the top disc of the series winding. 6) The top yoke frame at B-Phase HV side shifted from its original position. 7) Approximately 75 KL Oil spilled to sump pit from bell tank joint and cracked tank stiffener. The main | NOT COVERED | NOT VERIFIED | NOT VERIFIED | its original position. Copper conductor came out along with HV lead from the top disc of the series winding. 6) The top yoke frame at B-Phase HV side shifted from its original position. 7) Approximately 75 KL Oil spilled to sump pit from bell tank joint and cracked tank stiffener. The main | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 167 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0261 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | tank & OLTC conservator oil level was NIL. 8) Burnt paper and carbon particles were found on the tank bottom. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 167 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0262 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | conducted, periodicity of the maintenance activities) (b) Whether any abnormality observed in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 168 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0263 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 26. Failure report of 315 MVA, 400/220 kV ICT-2 at Munirabad Substation of Powergrid | NOT COVERED | NOT VERIFIED | 315 MVA; 220 kV | NOT COVERED | 26. Failure report of 315 MVA, 400/220 kV ICT-2 at Munirabad Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 170 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0264 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | • From the LV test it is observed that short circuit impedance values are violated. The% impedance | • From the LV test it is observed that short circuit impedance values are violated. The% impedance | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 171 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0265 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Winding Resistance | FAILURE_ANALYSIS | of HV to IV and HV to LV are falling under 25.165% and 58.35% respectively & short circuit currents are reduced 50% and 30% compared with other phases. • B Phase series winding resistance value is clear indicative of fault in the winding. In SFRA | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of HV to IV and HV to LV are falling under 25.165% and 58.35% respectively & short circuit currents are reduced 50% and 30% compared with other phases. • B Phase series winding resistance value is clear indicative of fault in the winding. In SFRA | 220 kV and above voltage class substation equipment | PDF p. 171 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0266 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Winding Resistance | FAILURE_ANALYSIS | response, generation of new resonances is also complementing the winding resistance test results which indicates fault in B phase series winding • There is increase of all the fault gases after tripping of ICT including high concentrations of H2 & | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | response, generation of new resonances is also complementing the winding resistance test results which indicates fault in B phase series winding • There is increase of all the fault gases after tripping of ICT including high concentrations of H2 & | 220 kV and above voltage class substation equipment | PDF p. 171 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0267 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | C2H2. xiii. Observations (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment/ Material etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 171 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0268 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Inspection | FAILURE_ANALYSIS | 1. Snout provided on B-ph HV winding lead take off was found loose. 2. Black marks were observed at the bottom of the HV winding of B-PH. 3. For detail inspection and to localize the fault, the outer barrier and press board was removed from | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 1. Snout provided on B-ph HV winding lead take off was found loose. 2. Black marks were observed at the bottom of the HV winding of B-PH. 3. For detail inspection and to localize the fault, the outer barrier and press board was removed from | 220 kV and above voltage class substation equipment | PDF p. 171 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0269 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS, Substation | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | 27. Failure report of 315 MVA, 400/220 kV ICT-1 at Kala GIS Substation of Powergrid | NOT COVERED | NOT VERIFIED | 315 MVA; 220 kV | NOT COVERED | 27. Failure report of 315 MVA, 400/220 kV ICT-1 at Kala GIS Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 174 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0270 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 28. Failure report of 160 MVA, 220/132 kV ICT-2 at Birpara Substation of Powergrid | NOT COVERED | NOT VERIFIED | 160 MVA; 132 kV | NOT COVERED | 28. Failure report of 160 MVA, 220/132 kV ICT-2 at Birpara Substation of Powergrid | 220 kV and above voltage class substation equipment | PDF p. 178 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0271 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 2.3-N 239 3.15 mA The magnetization current of 1.2-N & 2.2-N (HV & LV Y Ph – N) found to be very high in comparison to other phases. 3) Magnetic Balance Test | 2.3-N 239 3.15 mA The magnetization current of 1.2-N & 2.2-N (HV & LV Y Ph – N) found to be very high in comparison to other phases. 3) Magnetic Balance Test | NOT VERIFIED | 3.15 mA | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 179 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0272 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 29. Failure report of 160 MVA, 220/132 kV, BHEL Make Auto Power Transformer at Bhiwadi GSS of RRVPNL | NOT COVERED | NOT VERIFIED | 160 MVA; 132 kV | NOT COVERED | 29. Failure report of 160 MVA, 220/132 kV, BHEL Make Auto Power Transformer at Bhiwadi GSS of RRVPNL | 220 kV and above voltage class substation equipment | PDF p. 182 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0273 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 30. Failure Report of 50 MVA, 230/33 kV Power Transformer at Veeranam Substation of TANTRANSCO | NOT COVERED | NOT VERIFIED | 50 MVA; 33 kV | NOT COVERED | 30. Failure Report of 50 MVA, 230/33 kV Power Transformer at Veeranam Substation of TANTRANSCO | 220 kV and above voltage class substation equipment | PDF p. 186 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0274 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | Power Transformer | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | Date Hydrogen Methane Ethanae Ethylene Acetylene 27.01.2023 (Bottom) 5 6 1 6 0.05 06.10.2023 (Top) 3 4 1 8 0.01 06.10.2023 (Bottom) 7 11 2 29 41.92 06.10.2023 (OLTC) 5 7 2 16 0.15 DGA shows slight increase in fault gases compared with previous results. This may be due to development of suspected high thermal/ arcing fault inside the Power Transformer. 2) Magnetic Balance Test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Date Hydrogen Methane Ethanae Ethylene Acetylene 27.01.2023 (Bottom) 5 6 1 6 0.05 06.10.2023 (Top) 3 4 1 8 0.01 06.10.2023 (Bottom) 7 11 2 29 41.92 06.10.2023 (OLTC) 5 7 2 16 0.15 DGA shows slight increase in fault gases compared with previous results. This may be due to development of suspected high thermal/ arcing fault inside the Power Transformer. 2) Magnetic Balance Test | 220 kV and above voltage class substation equipment | PDF p. 186 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0275 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Bushing | NOT VERIFIED | Inspection | OLTC | INSPECTION | Findings of Open Inspection on 09.10.2023 1) HV&LV Bushing terminals, OLTC tap leads terminals and both Neutral bushing terminals found | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 187 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0276 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | cable found to have terminated at one end with sheath earthed and another end is free. Both ends are free in another cable. The free ends of cable are in open condition. xiv. Probable cause of failure: Internal fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | cable found to have terminated at one end with sheath earthed and another end is free. Both ends are free in another cable. The free ends of cable are in open condition. xiv. Probable cause of failure: Internal fault | 220 kV and above voltage class substation equipment | PDF p. 187 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0277 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Power Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 31. Failure report of 50 MVA, 230 kV Power Transformer at Udayathur Substation of TANTRANSCO | NOT COVERED | NOT VERIFIED | 50 MVA; 230 kV | NOT COVERED | 31. Failure report of 50 MVA, 230 kV Power Transformer at Udayathur Substation of TANTRANSCO | 220 kV and above voltage class substation equipment | PDF p. 189 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0278 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: B.29922 vii. Date and time of occurrence of fault: 04.11.23 at 07:01 hrs | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: B.29922 vii. Date and time of occurrence of fault: 04.11.23 at 07:01 hrs | 220 kV and above voltage class substation equipment | PDF p. 189 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0279 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | x. Date of Commissioning: 12.03.2007 xi. Sequence of events/ Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | x. Date of Commissioning: 12.03.2007 xi. Sequence of events/ Description of fault | 220 kV and above voltage class substation equipment | PDF p. 189 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0280 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | DGA shows increase in fault gas level when compared with the previous test dated 27.10.2023. This may be due to development of suspected high energy thermal/arcing fault (i.e. Circulating current or overheated joints) inside the Power Transformer. xiii. Observations | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | DGA shows increase in fault gas level when compared with the previous test dated 27.10.2023. This may be due to development of suspected high energy thermal/arcing fault (i.e. Circulating current or overheated joints) inside the Power Transformer. xiii. Observations | 220 kV and above voltage class substation equipment | PDF p. 190 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0281 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | before commissioning: (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/Nitrogen filled/ Oil filled | before commissioning: (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/Nitrogen filled/ Oil filled | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 192 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0282 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 32. Failure report of 315 MVA, 400/ 230 kV of ICT at Alamathy Substation of TANTRANSCO | NOT COVERED | NOT VERIFIED | 315 MVA; 230 kV | NOT COVERED | 32. Failure report of 315 MVA, 400/ 230 kV of ICT at Alamathy Substation of TANTRANSCO | 220 kV and above voltage class substation equipment | PDF p. 192 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0283 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 2) Buchholz relay 3) PRV for MAIN and OLTC tanks 4) NIFPS 5) Back up OC EL relay 6) Oil and Winding temp trip relays 7) OLTC surge relay. xxx. Details of Protection operated: Protection Operated details: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 194 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0284 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 33. Failure report of 160 MVA, 3 Phase Auto-transformer at Faridpur Substation of UPPTCL | NOT COVERED | NOT VERIFIED | 160 MVA | NOT COVERED | 33. Failure report of 160 MVA, 3 Phase Auto-transformer at Faridpur Substation of UPPTCL | 220 kV and above voltage class substation equipment | PDF p. 195 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0285 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | could not be ascertained. xv. If OEM representative had inspected the equipment or visited the site after failure, their remarks, MoM etc. may be attached. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | could not be ascertained. xv. If OEM representative had inspected the equipment or visited the site after failure, their remarks, MoM etc. may be attached. | 220 kV and above voltage class substation equipment | PDF p. 195 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0286 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 34. Failure report of 500 MVA, 400/220/33 kV, 3-Phase ICT at Rasara Substation of UPPTCL | NOT COVERED | NOT VERIFIED | 500 MVA; 33 kV | NOT COVERED | 34. Failure report of 500 MVA, 400/220/33 kV, 3-Phase ICT at Rasara Substation of UPPTCL | 220 kV and above voltage class substation equipment | PDF p. 198 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0287 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 35. Failure report of 400/220/33 kV, 240 MVA 3 Phase ICT at Gorakhpur Substation of UPPTCL | NOT COVERED | NOT VERIFIED | 33 kV; 240 MVA | NOT COVERED | 35. Failure report of 400/220/33 kV, 240 MVA 3 Phase ICT at Gorakhpur Substation of UPPTCL | 220 kV and above voltage class substation equipment | PDF p. 202 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0288 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: 71128-1 vii. Date and time of occurrence of fault: 11.11.2023,15:51Hrs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: 71128-1 vii. Date and time of occurrence of fault: 11.11.2023,15:51Hrs. | 220 kV and above voltage class substation equipment | PDF p. 202 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0289 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | xvii. (a) Details of previous maintenance (Activities carried out in previous maintenance including the tests conducted, periodicity of the maintenance activities) (b) Whether any abnormality observed in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 203 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0290 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Substation | Auto Transformer | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 36. Failure report of 100 MVA, 220/132 kV Auto Transformer at Bhartna Substation Etawah of UPPTCL | NOT COVERED | NOT VERIFIED | 100 MVA; 132 kV | NOT COVERED | 36. Failure report of 100 MVA, 220/132 kV Auto Transformer at Bhartna Substation Etawah of UPPTCL | 220 kV and above voltage class substation equipment | PDF p. 205 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0291 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Substation | Bus Reactor | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 38. Failure report of 50 MVAr, 420 kV Bus Reactor at Balipara Substation of Power grid | NOT COVERED | NOT VERIFIED | 50 MVAr; 420 kV | NOT COVERED | 38. Failure report of 50 MVAr, 420 kV Bus Reactor at Balipara Substation of Power grid | 220 kV and above voltage class substation equipment | PDF p. 211 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0292 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Serial No.: 6005276 vii. Date and time of occurrence of fault: 14.08.2023 at 00:29:52 Hrs | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Serial No.: 6005276 vii. Date and time of occurrence of fault: 14.08.2023 at 00:29:52 Hrs | 220 kV and above voltage class substation equipment | PDF p. 211 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0293 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (What tests were conducted after the discovery of failure. If no test were conducted, reason for the same may be stated) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (What tests were conducted after the discovery of failure. If no test were conducted, reason for the same may be stated) | 220 kV and above voltage class substation equipment | PDF p. 211 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0294 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | b) After removing the bushing leads, it was found that Y-Phase winding near bottom take-off point | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 213 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0295 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | HV Y phase winding. d) The bushing lead connections of R, Y & B HV side windings were checked visually, and no burnt | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 213 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0296 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | equipment or visited the site after failure, their remarks, MOM etc. may be attached. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | equipment or visited the site after failure, their remarks, MOM etc. may be attached. | 220 kV and above voltage class substation equipment | PDF p. 213 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0297 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | (Emulsifier system/ N2 Injection based fire protection system/ foam based protection etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (Emulsifier system/ N2 Injection based fire protection system/ foam based protection etc.) | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 214 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0298 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | before commissioning: (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/ Nitrogen filled/ Oil filled | before commissioning: (a) Period of storage (b) Idle charged or uncharged (c) Dry air filled/ Nitrogen filled/ Oil filled | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 214 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0299 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment/ Material etc.) 1) Main tank got ruptured and cracks observed at tank corner welding joints and stiffeners at HV | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 216 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0300 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | side. 2) HV side bottom inspection cover shattered and found 2mtrs away from the reactor with | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 216 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0301 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | pressboard and paper insulation came out from the opening. 3) Complete oil gushed out from the main tank. 4) PNRV was kept in auto mode and same was found in operated condition accordingly, oil was | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 216 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0302 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | found in conservator and MOG is also found OK. 5) PRD-1 completely damaged and fell on the ground. 6) HV Bushing got damaged during incidence and insulator parts were scattered around the reactor. 7) No oil was found in Neutral bushing. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 216 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0303 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, AIS, Substation | Bus Reactor | Failure / Failure Analysis | AIS | FAILURE_ANALYSIS | 40. Failure report of 50 MVAr, 400 kV Bus Reactor at Ramgarh Jaisalmer Substation of RRVPNL | NOT COVERED | NOT VERIFIED | 50 MVAr; 400 kV | NOT COVERED | 40. Failure report of 50 MVAr, 400 kV Bus Reactor at Ramgarh Jaisalmer Substation of RRVPNL | 220 kV and above voltage class substation equipment | PDF p. 219 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0304 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | v. Make (Original equipment manufacturer): BHEL vi. Serial No.: 6007650 vii. Date and time of occurrence of fault: 09.05.2024 at 02:11 hrs. viii. Fault discovered during | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | v. Make (Original equipment manufacturer): BHEL vi. Serial No.: 6007650 vii. Date and time of occurrence of fault: 09.05.2024 at 02:11 hrs. viii. Fault discovered during | 220 kV and above voltage class substation equipment | PDF p. 219 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0305 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | ix. Year of Manufacturing: 2017 x. Year of Commissioning: 06.12.2017 xi. Sequence of events/ Description of Fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ix. Year of Manufacturing: 2017 x. Year of Commissioning: 06.12.2017 xi. Sequence of events/ Description of Fault | 220 kV and above voltage class substation equipment | PDF p. 219 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0306 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment/ Material etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 219 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0307 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Safety | Failure | SAFETY | xiv. Probable cause of failure: The Cause of failure could not be ascertained as the post failure test could not be conducted due to complete damage of the Reactor. However, it appears that there is internal fault in the Reactor. xv. If OEM representative had inspected the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | xiv. Probable cause of failure: The Cause of failure could not be ascertained as the post failure test could not be conducted due to complete damage of the Reactor. However, it appears that there is internal fault in the Reactor. xv. If OEM representative had inspected the | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 219 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0308 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 41. Failure report of 420 kV CT at HVDC Mundra Substation of Adani Transmission Ltd | NOT COVERED | NOT VERIFIED | 420 kV | NOT COVERED | 41. Failure report of 420 kV CT at HVDC Mundra Substation of Adani Transmission Ltd | 220 kV and above voltage class substation equipment | PDF p. 221 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0309 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | x. Weather conditions at the time of failure (clear sky/ rainy / thunderstorm etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | x. Weather conditions at the time of failure (clear sky/ rainy / thunderstorm etc.) | 220 kV and above voltage class substation equipment | PDF p. 221 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0310 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Capacitance | TESTING | feeder, Y-Phase iv. Rating (Voltage/ current/ current-ratio/ capacitance/ MCOV etc., as applicable) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 223 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0311 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vii. Serial No.: 37994026426 viii. Date and time of occurrence of fault: 31.07.2024 at 10:22 hrs ix. Fault discovered during (Operation or periodic testing/ maintenance) | NOT COVERED | Fault discovered during (Operation or periodic testing/ maintenance) | NOT VERIFIED | NOT COVERED | vii. Serial No.: 37994026426 viii. Date and time of occurrence of fault: 31.07.2024 at 10:22 hrs ix. Fault discovered during (Operation or periodic testing/ maintenance) | 220 kV and above voltage class substation equipment | PDF p. 223 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0312 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. If OEM was contacted after failure, its recommendation/ remark/ report/ MoM | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. If OEM was contacted after failure, its recommendation/ remark/ report/ MoM | 220 kV and above voltage class substation equipment | PDF p. 223 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0313 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xvii. Details of previous failure (Any failure which has led to a major repair of the equipment in the past since its commissioning) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xvii. Details of previous failure (Any failure which has led to a major repair of the equipment in the past since its commissioning) | 220 kV and above voltage class substation equipment | PDF p. 223 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0314 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | switching station Tallapalli the 220 kV GE Make Y Phase CT in 220 kV TPL-Rentachintala- 2 feeder blasted due to internal fault and Bus- Bar protection operated and causes tripping of all 220 kV feeders on Bus-1&3 at 220 kV S/s Tallapalli. 220 kV Rentachintala-2 feeder kept isolated and all the remaining feeders taken into service one by one. After replacing the failed GE make CT with new CG power make CT for 220 kV TPL-Rentachintala-2 feeder in Y phase and then feeder taken into service at 06:55 Hrs on 01-08-2024 xix. Details of protection operated: -- xx. Details of tests done after failure: CT blasted and replaced with a new one, then | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | switching station Tallapalli the 220 kV GE Make Y Phase CT in 220 kV TPL-Rentachintala- 2 feeder blasted due to internal fault and Bus- Bar protection operated and causes tripping of all 220 kV feeders on Bus-1&3 at 220 kV S/s Tallapalli. 220 kV Rentachintala-2 feeder kept isolated and all the remaining feeders taken into service one by one. After replacing the failed GE make CT with new CG power make CT for 220 kV TPL-Rentachintala-2 feeder in Y phase and then feeder taken into service at 06:55 Hrs on 01-08-2024 xix. Details of protection operated: -- xx. Details of tests done after failure: CT blasted and replaced with a new one, then | 220 kV and above voltage class substation equipment | PDF p. 224 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0315 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: Physical inspection, small holes found in top | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Physical inspection, small holes found in top | 220 kV and above voltage class substation equipment | PDF p. 226 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0316 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Failure | SAFETY | bar Protection operated due to failure of R- Phase 220 kV CT of SSTP11-11 Feeder. Simultaneously 8 No. 220 kV feeder, 4 No. 220 kV class Transformer, I No. 220 kV Bus tie & 2 No. 220 kV Incoming I & II of 315 MVA Transformer Tripped. | NOT COVERED | NOT VERIFIED | 220 kV; 315 MVA | bar Protection operated due to failure of R- Phase 220 kV CT of SSTP11-11 Feeder. Simultaneously 8 No. 220 kV feeder, 4 No. 220 kV class Transformer, I No. 220 kV Bus tie & 2 No. 220 kV Incoming I & II of 315 MVA Transformer Tripped. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 228 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0317 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Tan Delta | FAILURE_ANALYSIS | xx. Details of tests done after failure: Installed new C.T. after testing Tan Delta, IR | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Installed new C.T. after testing Tan Delta, IR | 220 kV and above voltage class substation equipment | PDF p. 228 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0318 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Inspection | SAFETY | Transformer tripped on Differential Relay, during inspection Y phase 220 kV CT was found failed. xix. Details of protection operated: Differential Protection Operated | NOT COVERED | NOT VERIFIED | 220 kV | Transformer tripped on Differential Relay, during inspection Y phase 220 kV CT was found failed. xix. Details of protection operated: Differential Protection Operated | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 230 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0319 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | Note: Fire observed on CT Stud therefore 400 kV Chandrapur GCR HVDC Pole 1 Converter CB Hand tripped, to avoid further tripping. | NOT COVERED | NOT VERIFIED | 400 kV | Note: Fire observed on CT Stud therefore 400 kV Chandrapur GCR HVDC Pole 1 Converter CB Hand tripped, to avoid further tripping. | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 232 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0320 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | CT. xix. Details of protection operated: Distance protection operated xx. Details of tests done after failure: 100% Burnt, it is not possible to carry out the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | CT. xix. Details of protection operated: Distance protection operated xx. Details of tests done after failure: 100% Burnt, it is not possible to carry out the | 220 kV and above voltage class substation equipment | PDF p. 234 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0321 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xi. Year of manufacturing: 2008 xii. Date of commissioning: 22.03.2010 xiii. Storage condition of equipment if the gap | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 235 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0322 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) | 220 kV and above voltage class substation equipment | PDF p. 236 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0323 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | line by EHV Line maintenance Padgha in 19:25 hrs as per LD code 50. 2) At the time of line CB OFF at AKP | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 236 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0324 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Safety | Failure | SAFETY | Substation, 220 kV AKP Kalwa line Y ph CT to line Isolator conductor snapped due to hot spot at 220 kV AKP substation along with heavy sparking observed at Y ph CT. At the same time 220 kV AKP KALWA line tripped at kalwa end only and the CB remained ON at AKP end. Thus, 220 kV AKP Substation went into dark in 19:25hrs. Further, 220 kV AKP Kalwa Line CB hand tripped immediately. Busbar protection was out of service. xix. Details of protection operated: Distance protection operated at another end i.e. at Kalwa end (Distance-0.9 km from Kalwa end) xx. Details of tests done after failure: IR taken on 05.11.2024 and found normal xxi. Observations | NOT COVERED | NOT VERIFIED | 220 kV | Substation, 220 kV AKP Kalwa line Y ph CT to line Isolator conductor snapped due to hot spot at 220 kV AKP substation along with heavy sparking observed at Y ph CT. At the same time 220 kV AKP KALWA line tripped at kalwa end only and the CB remained ON at AKP end. Thus, 220 kV AKP Substation went into dark in 19:25hrs. Further, 220 kV AKP Kalwa Line CB hand tripped immediately. Busbar protection was out of service. xix. Details of protection operated: Distance protection operated at another end i.e. at Kalwa end (Distance-0.9 km from Kalwa end) xx. Details of tests done after failure: IR taken on 05.11.2024 and found normal xxi. Observations | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 236 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0325 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxii. Probable cause of failure: Ageing xxiii. Remark: 220 kV Apta Substation dark due to Y-ph CT of | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | xxii. Probable cause of failure: Ageing xxiii. Remark: 220 kV Apta Substation dark due to Y-ph CT of | 220 kV and above voltage class substation equipment | PDF p. 238 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0326 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation, Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | 400 kV Chakan-Lonikand-1 line bay at Chakan substation got burst and caught fire on dated 23.12.2024 at 23:39 hrs and same is replaced by another one. Line charged & taken in service on dated 24.12.2024 at 8.10 hrs. | NOT COVERED | NOT VERIFIED | 400 kV | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 240 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0327 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xi. Year of manufacturing: - xii. Date of commissioning: - xiii. Storage condition of equipment if the gap between delivery at site and commissioning is over 6 months | NOT COVERED | NOT VERIFIED | 6 months | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 243 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0328 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vii. Serial No.: 37994010128/ 2016 viii. Date and time of occurrence of fault: On 27.12.2023 at 5:58 hrs ix. Fault discovered during (Operation or periodic testing/ maintenance) | NOT COVERED | Fault discovered during (Operation or periodic testing/ maintenance) | NOT VERIFIED | NOT COVERED | vii. Serial No.: 37994010128/ 2016 viii. Date and time of occurrence of fault: On 27.12.2023 at 5:58 hrs ix. Fault discovered during (Operation or periodic testing/ maintenance) | 220 kV and above voltage class substation equipment | PDF p. 245 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0329 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Capacitance | TESTING | feeder iv. Rating (Voltage/ current/ current ratio/ capacitance/ MCOV etc., as applicable) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 246 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0330 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | : - x. Weather conditions at the time of failure (clear sky/ rainy / thunderstorm etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | : - x. Weather conditions at the time of failure (clear sky/ rainy / thunderstorm etc.) | 220 kV and above voltage class substation equipment | PDF p. 246 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0331 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vi. Make (Original equipment manufacturer): ABB vii. Serial No.: 2105314 viii. Date and time of occurrence of fault: 26.8.23 / 10.04 Hrs ix. Fault discovered during (Operation or | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | vi. Make (Original equipment manufacturer): ABB vii. Serial No.: 2105314 viii. Date and time of occurrence of fault: 26.8.23 / 10.04 Hrs ix. Fault discovered during (Operation or | 220 kV and above voltage class substation equipment | PDF p. 251 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0332 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xi. Year of manufacturing: 2005 xii. Date of commissioning: 25.04.2006 xiii. Storage condition of equipment if the gap | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 251 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0333 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Failure | SAFETY | Transformer HV & LV breaker tripped. xx. Details of tests done after failure: - xxi. Observations: CT burst out with heavy sound | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Transformer HV & LV breaker tripped. xx. Details of tests done after failure: - xxi. Observations: CT burst out with heavy sound | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 252 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0334 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xi. Year of manufacturing: 2003 xii. Date of commissioning: 04.05.2014 xiii. Storage condition of equipment if the gap between delivery at site and commissioning is over 6 months | NOT COVERED | NOT VERIFIED | 6 months | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 253 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0335 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xix. Details of protection operated: Distance TnpZ1 xx. Details of tests done after failure: - xxi. Observations (Any relevant observation made by the field staff or during visual inspection) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xix. Details of protection operated: Distance TnpZ1 xx. Details of tests done after failure: - xxi. Observations (Any relevant observation made by the field staff or during visual inspection) | 220 kV and above voltage class substation equipment | PDF p. 254 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0336 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxii. Probable cause of failure: As the CT got burst so cause of failure could not be determined | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxii. Probable cause of failure: As the CT got burst so cause of failure could not be determined | 220 kV and above voltage class substation equipment | PDF p. 254 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0337 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xi. Year of manufacturing: 2007 xii. Date of commissioning: 15.08.2015 xiii. Storage condition of equipment if the gap between delivery at site and commissioning is over 6 months | NOT COVERED | NOT VERIFIED | 6 months | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 255 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0338 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | xvi. (a) Details of previous maintenance (Activities carried out in previous maintenance including the tests conducted, periodicity of the maintenance activities) (b) Whether any abnormality observed in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 259 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0339 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xix. Details of protection operated: Bus bar protection operated xx. Details of tests done after failure: Equipment was completed damaged no test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xix. Details of protection operated: Bus bar protection operated xx. Details of tests done after failure: Equipment was completed damaged no test | 220 kV and above voltage class substation equipment | PDF p. 260 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0340 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 10.94 kA, 1.10 kA at Sirathu-trip xx. Details of tests done after failure: Nil, Complete damage | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 10.94 kA, 1.10 kA at Sirathu-trip xx. Details of tests done after failure: Nil, Complete damage | 220 kV and above voltage class substation equipment | PDF p. 266 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0341 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | vii. Serial No.: 2239732 viii. Date and time of occurrence of fault: 11.04.2024, 00:32 Hrs. ix. Fault discovered during (Operation or periodic testing/maintenance) | NOT COVERED | Fault discovered during (Operation or periodic testing/maintenance) | NOT VERIFIED | NOT COVERED | vii. Serial No.: 2239732 viii. Date and time of occurrence of fault: 11.04.2024, 00:32 Hrs. ix. Fault discovered during (Operation or periodic testing/maintenance) | 220 kV and above voltage class substation equipment | PDF p. 267 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0342 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | xxi. Observations (Any relevant observation made by the field staff or during visual inspection) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 270 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0343 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 67. Failure report of 220 kV CT at Jolly Road-Muzaffarnagar Substation of UPPTCL | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 67. Failure report of 220 kV CT at Jolly Road-Muzaffarnagar Substation of UPPTCL | 220 kV and above voltage class substation equipment | PDF p. 271 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0344 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xiii. Storage condition of equipment if the gap between delivery at site and commissioning is over 6months | NOT COVERED | NOT VERIFIED | 6months | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 271 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0345 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. If OEM was contacted after failure, its recommendation /remark / report/ MoM | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. If OEM was contacted after failure, its recommendation /remark / report/ MoM | 220 kV and above voltage class substation equipment | PDF p. 271 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0346 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events/Description of fault (SOE with time stamp) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events/Description of fault (SOE with time stamp) | 220 kV and above voltage class substation equipment | PDF p. 272 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0347 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | CB Open Flag: C/P—DPO, DPS P,R/P-Z-1,Z-2,Z-3,Z-4 Trip, PSB operated,86B RYB, R phase, Y-phase, B phase & Bus-A Bus bar protection operated xx. Details of tests done after failure: Replace by new CT | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | CB Open Flag: C/P—DPO, DPS P,R/P-Z-1,Z-2,Z-3,Z-4 Trip, PSB operated,86B RYB, R phase, Y-phase, B phase & Bus-A Bus bar protection operated xx. Details of tests done after failure: Replace by new CT | 220 kV and above voltage class substation equipment | PDF p. 272 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0348 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | xiii. Storage condition of equipment if the gap between delivery at site and commissioning is over 6 months | NOT COVERED | NOT VERIFIED | 6 months | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 273 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0349 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. If OEM was contacted after failure, its recommendation/ remark / report/ MoM | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. If OEM was contacted after failure, its recommendation/ remark / report/ MoM | 220 kV and above voltage class substation equipment | PDF p. 275 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0350 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Bus Bar protection. Relay R, Y, B phase operated xx. Details of tests done after failure: Meggering | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Bus Bar protection. Relay R, Y, B phase operated xx. Details of tests done after failure: Meggering | 220 kV and above voltage class substation equipment | PDF p. 278 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0351 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events/ Description of fault (SOE with time stamp) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events/ Description of fault (SOE with time stamp) | 220 kV and above voltage class substation equipment | PDF p. 280 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0352 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | xx. Observations (Any relevant observation made by the field staff or during visual inspection) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 286 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0353 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxii. Probable cause of failure: As the CT got completely damaged so cause of failure could not be determined | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxii. Probable cause of failure: As the CT got completely damaged so cause of failure could not be determined | 220 kV and above voltage class substation equipment | PDF p. 290 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0354 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: Replacement of CT and current ratio test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Replacement of CT and current ratio test | 220 kV and above voltage class substation equipment | PDF p. 296 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0355 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | CT, 400 kV Mau-Azamgarh Line got damaged as per the DR/ EL Zone-1 Protection of main- 1 relay and Bus Bar Differential Protection Operated (Operating Current 6 pu) and elements connected through Bus-1 Got tripped in 60 ms (ICT-III, PGCIL Ballia). At the time of fault B Phase current of core -2 (Used for Main-II and LBB Protection as per scheme) is negligible and B Phase current of core-I (Used for Main-I protection) is about 30 kA, after 280 ms Y Phase Fault 6 kA created and LBB Protection operated in 480 ms xix. Details of protection operated: M-1 (REL670) – Zone-1 B Phase Distance 0 | NOT COVERED | NOT VERIFIED | 400 kV | CT, 400 kV Mau-Azamgarh Line got damaged as per the DR/ EL Zone-1 Protection of main- 1 relay and Bus Bar Differential Protection Operated (Operating Current 6 pu) and elements connected through Bus-1 Got tripped in 60 ms (ICT-III, PGCIL Ballia). At the time of fault B Phase current of core -2 (Used for Main-II and LBB Protection as per scheme) is negligible and B Phase current of core-I (Used for Main-I protection) is about 30 kA, after 280 ms Y Phase Fault 6 kA created and LBB Protection operated in 480 ms xix. Details of protection operated: M-1 (REL670) – Zone-1 B Phase Distance 0 | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 298 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0356 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Km, Gr-A Trip M-2 (Siprotec)- B phase Pickup, Raica Protection Operated Bus Bar Operation Relay (SEL-487B)- Trip, 87 Differential, Zone-1, LBB operated, BKR Fail, 96 Operated xx. Details of tests done after failure: CT got damaged so test after failure not | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Km, Gr-A Trip M-2 (Siprotec)- B phase Pickup, Raica Protection Operated Bus Bar Operation Relay (SEL-487B)- Trip, 87 Differential, Zone-1, LBB operated, BKR Fail, 96 Operated xx. Details of tests done after failure: CT got damaged so test after failure not | 220 kV and above voltage class substation equipment | PDF p. 298 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0357 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | abnormality? xvii. Details of previous failure (Any failure which has led to a major repair of the equipment in the past since its commissioning) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | abnormality? xvii. Details of previous failure (Any failure which has led to a major repair of the equipment in the past since its commissioning) | 220 kV and above voltage class substation equipment | PDF p. 302 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0358 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | RP- Z1, M1Rx, Bx, Yx, 86A, 86B M1 (relay)- R phase, Z-1, dist-4.4 kms. IR-3.988 kA, IR=51.399 kA, RB=740.3 kA xx. Details of tests done after failure: - | NOT COVERED | NOT VERIFIED | 86A | NOT COVERED | RP- Z1, M1Rx, Bx, Yx, 86A, 86B M1 (relay)- R phase, Z-1, dist-4.4 kms. IR-3.988 kA, IR=51.399 kA, RB=740.3 kA xx. Details of tests done after failure: - | 220 kV and above voltage class substation equipment | PDF p. 302 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0359 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | insulation failure xix. Details of protection operated: Bus Bar protection operated | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | insulation failure xix. Details of protection operated: Bus Bar protection operated | 220 kV and above voltage class substation equipment | PDF p. 304 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0360 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | lines tripped in reverse zone in local end. 110 kV Niwali-Aarwali TSS line tripped on back up protection. xx. Details of tests done after failure: Not possible due to PT was completely | NOT COVERED | NOT VERIFIED | 110 kV | lines tripped in reverse zone in local end. 110 kV Niwali-Aarwali TSS line tripped on back up protection. xx. Details of tests done after failure: Not possible due to PT was completely | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 306 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0361 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Operated and simultaneously all the associated Lines and Transformers of 220 kV Main Bus tripped, during yard inspection, Y ph PT found burning and mechanically damaged at the oil tank hence extinguished by fire extinguishers and isolated the 220 kV PT. xix. Details of protection operated: At 16:30 Hrs Bus Bar protection Operated and | NOT COVERED | NOT VERIFIED | 220 kV | Operated and simultaneously all the associated Lines and Transformers of 220 kV Main Bus tripped, during yard inspection, Y ph PT found burning and mechanically damaged at the oil tank hence extinguished by fire extinguishers and isolated the 220 kV PT. xix. Details of protection operated: At 16:30 Hrs Bus Bar protection Operated and | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 308 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0362 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | simultaneously all the associated Lines and PTRs of 220 kV Main Bus Tripped. Window indications: - 1)Bus Bar-1 Operated 2) Bus Bar Yph Trip Relay indications: - 1)Bus Bar Operated 2) Bus Bar-1 operated 3) Y Phase Operated No Window and Relay Indications received on 220 kV Lines and PTRs xx. Details of tests done after failure: As PT burst and beyond repairable, no test | NOT COVERED | NOT VERIFIED | 220 kV | simultaneously all the associated Lines and PTRs of 220 kV Main Bus Tripped. Window indications: - 1)Bus Bar-1 Operated 2) Bus Bar Yph Trip Relay indications: - 1)Bus Bar Operated 2) Bus Bar-1 operated 3) Y Phase Operated No Window and Relay Indications received on 220 kV Lines and PTRs xx. Details of tests done after failure: As PT burst and beyond repairable, no test | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 308 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0363 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | – Kharepatan line tripped on Distance protection (Z2, Y-N fault, IL2= 1.55 kA) (4) From the above events, it is observed that | NOT COVERED | NOT VERIFIED | NOT VERIFIED | – Kharepatan line tripped on Distance protection (Z2, Y-N fault, IL2= 1.55 kA) (4) From the above events, it is observed that | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 310 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0364 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | the fault on Y-ph 220 kV Bus PT got initiated at 19:58 hrs on 08.10.2023 & the 220 kV PT was burst at 20:03 hrs on 08.10.2023; this indicates that the fault has developed slowly due to which the RADSS type bus bar protection entered in Blocking mode. Hence the fault is cleared from Pawas S/s. (5) At 20:03 Hrs on 08.10.2023 220 kV Yph PT | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | the fault on Y-ph 220 kV Bus PT got initiated at 19:58 hrs on 08.10.2023 & the 220 kV PT was burst at 20:03 hrs on 08.10.2023; this indicates that the fault has developed slowly due to which the RADSS type bus bar protection entered in Blocking mode. Hence the fault is cleared from Pawas S/s. (5) At 20:03 Hrs on 08.10.2023 220 kV Yph PT | 220 kV and above voltage class substation equipment | PDF p. 310 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0365 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Distance Protection at remote end. xx. Details of tests done after failure: Not possible due to PT in completely | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Distance Protection at remote end. xx. Details of tests done after failure: Not possible due to PT in completely | 220 kV and above voltage class substation equipment | PDF p. 311 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0366 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. If OEM was contacted after failure, its recommendation/ remark/ report / MOM | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. If OEM was contacted after failure, its recommendation/ remark/ report / MOM | 220 kV and above voltage class substation equipment | PDF p. 314 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0367 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: No Testing carried out as equipment was | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: No Testing carried out as equipment was | 220 kV and above voltage class substation equipment | PDF p. 315 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0368 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | section protection Operated. WI:- O/C Operated RI:- Master trip relay operated. xx. Details of tests done after failure: Not Applicable | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | section protection Operated. WI:- O/C Operated RI:- Master trip relay operated. xx. Details of tests done after failure: Not Applicable | 220 kV and above voltage class substation equipment | PDF p. 317 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0369 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | completely which caught fire with oil spillover and complete insulation breakdown resulting in tripping of all EHV Bays on 220 kV Main Bus Bar protection (ABB RADSS Make) with R, S, T & U Flag & fire incidence in Switch-yard so faulty 220 kV Main Bus PT Bay was isolated and fire was controlled & supply to the end consumers was restored immediately. xix. Details of protection operated: Bus Bar protection Operated (ABB RADSS | NOT COVERED | NOT VERIFIED | 220 kV | EXPLICIT IN SOURCE | completely which caught fire with oil spillover and complete insulation breakdown resulting in tripping of all EHV Bays on 220 kV Main Bus Bar protection (ABB RADSS Make) with R, S, T & U Flag & fire incidence in Switch-yard so faulty 220 kV Main Bus PT Bay was isolated and fire was controlled & supply to the end consumers was restored immediately. xix. Details of protection operated: Bus Bar protection Operated (ABB RADSS | 220 kV and above voltage class substation equipment | PDF p. 319 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0370 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: Y-Phase PT Completely burst so no test taken | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Y-Phase PT Completely burst so no test taken | 220 kV and above voltage class substation equipment | PDF p. 319 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0371 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | x. Weather conditions at the time of failure (clear sky/ rainy/ thunderstorm etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | x. Weather conditions at the time of failure (clear sky/ rainy/ thunderstorm etc.) | 220 kV and above voltage class substation equipment | PDF p. 320 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0372 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | which has led to a major repair of the equipment in the past since its commissioning) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 325 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0373 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: Not applicable since the PT completely burst | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Not applicable since the PT completely burst | 220 kV and above voltage class substation equipment | PDF p. 325 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0374 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Busbar Operated on LBB Back trip xx. Details of tests done after failure: DCRM, Time Analyzer, IR | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Busbar Operated on LBB Back trip xx. Details of tests done after failure: DCRM, Time Analyzer, IR | 220 kV and above voltage class substation equipment | PDF p. 335 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0375 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: SF6 gas purity, Dew point, SO2 content and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: SF6 gas purity, Dew point, SO2 content and | 220 kV and above voltage class substation equipment | PDF p. 337 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0376 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. If OEM was contacted after failure, its recommendation /remark/ report/ MoM | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. If OEM was contacted after failure, its recommendation /remark/ report/ MoM | 220 kV and above voltage class substation equipment | PDF p. 338 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0377 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | STPS- RTGH Ckt-II. Operator manually tripped the 400 kV STPS- RTGH Ckt-I from the control room immediately. xx. Details of tests done after failure: None | NOT COVERED | NOT VERIFIED | 400 kV | STPS- RTGH Ckt-II. Operator manually tripped the 400 kV STPS- RTGH Ckt-I from the control room immediately. xx. Details of tests done after failure: None | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 339 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0378 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | in these tests. If yes, attach the test reports. (c) What steps were taken to address the | in these tests. If yes, attach the test reports. (c) What steps were taken to address the | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 342 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0379 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xvii. Sequence of events/ Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xvii. Sequence of events/ Description of fault | 220 kV and above voltage class substation equipment | PDF p. 343 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0380 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xix. Details of tests done after failure: Physically checked and pneumatic system of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xix. Details of tests done after failure: Physically checked and pneumatic system of | 220 kV and above voltage class substation equipment | PDF p. 343 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0381 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxi. Probable cause of failure: As the CT got completely damaged so cause of failure could not be determined | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxi. Probable cause of failure: As the CT got completely damaged so cause of failure could not be determined | 220 kV and above voltage class substation equipment | PDF p. 345 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0382 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xiv. If OEM was contacted after failure, its recommendation / remark / report/ MoM | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xiv. If OEM was contacted after failure, its recommendation / remark / report/ MoM | 220 kV and above voltage class substation equipment | PDF p. 350 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0383 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Flags: C/P-- DPO, DPSPU, CB trip circuit 1/2 faulty R/P-- R, Y, B-ph trip, A/R lockout, Z-1, CS, 86B, K86R, loc-3.839 km, Ir-12.18 kA. xx. Details of tests done after failure: Replaced by new breaker | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Flags: C/P-- DPO, DPSPU, CB trip circuit 1/2 faulty R/P-- R, Y, B-ph trip, A/R lockout, Z-1, CS, 86B, K86R, loc-3.839 km, Ir-12.18 kA. xx. Details of tests done after failure: Replaced by new breaker | 220 kV and above voltage class substation equipment | PDF p. 351 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0384 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | of Red Phase got Damaged due to some internal fault on 20.08.2023. The damaged LA has been replaced with new one of Elektrolites make Sr.No.76 and commissioned on dated 21.08.2023 at 17:36 Hrs. xix. Details of protection operated: Main-I | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of Red Phase got Damaged due to some internal fault on 20.08.2023. The damaged LA has been replaced with new one of Elektrolites make Sr.No.76 and commissioned on dated 21.08.2023 at 17:36 Hrs. xix. Details of protection operated: Main-I | 220 kV and above voltage class substation equipment | PDF p. 355 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0385 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | A,Z-1, 212.7 Meter Main -II L1N, Z-1, 0.236 K.M xx. Details of tests done after failure: No test was possible as the LA was completely | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | A,Z-1, 212.7 Meter Main -II L1N, Z-1, 0.236 K.M xx. Details of tests done after failure: No test was possible as the LA was completely | 220 kV and above voltage class substation equipment | PDF p. 355 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0386 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxii. Probable cause of failure: As LA got burs therefore cause of failure could | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xxii. Probable cause of failure: As LA got burs therefore cause of failure could | 220 kV and above voltage class substation equipment | PDF p. 355 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0387 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | 220 kV Jalandhar-Jamalpur Ckt 2 burst with heavy noise and Caught fire. xix. Details of protection operated: MICOM P-442 | NOT COVERED | NOT VERIFIED | 220 kV | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 359 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0388 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | Started Phase-AN, Tripped phase- ABC, Zone- 1 Fault Location – 93.57 meter REL-650 –Loop L1-N Zone -1 xx. Details of tests done after failure: No test was possible as the LA was completely | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Started Phase-AN, Tripped phase- ABC, Zone- 1 Fault Location – 93.57 meter REL-650 –Loop L1-N Zone -1 xx. Details of tests done after failure: No test was possible as the LA was completely | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 359 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0389 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: No surge arrestor physically got damaged. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: No surge arrestor physically got damaged. | 220 kV and above voltage class substation equipment | PDF p. 361 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0390 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Switchyard | NOT VERIFIED | Inspection | Inspection | INSPECTION | 12.41 hrs and heavy sound observed from switchyard. On inspection, R phase LA found broken and suspended. xix. Details of protection operated: Relay Details- Distance Protection Operated- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 365 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0391 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | loud sound and after yard inspection it was found that R-Phase LA of said line found busted zone-1opted 12.57.246 sec xix. Details of protection operated: 21M1-R, Y phase operated, Zone-1 Operated, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 367 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0392 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | PSB detected 21M2- -R,Y phase operated, Zone-1 Operated, F.D-0.1 86A,86B, 86L/O, xx. Details of tests done after failure: Not done (As LA Got Busted Completely) | NOT COVERED | NOT VERIFIED | 86A; 86L | NOT COVERED | PSB detected 21M2- -R,Y phase operated, Zone-1 Operated, F.D-0.1 86A,86B, 86L/O, xx. Details of tests done after failure: Not done (As LA Got Busted Completely) | 220 kV and above voltage class substation equipment | PDF p. 367 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0393 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | both end, Indication Indore end-Rph Z-1 Loc- 5.5 km, Fc-16.975 kA Jetura end-Rph Z-1, Loc- 29.2 km, FC-4.82 kА xx. Details of tests done after failure: LA Burst | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | both end, Indication Indore end-Rph Z-1 Loc- 5.5 km, Fc-16.975 kA Jetura end-Rph Z-1, Loc- 29.2 km, FC-4.82 kА xx. Details of tests done after failure: LA Burst | 220 kV and above voltage class substation equipment | PDF p. 375 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0394 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | Itarsi-2 tripped ZONE 1, Y&B Phase/38.47 kM/Iy-9.53 kA/169.59 kA. Line Declared Faulty on dated 25.09.2023 at 00.12 Hrs. Line Charged & again Tripped at 00.15 hrs With Failure B Phase L.A. xix. Details of protection operated: DPR Main 1 & 2 Operated | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Itarsi-2 tripped ZONE 1, Y&B Phase/38.47 kM/Iy-9.53 kA/169.59 kA. Line Declared Faulty on dated 25.09.2023 at 00.12 Hrs. Line Charged & again Tripped at 00.15 hrs With Failure B Phase L.A. xix. Details of protection operated: DPR Main 1 & 2 Operated | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 377 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0395 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: As the LA got completely burst, No Tests | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: As the LA got completely burst, No Tests | 220 kV and above voltage class substation equipment | PDF p. 377 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0396 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | 8) At 18:37 Hrs on Dated 08.07.2023 Undertaking to take 220 kV TSS- I line in service is submitted to LD Nagpur via Email. 9) At 18:38 Hrs on Dated 08.07.2023 Permission granted by LD Nagpur telephonically to Charge 220 kV TSS- I line. 10) At 18:42 Hrs on Dated 08.07.2023 220 kV TSS- I line is charged and stood ok. 11) At 18:43 Hrs on Dated 08.07.2023 220 kV TSS- I line charging time is conveyed to LD Nagpur. xix. Details of protection operated: Before tripping of 220 kV TBC bay i.e. before bursting of R-ph LA:- No Indications on 220 kV TSS-I Line/Bay After tripping of 220 kV TBC bay i.e after bursting of R-ph LA:- Window indications at 220 kV Badnera S/s 1) Distance Protection operated 2) Zone I trip 3) R ph Trip Relay indications at 220 kV Badnera S/s: | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 379 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0397 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 1) A Trip, N Z1, 2) Distance- 0.107 m, 3) R phase, Zone-1 4)Fault current Ir –10.29kA,Ic – 2.417A 5) Master Trip 863C xx. Details of tests done after failure: As LA burst and beyond repairable, no test carried out after failure. xxi. Observations | NOT COVERED | NOT VERIFIED | 2.417A; 863C | NOT COVERED | 1) A Trip, N Z1, 2) Distance- 0.107 m, 3) R phase, Zone-1 4)Fault current Ir –10.29kA,Ic – 2.417A 5) Master Trip 863C xx. Details of tests done after failure: As LA burst and beyond repairable, no test carried out after failure. xxi. Observations | 220 kV and above voltage class substation equipment | PDF p. 380 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0398 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | already off at Flagship S/s xx. Details of tests done after failure: LA IR values measured. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | already off at Flagship S/s xx. Details of tests done after failure: LA IR values measured. | 220 kV and above voltage class substation equipment | PDF p. 382 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0399 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | flashover. Faulty LA replaced and 220/132 kV 100 MVA ICT No.2 Charged on 16.08.2023 @ 02:20 hrs. xix. Details of protection operated Differential protection operated Master trip HV Diff trip Diff R Y B Diff HS Master trip LV xx. Details of tests done after failure: Not taken as LA got burst | NOT COVERED | NOT VERIFIED | 132 kV; 100 MVA | NOT COVERED | flashover. Faulty LA replaced and 220/132 kV 100 MVA ICT No.2 Charged on 16.08.2023 @ 02:20 hrs. xix. Details of protection operated Differential protection operated Master trip HV Diff trip Diff R Y B Diff HS Master trip LV xx. Details of tests done after failure: Not taken as LA got burst | 220 kV and above voltage class substation equipment | PDF p. 384 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0400 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: As LA was burst, no tests done after failure. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: As LA was burst, no tests done after failure. | 220 kV and above voltage class substation equipment | PDF p. 386 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0401 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Failure / Failure Analysis | Fire Protection | FAILURE_ANALYSIS | xxii. Probable cause of failure: R Ph,Y Ph & B Ph LA burst due to Transformer fire. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | xxii. Probable cause of failure: R Ph,Y Ph & B Ph LA burst due to Transformer fire. | 220 kV and above voltage class substation equipment | PDF p. 388 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0402 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Bushing of 400/220 kV 501 MVA ICT-3 was burst; it also damaged the HV side LA. xix. Details of protection operated: Differential Protection | NOT COVERED | NOT VERIFIED | 220 kV; 501 MVA | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 390 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0403 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | xx. Details of tests done after failure: Due to bursting of HV bushing, collars of this | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Due to bursting of HV bushing, collars of this | 220 kV and above voltage class substation equipment | PDF p. 390 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0404 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events/ Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events/ Description of fault | 220 kV and above voltage class substation equipment | PDF p. 392 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0405 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Inspection | SAFETY | 220/66 kV PTR-2 tripped on differential and REF protection operated. At the time of tripping huge sound was heard and after inspection it is found that B-PH HV LA of 50 MVA 220/66 kV PTR-2 burst. Hence, after tripping HV equipment isolator and LV bus isolator opened & LA replaced. xix. Details of protection operated: W.I.: Differential Protection Trip, HV REF trip | NOT COVERED | NOT VERIFIED | 66 kV; 50 MVA | 220/66 kV PTR-2 tripped on differential and REF protection operated. At the time of tripping huge sound was heard and after inspection it is found that B-PH HV LA of 50 MVA 220/66 kV PTR-2 burst. Hence, after tripping HV equipment isolator and LV bus isolator opened & LA replaced. xix. Details of protection operated: W.I.: Differential Protection Trip, HV REF trip | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 392 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0406 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | R. I.: LED:Gen. trip, Rph diff, Yph diff, Bph diff, HS1, HS2. REF relay, Master trip relay xx. Details of tests done after failure: LA was burst hence test not carried out. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | R. I.: LED:Gen. trip, Rph diff, Yph diff, Bph diff, HS1, HS2. REF relay, Master trip relay xx. Details of tests done after failure: LA was burst hence test not carried out. | 220 kV and above voltage class substation equipment | PDF p. 392 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0407 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | W/I:- Distance protection operated, A/R Lockout R/I:- R ph, Y ph, B ph trip. Fault Current: - IL1-1.87 kA, IL2-5.42 kA, IL3-1.10 kA Fault Location- 0.1 km IR:- 20111308 ohm xx. Details of tests done after failure: LA Burst | NOT COVERED | NOT VERIFIED | 20111308 ohm | NOT COVERED | W/I:- Distance protection operated, A/R Lockout R/I:- R ph, Y ph, B ph trip. Fault Current: - IL1-1.87 kA, IL2-5.42 kA, IL3-1.10 kA Fault Location- 0.1 km IR:- 20111308 ohm xx. Details of tests done after failure: LA Burst | 220 kV and above voltage class substation equipment | PDF p. 394 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0408 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | IL1=1.44 kA, IL2=1.02 kA, IL3=0.15 kA xx. Details of tests done after failure: Flashed over | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | IL1=1.44 kA, IL2=1.02 kA, IL3=0.15 kA xx. Details of tests done after failure: Flashed over | 220 kV and above voltage class substation equipment | PDF p. 396 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0409 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Fault Location - Y-phase-E, zone1, Fault Duration- 59.96 ms, Ia- 105.3 A, Ib- 28.66 kA, Ic- 67.27 A, Fault Resistance- 2.95 ohm Dp-2: F.L- Y-phase-E, zone1, F.D- 0.2 km, Ia- 0.09 kA, Ib- 32.80 kA, Ic- 0.07 kA. xx. Details of tests done after failure: -- | NOT COVERED | NOT VERIFIED | 105.3 A; 67.27 A; 2.95 ohm | NOT COVERED | Fault Location - Y-phase-E, zone1, Fault Duration- 59.96 ms, Ia- 105.3 A, Ib- 28.66 kA, Ic- 67.27 A, Fault Resistance- 2.95 ohm Dp-2: F.L- Y-phase-E, zone1, F.D- 0.2 km, Ia- 0.09 kA, Ib- 32.80 kA, Ic- 0.07 kA. xx. Details of tests done after failure: -- | 220 kV and above voltage class substation equipment | PDF p. 400 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0410 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | General | SAFETY | Arrester of Generator Transformer -2 and Generator Transformer -2 tripped on over current protection. xxvi. Details of protection operated: Generator Transformer -2 Over current fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Arrester of Generator Transformer -2 and Generator Transformer -2 tripped on over current protection. xxvi. Details of protection operated: Generator Transformer -2 Over current fault | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 402 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0411 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Failure | SAFETY | protection Numerical relay read the 29.19 kA current in R-phase and Generator Transformer -2 Over current fault protection Numerical relay generated instantaneous Class-A trip command and Unit#2 Tripped on Generator electrical protection activated. xxvii. Details of tests done after failure: Equipment failed (Blasted) and replaced with | NOT COVERED | NOT VERIFIED | NOT VERIFIED | protection Numerical relay read the 29.19 kA current in R-phase and Generator Transformer -2 Over current fault protection Numerical relay generated instantaneous Class-A trip command and Unit#2 Tripped on Generator electrical protection activated. xxvii. Details of tests done after failure: Equipment failed (Blasted) and replaced with | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 402 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0412 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 38.3 Km at khuskhera End. No any protection operated at 220 kV GSS KGBAS end. xx. Details of tests done after failure: Burst | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 38.3 Km at khuskhera End. No any protection operated at 220 kV GSS KGBAS end. xx. Details of tests done after failure: Burst | 220 kV and above voltage class substation equipment | PDF p. 408 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0413 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 135. Failure report of 400 kV SA at PGCIL Navsari Substation of Torrent Power Limited | NOT COVERED | NOT VERIFIED | 400 kV | NOT COVERED | 135. Failure report of 400 kV SA at PGCIL Navsari Substation of Torrent Power Limited | 220 kV and above voltage class substation equipment | PDF p. 409 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0414 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: Fault observed during IR measured Testing | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Fault observed during IR measured Testing | 220 kV and above voltage class substation equipment | PDF p. 410 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0415 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | ends on 09.08.2024 at 17:32 Hrs due to Ro Jumper cut at location No. 162, declared by AE/Lines/Gummidipoondi. After the rectification of Jumper cut, Test charged at 22.21 Hrs. Observed that Y & line voltage was zero, immediately hand tripped on emergency basis. xix. Details of protection operated: Main 1 Relay Indications: PSB/ VT Fail/ | NOT COVERED | NOT VERIFIED | NOT VERIFIED | ends on 09.08.2024 at 17:32 Hrs due to Ro Jumper cut at location No. 162, declared by AE/Lines/Gummidipoondi. After the rectification of Jumper cut, Test charged at 22.21 Hrs. Observed that Y & line voltage was zero, immediately hand tripped on emergency basis. xix. Details of protection operated: Main 1 Relay Indications: PSB/ VT Fail/ | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 412 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0416 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | BRC/SOTF Main 2 Relay Indications: VT fails. NIL xx. Details of tests done after failure: Ratio Test: Core 1: 0.168V, Core 2: 0.139V, | NOT COVERED | NOT VERIFIED | 0.168V; 0.139V | NOT COVERED | BRC/SOTF Main 2 Relay Indications: VT fails. NIL xx. Details of tests done after failure: Ratio Test: Core 1: 0.168V, Core 2: 0.139V, | 220 kV and above voltage class substation equipment | PDF p. 412 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0417 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Inspection | FAILURE_ANALYSIS | on distance protection. On inspection of the yard blue phase LA found failed. xix. Details of protection operated: 230 kV manali-2 feeders main 1: start C, Trip- | NOT COVERED | NOT VERIFIED | 230 kV | NOT COVERED | on distance protection. On inspection of the yard blue phase LA found failed. xix. Details of protection operated: 230 kV manali-2 feeders main 1: start C, Trip- | 220 kV and above voltage class substation equipment | PDF p. 414 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0418 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | ABC, Zone-1, and IC: 24.5 kA. Fault duration 50.01 ms LOC:00 mts Main 02 NIL xx. Details of tests done after failure: LA on stack flashed over. Hence no test was | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ABC, Zone-1, and IC: 24.5 kA. Fault duration 50.01 ms LOC:00 mts Main 02 NIL xx. Details of tests done after failure: LA on stack flashed over. Hence no test was | 220 kV and above voltage class substation equipment | PDF p. 414 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0419 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | of the equipment in the past since its commissioning) xviii. Sequence of events/ Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of the equipment in the past since its commissioning) xviii. Sequence of events/ Description of fault | 220 kV and above voltage class substation equipment | PDF p. 416 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0420 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 1, Distance-6.2 Km, 1.3.15 kA, 86 A Sohawal (PGCIL) end R, N, 86A MI- Relay distance 86.6 Km, IR 2:38 KA M2-Relay distance 89.9 Km, IR 1.8KA xx. Details of tests done after failure: - | NOT COVERED | NOT VERIFIED | 86 A; 86A | NOT COVERED | 1, Distance-6.2 Km, 1.3.15 kA, 86 A Sohawal (PGCIL) end R, N, 86A MI- Relay distance 86.6 Km, IR 2:38 KA M2-Relay distance 89.9 Km, IR 1.8KA xx. Details of tests done after failure: - | 220 kV and above voltage class substation equipment | PDF p. 418 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0421 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Relay-Differential LV side flag-86A, 86B xx. Details of tests done after failure: - | NOT COVERED | NOT VERIFIED | 86A | NOT COVERED | Relay-Differential LV side flag-86A, 86B xx. Details of tests done after failure: - | 220 kV and above voltage class substation equipment | PDF p. 420 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0422 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events / Description of fault (SOE with time stamp) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events / Description of fault (SOE with time stamp) | 220 kV and above voltage class substation equipment | PDF p. 424 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0423 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Capacitance | TESTING | iv. Rating (Voltage/ current/ current ratio/ Capacitance/ MCOV etc., as applicable) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 429 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0424 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 20:57 hrs xix. Details of protection operated: Phase- YN, Zone-1, distance - 0.144 Km, fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 20:57 hrs xix. Details of protection operated: Phase- YN, Zone-1, distance - 0.144 Km, fault | 220 kV and above voltage class substation equipment | PDF p. 430 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0425 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | current - Ia- 822 mA Ib- 2.715 A Ic- 432 mA Note- Y phase LA got damaged xx. Details of tests done after failure: N/A | NOT COVERED | NOT VERIFIED | 822 mA; 2.715 A; 432 mA | NOT COVERED | current - Ia- 822 mA Ib- 2.715 A Ic- 432 mA Note- Y phase LA got damaged xx. Details of tests done after failure: N/A | 220 kV and above voltage class substation equipment | PDF p. 430 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0426 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events / Description of fault | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (Any failure which has led to a major repair of the equipment in the past since its commissioning) xviii. Sequence of events / Description of fault | 220 kV and above voltage class substation equipment | PDF p. 432 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0427 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | DPR operated, BN -Phase, Zone-1, Fault distance 1.5 Km, Fault current 24.01 kA. 400 kV substation Sagar end indication: -DPR operated. BN -Phase, Zone-1, Fault distance 89.7 Km, Fault current 1.755 kA. xx. Details of tests done after failure: - | NOT COVERED | NOT VERIFIED | 400 kV | NOT COVERED | DPR operated, BN -Phase, Zone-1, Fault distance 1.5 Km, Fault current 24.01 kA. 400 kV substation Sagar end indication: -DPR operated. BN -Phase, Zone-1, Fault distance 89.7 Km, Fault current 1.755 kA. xx. Details of tests done after failure: - | 220 kV and above voltage class substation equipment | PDF p. 440 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0428 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | due to its insulation failure. xix. Details of protection operated: DPR operated from both the ends, Indication | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | due to its insulation failure. xix. Details of protection operated: DPR operated from both the ends, Indication | 220 kV and above voltage class substation equipment | PDF p. 444 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0429 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | xvi. a) Details of previous maintenance (Activities carried out in previous maintenance including the tests conducted, periodicity of the maintenance activities) b) Whether any abnormality observed in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 445 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0430 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | these tests. If yes, attach the test reports. c) What steps were taken to address the | these tests. If yes, attach the test reports. c) What steps were taken to address the | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 445 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0431 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Failure | SAFETY | xix. Details of protection operated: 220 kV Pusad-Yavatmal line tripped. Area interrupted- Nil. xx. Details of tests done after failure: NA | NOT COVERED | NOT VERIFIED | 220 kV | xix. Details of protection operated: 220 kV Pusad-Yavatmal line tripped. Area interrupted- Nil. xx. Details of tests done after failure: NA | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 447 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0432 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | ph-E, Fault current IL1- 24.76 kA, Distance- 0.0 km xx. Details of tests done after failure: Faulty / damaged equipment is bypassed. For | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | ph-E, Fault current IL1- 24.76 kA, Distance- 0.0 km xx. Details of tests done after failure: Faulty / damaged equipment is bypassed. For | 220 kV and above voltage class substation equipment | PDF p. 451 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0433 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS, Substation | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | 157. Failure report of 220 kV GIS Disconnector at Saki Substation of Adani Electricity Mumbai Ltd | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 157. Failure report of 220 kV GIS Disconnector at Saki Substation of Adani Electricity Mumbai Ltd | 220 kV and above voltage class substation equipment | PDF p. 452 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0434 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: Visual Inspection done under the supervision | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: Visual Inspection done under the supervision | 220 kV and above voltage class substation equipment | PDF p. 453 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0435 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | with flags RP- Gen trip, R phase trip, Y phase trip, B phase trip, Z-2, IL1=0.82 KA, IL2=1.15 KA IL3=6.47 KA, distance=20 km. (Flags of other end breaker was opened manually at Pratap vihar end) Reason: DS3 isolator (Line side) of B phase hybrid unit got damaged. At the same time 220 kV Pratap vihar-Sahibabad line tripped with flags Z-2, Ia=473 A, Ib= 521 A, Ic=8.2 KA, Fault distance = 12.62 km Fault duration =399.7 ms (other end flags breaker was opened manually at Pratap vihar end) After isolating damaged hybrid unit 220 kV Pratap vihar-Sahibabad line charged at 18:45 hrs and 220 kV Pratapvihar- Muradnagar line is charged by using hybrid unit of 220 kV Indirapuaram–Pratapvihar line xix. Details of protection operated: 220 kV Pratapvihar-Muradnagar line tripped | NOT COVERED | NOT VERIFIED | 220 kV; 473 A; 521 A | with flags RP- Gen trip, R phase trip, Y phase trip, B phase trip, Z-2, IL1=0.82 KA, IL2=1.15 KA IL3=6.47 KA, distance=20 km. (Flags of other end breaker was opened manually at Pratap vihar end) Reason: DS3 isolator (Line side) of B phase hybrid unit got damaged. At the same time 220 kV Pratap vihar-Sahibabad line tripped with flags Z-2, Ia=473 A, Ib= 521 A, Ic=8.2 KA, Fault distance = 12.62 km Fault duration =399.7 ms (other end flags breaker was opened manually at Pratap vihar end) After isolating damaged hybrid unit 220 kV Pratap vihar-Sahibabad line charged at 18:45 hrs and 220 kV Pratapvihar- Muradnagar line is charged by using hybrid unit of 220 kV Indirapuaram–Pratapvihar line xix. Details of protection operated: 220 kV Pratapvihar-Muradnagar line tripped | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 455 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0436 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 159. Failure report of 220 kV Isolator at Kudankulam Nuclear Power Project of NPCIL | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 159. Failure report of 220 kV Isolator at Kudankulam Nuclear Power Project of NPCIL | 220 kV and above voltage class substation equipment | PDF p. 456 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0437 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Failure | SAFETY | ICT10 breaker at 13:22 Hrs dated on 03.12.2024. ICT10 Interconnecting transformer breaker got tripped at 13:24 Hrs due to 87BB (ADA) trip, because of ADL14GS100 R phase Disconnector component failure. xix. Details of protection operated: Bus bar Differential protection (87BB) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | ICT10 breaker at 13:22 Hrs dated on 03.12.2024. ICT10 Interconnecting transformer breaker got tripped at 13:24 Hrs due to 87BB (ADA) trip, because of ADL14GS100 R phase Disconnector component failure. xix. Details of protection operated: Bus bar Differential protection (87BB) | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 457 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0438 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 160. Failure report of 220 kV Cable at Aarey EHV Substation of Adani Transmission Ltd | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | 160. Failure report of 220 kV Cable at Aarey EHV Substation of Adani Transmission Ltd | 220 kV and above voltage class substation equipment | PDF p. 458 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0439 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Capacitance | TESTING | conductor, Extruded Corrugated Aluminum sheath, Capacitance of cable - 0.191 pF i.e, Rated Current - 800A | NOT COVERED | NOT VERIFIED | 800A | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 458 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0440 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | GIS | NOT VERIFIED | Failure / Failure Analysis | GIS | FAILURE_ANALYSIS | differential protection from both ends due to 220kV Cable fault between Aarey GIS to JC-01 xx. Details of tests done after failure: (i) Physical Inspection of Cable route carried | NOT COVERED | NOT VERIFIED | 220kV | NOT COVERED | differential protection from both ends due to 220kV Cable fault between Aarey GIS to JC-01 xx. Details of tests done after failure: (i) Physical Inspection of Cable route carried | 220 kV and above voltage class substation equipment | PDF p. 459 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0441 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xx. Details of tests done after failure: A gas purity test detected high SO2 levels in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xx. Details of tests done after failure: A gas purity test detected high SO2 levels in | 220 kV and above voltage class substation equipment | PDF p. 461 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0442 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | other end. xix. Details of tests done after failure: Physically Inspection & IR Test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | other end. xix. Details of tests done after failure: Physically Inspection & IR Test | 220 kV and above voltage class substation equipment | PDF p. 463 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0443 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation, Switchyard | NOT VERIFIED | Maintenance | General | MAINTENANCE | Annexure-III: General Guidelines for Substation/ Switchyard Operation & Maintenance Activities by Transmission Utilities | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 464 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0444 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Substation, Switchyard | NOT VERIFIED | Maintenance | General | MAINTENANCE | Substation/ Switchyard Operation & Maintenance Activities (Issued vide CEA letter no: CEA-PS-14-12/18/2022-PSETD Division dated 22.06.2023) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 465 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0445 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Bushing | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | 16. Oil parameters of tank oil Yearly 17. Thermo-vision Scanning Half Yearly 18. Other maintenance checks: (a) Checking of bushing oil level Monthly (b) Checking of oil level in conservator Monthly (c) Checking of oil level in OLTC conservator Monthly | NOT COVERED | Oil parameters of tank oil Yearly 17 | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 465 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0446 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | (d) Checking of oil leaks Monthly (e) Checking condition of silica gel in breather Monthly (f) Checking of oil level in oil seal of breather Monthly (g) Manual actuation of cooler fans and oil pumps Monthly (h) External cleaning of all bushings Yearly (i) External cleaning of radiators Yearly (j) Checking of marshalling box/control cubicles: cleaning, | NOT COVERED | (d) Checking of oil leaks Monthly (e) Checking condition of silica gel in breather Monthly (f) Checking of oil level in oil seal of b | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 466 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0447 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Testing | Transformer Oil | TESTING | (k) Maintenance of OLTC driving mechanism Yearly (l) Checking/testing of buchholz relay by oil draining Yearly (m) Electrical checking/testing of Pressure Relief Device | NOT COVERED | (k) Maintenance of OLTC driving mechanism Yearly (l) Checking/testing of buchholz relay by oil draining Yearly (m) Electrical checking/testing of Pr | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 466 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0448 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | (PRD), buchholz relay, rapid pressure rise relay, OLTC surge relay, checking of alarm/trip | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 466 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0449 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (n) Checking of gaskets Yearly (o) Checking of Oil Temperature Indicator (OTI)/Winding | NOT COVERED | (n) Checking of gaskets Yearly (o) Checking of Oil Temperature Indicator (OTI)/Winding | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 466 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0450 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Temperature Indicator (WTI) and tap position indicator and top up of oil in pockets, if required | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 466 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0451 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 17. Checking of space heater Yearly 18. Dynamic Contact Resistance Measurement (DCRM) test 2 Yearly | 17. Checking of space heater Yearly 18. Dynamic Contact Resistance Measurement (DCRM) test 2 Yearly | Checking of space heater Yearly 18 | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 468 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0452 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Annexure-IV: Format for report of failure of the Transformer/Reactors or Other equipment | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Annexure-IV: Format for report of failure of the Transformer/Reactors or Other equipment | 220 kV and above voltage class substation equipment | PDF p. 472 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0453 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | xi. Sequence of events/ Description of fault (SOE with time stamp, Protection operated during fault) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xi. Sequence of events/ Description of fault (SOE with time stamp, Protection operated during fault) | 220 kV and above voltage class substation equipment | PDF p. 473 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0454 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xii. Details of Tests done after failure (What tests were conducted after the discovery of failure. If no tests were conducted, reasons for the same may be stated.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xii. Details of Tests done after failure (What tests were conducted after the discovery of failure. If no tests were conducted, reasons for the same may be stated.) | 220 kV and above voltage class substation equipment | PDF p. 473 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0455 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | xiii. Observations (Visual observations e.g. bulging of tank, fire, any leakage of oil, damage to various components of transformer and nearby equipment / material etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 473 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0456 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xv. If OEM representative had inspected the equipment or visited the site after failure, their remarks, MoM etc. may be attached. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | xv. If OEM representative had inspected the equipment or visited the site after failure, their remarks, MoM etc. may be attached. | 220 kV and above voltage class substation equipment | PDF p. 473 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0457 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | (Activities carried out in previous maintenance including the tests conducted, periodicity of the maintenance activities) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 474 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0458 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | xxxvi. Type of Fire protection provided (Emulsifier system Injection based fire Protection system/ for based protection etc.) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | xxxvi. Type of Fire protection provided (Emulsifier system Injection based fire Protection system/ for based protection etc.) | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 475 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0459 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | xxxix. Whether short circuit test was carried out on this transformer or same design transformer or short circuit with stand, capability was verified on the basis of calculation? | xxxix. Whether short circuit test was carried out on this transformer or same design transformer or short circuit with stand, capability was verified on the basis of calculation? | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 475 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0460 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker, Substation | NOT VERIFIED | Failure / Failure Analysis | Circuit Breaker | FAILURE_ANALYSIS | B. Proforma for failure report of other substation equipment [Circuit Breaker, Instrument | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | B. Proforma for failure report of other substation equipment [Circuit Breaker, Instrument | 220 kV and above voltage class substation equipment | PDF p. 476 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0461 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CVT, Surge Arrester | NOT VERIFIED | Design / Technical Reference | Surge Arrester | DESIGN_REFERENCE | Transformers (CT/ PT/ CVT), Wave Trap, Isolator, Surge Arrester, Coupling Capacitor, Cable] | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | 220 kV and above voltage class substation equipment | PDF p. 476 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0462 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | the test reports. (c) What steps were taken to address the abnormality? xvii. Details of previous failure (Any failure which has led to a major repair of the equipment in the past since its commissioning) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | the test reports. (c) What steps were taken to address the abnormality? xvii. Details of previous failure (Any failure which has led to a major repair of the equipment in the past since its commissioning) | 220 kV and above voltage class substation equipment | PDF p. 477 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D06-C0463 | D06 | SS_Report_on_SSE_failre_July23_Dec24_with_Covering_letter.pdf | Report of Standing Committee of Experts on Failure of 220 kV & Above Voltage Class Substation Equipment (July 2023 - Dec 2024) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | xxiii. Attach reports of tests during pre-commissioning, periodic maintenance and after failure; Photographs of the failed equipment etc. | NOT COVERED | Attach reports of tests during pre-commissioning, periodic maintenance and after failure; Photographs of the failed equipment etc | NOT VERIFIED | NOT COVERED | xxiii. Attach reports of tests during pre-commissioning, periodic maintenance and after failure; Photographs of the failed equipment etc. | 220 kV and above voltage class substation equipment | PDF p. 477 | CENTRAL ELECTRICITY AUTHORITY | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0001 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING | B.1 Drum oil test - BDV, PPM, Tan Delta, Resistivity and IFT Number of sample to be tested as per customer standard procedure. | B.1 Drum oil test - BDV, PPM, Tan Delta, Resistivity and IFT Number of sample to be tested as per customer standard procedure. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 188 | A. | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0002 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Ensure filter M/C outlet pipe (heated oil pipe) must be connected at bottom valve of main tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 189 | C.3 | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0003 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Drums containing oil which have been dispatched separately should be examined carefully for leaks or any sign of tampering. All drums are dispatched filled up to their capacity and any shortage should be reported. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 192 | 21 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0004 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Dismantled equipment and components are packed to be protected against normal handling and transport stresses. The instructions for lifting given on the packages, must be complied with to avoid damages. Goods stored outdoors must not be placed directly on the ground, and should be covered carefully with tarpaulin or similar material. Oil drums should be stored in horizontal (lying) position with both the bungs also in horizontal position. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 193 | 22 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0005 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Bushing | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Lifting devices on the transformer tank are dimensioned for lifting of the complete transformer filled with oil. The positioning of the lifting devices, permissible lifting angles, minimum height to crane hook and transformer weight, appear from the OGA drawings. Check at lifting of complete transformer that the lifting wires/ropes are not in contact with bushing or other components on the cover. For lifting with hydraulic jacks, the transformer is provided with jacking pads dimensioned for lifting of complete transformer filled with oil. The positions of the pads appear on the OGA drawings. If active part is to be lifted refer instructions given in clause 2.7. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Lifting devices on the transformer tank are dimensioned for lifting of the complete transformer filled with oil. The positioning of the lifting devices, permissible lifting angles, minimum height to crane hook and transformer weight, appear from the OGA drawings. Check at lifting of complete transformer that the lifting wires/ropes are not in contact with bushing or other components on the cover. For lifting with hydraulic jacks, the transformer is provided with jacking pads dimensioned for lifting of complete transformer filled with oil. The positions of the pads appear on the OGA drawings. If active part is to be lifted refer instructions given in clause 2.7. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 193 | 22 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0006 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | b) Transformer/reactor should be placed on the foundation so that easy access is available all around and diagram plates, thermometers, valves, oil gauges, etc. can be easily reached or read. Adequate electrical clearances are also to be provided from various live points of the transformer to earthed parts. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 193 | 22 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0007 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Bushing, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | f) Where rollers are fitted, suitable rails or tracks should be used and the wheels locked to prevent accidental movement of the transformer. Where walls are provided, it should be ensured that the transformer gets a good ventilation as mentioned above for indoor transformers. Provision should be made for the emergency drainage of the oil from the transformers (e.g. in case of fire in neighboring apparatus or bushing or the transformer tank), by surrounding the transformer plinth with sump filled with small pebbles. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 194 | 23 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0008 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | 2.1.6 INTERNAL INSPECTION AND CHECK POINTS FOR ASSEMBLING THE TRANSFORMER/REACTOR | 2.1.6 INTERNAL INSPECTION AND CHECK POINTS FOR ASSEMBLING THE TRANSFORMER/REACTOR | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 194 | 23 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0009 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | 12. Check that the bushing leads set without being too close to ground or other points of different potential. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 194 | 23 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0010 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 1. Fire-fighting equipment shall be available at the oil-treatment equipment as well as at work on and adjacent to the transformer. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 195 | 24 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0011 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | 2. Welding work on or adjacent to the transformer shall be avoided, but if this is not possible, the work shall be supervised by fire-protection personnel. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 195 | 24 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0012 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 4. Transformer tank, control cabinet etc. as well as assembling and oil treatment equipment shall be connected with the permanent earthing system of the station. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 195 | 24 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0013 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | 11. Fibrous cleaning material should not be used as it can deteriorate oil when mixed with it. | 11. Fibrous cleaning material should not be used as it can deteriorate oil when mixed with it. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 195 | 24 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0014 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 13. A transformer/reactor is best protected from damp hazard by circulating warm, dry, de-aerated oil through it until it temperature is 5 °C to 100 °C above ambient. This should be done before allowing external excess to the interior of the tank. The warm oil should be circulated all the time transformer is open to atmosphere, | NOT COVERED | NOT VERIFIED | 5 °C; 100 °C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 195 | 24 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0015 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 14. Oil pump & all joints in the oil pipe work should be airtight to avoid entrance of air through leakage joints. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 195 | 24 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0016 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | General | SAFETY | 16. Objects which-despite all precaution are dropped inside transformer/reactor, must absolutely be brought up from the equipment. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 16. Objects which-despite all precaution are dropped inside transformer/reactor, must absolutely be brought up from the equipment. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 196 | 25 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0017 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Bushing | NOT VERIFIED | Installation | Bushing | INSTALLATION | Assembling of bushings is carried out according to bushings installation manual available. In case of draw rod / lead connection of bushing with transformer lead, half connector joint to be insulated with 3 layers of crepe paper after making proper connection. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 196 | 25 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0018 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The shut-off valves against the transformer tank shall be closed until the oil-filling is started. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 196 | 25 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0019 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The conservator, which may be with or without aircell is assembled either on the transformer, or on a separate frame. Before the conservator is assembled it shall be checked that belonging equipment -e.g. Oil-level indicator -functions satisfactorily. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 196 | 25 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0020 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The breather is connected to the oil conservator, and it is very important that joints and couplings in the pipe between breather and conservator are air tight. Refer Clause 2.6 for detailed instruction for oil filling. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 197 | 26 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0021 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Pipes with flanges for connection of conservator, radiators, as well as pipes for equalizing of turrets etc. are mostly delivered completely ready for assembling according to OGA & part list. In certain cases -e.g. at a separately assembled oil conservator certain fitting and welding of pipes and flanges on site is however required. Instruction for such assembly of external pipes is given in Clause 2.3. Before assembly, all associated pipework for cooler system/radiators to be physically inspected for the presence of any dirt/dust etc. and all visible dirt/dust to be thoroughly cleaned with clean cloth. Individual radiator/cooler and pipework to be flushed with compressed air followed by carrying out Pressure test on individual radiator/cooler Bank to check any leakages/damages before start of Erection at site | Pipes with flanges for connection of conservator, radiators, as well as pipes for equalizing of turrets etc. are mostly delivered completely ready for assembling according to OGA & part list. In certain cases -e.g. at a separately assembled oil conservator certain fitting and welding of pipes and flanges on site is however required. Instruction for such assembly of external pipes is given in Clause 2.3. Before assembly, all associated pipework for cooler system/radiators to be physically inspected for the presence of any dirt/dust etc. and all visible dirt/dust to be thoroughly cleaned with clean cloth. Individual radiator/cooler and pipework to be flushed with compressed air followed by carrying out Pressure test on individual radiator/cooler Bank to check any leakages/damages before start of Erection at site | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 197 | 26 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0022 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Accessories like cooling fans, pumps, OLTC and components for supervision and control, oil-level indicator, flow indicators, gauges, Buchholz relay, PRV, thermometers etc. are assembled according to leaflet/description valid for the components (refer Vol. I). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 197 | 26 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0023 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The sealing system normally used against oil and gas in BHEL's transformers and belonging components has rubber gaskets in grooves and nitrile rubber bonded cork gaskets at other places. Refer clause 2.8 for general information and assembly instructions for gasket mounting. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 197 | 26 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0024 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY | The completely mounted Transformer is oil-filled according to directions in Clause 2.5 & 2.6. The oil shall be treated according to Clause 2.4. The lower and upper shut-off valves for radiators/coolers and possible headers shall be open during evacuation and oil-filling. If coolers are placed on suspension beams, which are mounted at right angle to the tank, the suspension beams shall be supported against the ground during the evacuation. Also radiators mounted on the tank wall shall be supported in a similar way. The hose for filling of oil is connected to the bottom valve of the transformer which must not be opened until the hose has been de-aerated and completely filled with oil. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The completely mounted Transformer is oil-filled according to directions in Clause 2.5 & 2.6. The oil shall be treated according to Clause 2.4. The lower and upper shut-off valves for radiators/coolers and possible headers shall be open during evacuation and oil-filling. If coolers are placed on suspension beams, which are mounted at right angle to the tank, the suspension beams shall be supported against the ground during the evacuation. Also radiators mounted on the tank wall shall be supported in a similar way. The hose for filling of oil is connected to the bottom valve of the transformer which must not be opened until the hose has been de-aerated and completely filled with oil. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 197 | 26 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0025 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | The transformer and its equipment are cleaned carefully from dirt, oil, lubricating grease, and damaged surfaces are touch-up painted with the primer paints and finish paints delivered as per clause 2.11. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0026 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Testing | Bushing | TESTING | When it is required at site to replace the Bushing (HV/ IV/ LV/ Neutral) due to reasons associated with the deviation in test results from the standard acceptable values or any other reason, following process to be adopted | When it is required at site to replace the Bushing (HV/ IV/ LV/ Neutral) due to reasons associated with the deviation in test results from the standard acceptable values or any other reason, following process to be adopted | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0027 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Drain out the oil from Transformer Main tank into the storage Tank up to the level of stress shield. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0028 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Fill the Transformer Tank with Dry Nitrogen, UHP grade of Dew point less than -50 or better, if the replacement is not planned to be carried out immediately after draining out of oil from Main Tank up to the required level. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0029 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | While carrying out the replacement, release the filled in Dry Nitrogen inside the Main Tank (as mentioned in step 3 of replacement procedure). During replacement of Bushing keep the Transformer tank pressurized from continuous flow of Dry air of UHP grade of Dew point less than -50 or better in order to avoid the ingress of moisture. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0030 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | shall be carried out after clearance of pre-erection test results from concerned Division. | shall be carried out after clearance of pre-erection test results from concerned Division. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0031 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Carry out the replacement of bushing as per BHEL standard procedure, in case of replacement of 400 KV HV bushing having half connector joint between bushing and winding lead at Turret level care shall be taken that hardware used should be of appropriate length and after connection the bolt used in connection shall not be protruded from profile of half connector. | NOT COVERED | NOT VERIFIED | 400 KV | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0032 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | During replacement the half connector joint between Bushing and winding lead shall be wrapped by three layer of Crepe paper with half overlap. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | During replacement the half connector joint between Bushing and winding lead shall be wrapped by three layer of Crepe paper with half overlap. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0033 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Inspection | Bushing | INSPECTION | Carry out the profile inspection of winding lead entering inside the bottom of stress shield of Bushing replaced. Also take the photographs of winding lead profile after replacement for record purpose. In case of any doubt during bushing replacement contact concerned Service division. | Carry out the profile inspection of winding lead entering inside the bottom of stress shield of Bushing replaced. Also take the photographs of winding lead profile after replacement for record purpose. In case of any doubt during bushing replacement contact concerned Service division. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0034 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Inspection | Bushing | INSPECTION | All Nitrile rubber cord of the inspection cover opened during the bushing replacement needs to be replaced by new Nitrile rubber cord. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0035 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | After replacement of bushing, apply vacuum in the Main Tank and start filling the filtered oil (as per BHEL standard) in the main Tank under vacuum. | After replacement of bushing, apply vacuum in the Main Tank and start filling the filtered oil (as per BHEL standard) in the main Tank under vacuum. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 198 | 27 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0036 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Commissioning | Bushing | COMMISSIONING | Carry out the de aeration from Turrets, Bushing and Main Tank, cooler bank and if required carry out conservator commissioning as per site requirement. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 199 | 28 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0037 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | After replacement carry out the Tan Delta and Capacitance measurement of the bushing replaced and provide the test results to BHEL. | After replacement carry out the Tan Delta and Capacitance measurement of the bushing replaced and provide the test results to BHEL. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 199 | 28 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0038 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Inspection | Inspection | INSPECTION | The storing place should be easily accessible for inspection and maintenance of the transformer. The bedding for the equipment should be larger than its bottom surface and dimensioned for the load. The transformer is placed on boardings or beams so that good ventilation is obtained underneath the transformer bottom. | The storing place should be easily accessible for inspection and maintenance of the transformer. The bedding for the equipment should be larger than its bottom surface and dimensioned for the load. The transformer is placed on boardings or beams so that good ventilation is obtained underneath the transformer bottom. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 199 | 28 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0039 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | A transformer without remarks may be stored up to 6 months after arrival at the site without oil-filling. During the storing time, the inert gas (nitrogen) filling shall be maintained and pressure regulated, so that exposure of active part to atmosphere is avoided. If the storage time is judged to exceed 6 months, the transformer should be provided with oil conservator including oil-level indicator and breather, and oil-filled according to Clause 2.5. "Oil filling under vacuum". Certain valves must be re- mounted to enable the oil-filling being carried out. Furthermore, at the time at oil-filling of a completely assembled transformer, certain rules in Clause 2.5 & 2.6 must be complied with absolutely. | A transformer without remarks may be stored up to 6 months after arrival at the site without oil-filling. During the storing time, the inert gas (nitrogen) filling shall be maintained and pressure regulated, so that exposure of active part to atmosphere is avoided. If the storage time is judged to exceed 6 months, the transformer should be provided with oil conservator including oil-level indicator and breather, and oil-filled according to Clause 2.5. "Oil filling under vacuum". Certain valves must be re- mounted to enable the oil-filling being carried out. Furthermore, at the time at oil-filling of a completely assembled transformer, certain rules in Clause 2.5 & 2.6 must be complied with absolutely. | NOT VERIFIED | 6 months | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 199 | 28 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0040 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | The oil quality should also be periodically monitored. If for some reason, oil filling cannot be carried out after a storage period longer than 6 months, the nitrogen pressure shall be maintained and supervised carefully. If the storage time without oil exceeds 18 months BHEL should be consulted about measures to be taken. | NOT COVERED | NOT VERIFIED | 6 months; 18 months | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 199 | 28 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0041 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 7. M Box, OLTC motor drive, Fans, Pumps, Instruments & fittings. (Heating elements provided shall be connected to supply) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 200 | 29 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0042 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | 8. Online DGA, Online moisture removal system, sudden pressure relay, Conservator isolation valve | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 200 | 29 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0043 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 3. Structures, A frames, Pipe supports, Supports for oil-conservators, radiators, control cabinets etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 200 | 29 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0044 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | Inspect the transformer/reactor periodically with regard to possible external faults and/or rust-damage. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Inspect the transformer/reactor periodically with regard to possible external faults and/or rust-damage. | BHEL-specific transformer/reactor procedure | PDF p. 200 | 29 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0045 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The positioning of the radiators/coolers is indicated on OGA drawing. These are positioned so that the highest point of the oil-pipe system is always positioned below the bottom level of the conservator. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 201 | 32 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0046 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The pipe system is provided with filter valves at the start and finish to enable pumping the oil through the system. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 201 | 32 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0047 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | The pipe having dimensions as per OGA drawing and may be provided with weld- flanges, expansion joints. No pipe part is allowed to be so long that internal inspection and cleaning will be difficult. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 201 | 32 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0048 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The pipes shall be placed so that air release plugs will be positioned at the highest point of the pipe part. The pipes shall be painted internally with a yellow, oil-resistant paint and externally according to the paint as per specification. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 201 | 32 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0049 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | Note 2: The documents, relevant to Oil, are prepared based on the IEC standard applicable as on October-2016. If user wants to refer the latest standard applicable, the confirmation shall be obtained from manufacturer. | Note 2: The documents, relevant to Oil, are prepared based on the IEC standard applicable as on October-2016. If user wants to refer the latest standard applicable, the confirmation shall be obtained from manufacturer. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0050 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Note - 3: For Mixing of oil, please refer IEC: 60296. Please ask the OEM, before mixing the oil. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0051 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | Transformer oil should be carefully handled at site to ensure satisfactory service. Drums used for transport and storage should be kept under cover. In practice owing to contamination in the containers, difficulty may be experienced in maintaining the purity of the oil when it is transferred from one vessel to another, and once a vessel or drum has been filled with moist oil it is extremely difficult to clean. Drums should be clearly marked to indicate whether they are for clean or for dirty oil and should be reserved for the type indicated. | Transformer oil should be carefully handled at site to ensure satisfactory service. Drums used for transport and storage should be kept under cover. In practice owing to contamination in the containers, difficulty may be experienced in maintaining the purity of the oil when it is transferred from one vessel to another, and once a vessel or drum has been filled with moist oil it is extremely difficult to clean. Drums should be clearly marked to indicate whether they are for clean or for dirty oil and should be reserved for the type indicated. | ng the purity of the oil when it is transferred from one vessel to another, and once a vessel or drum has been filled with moist oil it is extremely difficult to clean | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0052 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Oil drums should be stored at site preferably on pallets or Bricks layer, in horizontal | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0053 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | so that ingress of moisture is prevented. It is always recognized that storage of oil in drums is not always satisfactory, particularly when oil is stored in drums which have been bent or otherwise damaged in transit or storage, and the transfer of oil from such containers to electrical equipment should normally be through a suitable treatment plant. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0054 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Substation | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | In substations with fixed oil handling equipment like oil storage tank, the pipe work from the clean oil tank to the electrical apparatus should be kept clean and free from moisture. Where portable oil handling equipment is used, flexible pipe work and hand pump should be carefully inspected to ensure that they are free from dirt and water and should be flushed with clean oil before use. If the clean oil is being used from drums, it should have been recently tested and filling orifices of the drums should be clean. Hoses used for clean oil and dirty oil should be clearly marked and provided with plugs for sealing the ends when not in use. | In substations with fixed oil handling equipment like oil storage tank, the pipe work from the clean oil tank to the electrical apparatus should be kept clean and free from moisture. Where portable oil handling equipment is used, flexible pipe work and hand pump should be carefully inspected to ensure that they are free from dirt and water and should be flushed with clean oil before use. If the clean oil is being used from drums, it should have been recently tested and filling orifices of the drums should be clean. Hoses used for clean oil and dirty oil should be clearly marked and provided with plugs for sealing the ends when not in use. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0055 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | Special care must be taken for oil filtration machine, which is used during treatment of oil. It is to be ensured that there is on residual quantity of oil left in oil filtration machine. The paper filters or centrifuges used with filtration machine shall be cleaned or replaced periodically as per supplier's recommendation. The pipe/hoses used with filtration machine should be properly blanked after use. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0056 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Before using oil tankers and filtration plant for handling of oil, the internals/chambers need to be thoroughly cleaned using good transformer oil so that the residual of earlier used chemical/oil is removed totally. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 202 | 35 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0057 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | After reconditioning, Insulating Oil is filled into Transformer/ Reactor. As the oil comes into contact with insulating and other materials, it can no longer be considered as | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 203 | 36 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0058 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | -2012. Therefore its properties are regarded as those applicable to oil in service, even though the electrical equipment itself may not have been energized. Oil properties should be appropriate to the category and functions of the equipment (see Annexure- 4.3). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 203 | 36 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0059 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Transformers and Reactors with vacuum-proof tanks shall be filled with oil according to this method. | Transformers and Reactors with vacuum-proof tanks shall be filled with oil according to this method. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 203 | 36 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0060 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | Generally it applies that Transformers and reactors which during transport are filled with dry nitrogen on arrival at the site shall be evacuated and oil filled. Before storing, the equipment shall be inspected according to the directions given in Clause 2.1 "Reception and assembling of transformer/reactor dispatched partly dissembled and filled with nitrogen". During the storing time, overpressure shall be maintained, and nitrogen consumption checked according Clause 2.2. | Generally it applies that Transformers and reactors which during transport are filled with dry nitrogen on arrival at the site shall be evacuated and oil filled. Before storing, the equipment shall be inspected according to the directions given in Clause 2.1 "Reception and assembling of transformer/reactor dispatched partly dissembled and filled with nitrogen". During the storing time, overpressure shall be maintained, and nitrogen consumption checked according Clause 2.2. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 204 | 37 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0061 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | In Annexure 2.1 is given a flow chart of handling procedures. The pressure should be measured at different times. The pressure is OK if it is maintained according to instructions given in Clause 2.2. Reference is also drawn to para 9.0 of IS: 1866 regarding handling and filling of oil. | In Annexure 2.1 is given a flow chart of handling procedures. The pressure should be measured at different times. The pressure is OK if it is maintained according to instructions given in Clause 2.2. Reference is also drawn to para 9.0 of IS: 1866 regarding handling and filling of oil. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 204 | 37 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0062 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | (i) Blank all the openings on the Transformer / Reactor Main Tank. Transformer / Reactor Main Tank is than subjected to vacuum up to 1.00 torr (1 mm of Hg) to be pulled and maintained for 72 hrs duration. During this first dry out cycle leakages if any observed in the system to be attended and rectified in this cycle. | (i) Blank all the openings on the Transformer / Reactor Main Tank. Transformer / Reactor Main Tank is than subjected to vacuum up to 1.00 torr (1 mm of Hg) to be pulled and maintained for 72 hrs duration. During this first dry out cycle leakages if any observed in the system to be attended and rectified in this cycle. | NOT VERIFIED | 1 mm | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 204 | 37 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0063 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | General | INSTALLATION | (ii) After vacuum cycle Dry Nitrogen of dew point more than -60°C or of UHP grade (purity 99.9999%) to be pushed in Main Tank under vacuum till Min. pressure of 2.0 psi is achieved in Transformer Main tank. The Transformer Tank is to be kept pressurized for a duration of 24 hrs. | (ii) After vacuum cycle Dry Nitrogen of dew point more than -60°C or of UHP grade (purity 99.9999%) to be pushed in Main Tank under vacuum till Min. pressure of 2.0 psi is achieved in Transformer Main tank. The Transformer Tank is to be kept pressurized for a duration of 24 hrs. | NOT VERIFIED | 60°C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 204 | 37 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0064 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | General | INSTALLATION | (i) Again start vacuuming of Transformer Main Tank up to 1.00 torr (1 mm of Hg) and vacuum is to be maintained for 48 hrs in second dry out cycle. | (i) Again start vacuuming of Transformer Main Tank up to 1.00 torr (1 mm of Hg) and vacuum is to be maintained for 48 hrs in second dry out cycle. | NOT VERIFIED | 1 mm | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 204 | 37 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0065 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | General | INSTALLATION | (ii) Dry Nitrogen of dew point more than -60°C dew point or nitrogen of UHP grade (purity 99.9999%) is again pushed inside Main Tank under vacuum till pressure of Min. 2.0 psi is achieved in Transformer Main Tank. The Transformer Tank is to be kept pressurized for a duration of 24 hrs. | (ii) Dry Nitrogen of dew point more than -60°C dew point or nitrogen of UHP grade (purity 99.9999%) is again pushed inside Main Tank under vacuum till pressure of Min. 2.0 psi is achieved in Transformer Main Tank. The Transformer Tank is to be kept pressurized for a duration of 24 hrs. | NOT VERIFIED | 60°C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 204 | 37 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0066 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (iv) If the dew point values of second cycle is in line with the BHEL Standard norms, Transformer is cleared for further vacuuming followed by filling of filtered oil under vacuum and carrying out Hot Oil Circulation process. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0067 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | General | INSTALLATION | (v) In case desired value of dew point is not achieved than Transformer tank is to be again subjected for vacuum pulling for 24 hrs, followed by N2 filling for duration of 24 hrs. After each dry out cycle measure the Dew point values and compare with BHEL standard norms. | (v) In case desired value of dew point is not achieved than Transformer tank is to be again subjected for vacuum pulling for 24 hrs, followed by N2 filling for duration of 24 hrs. After each dry out cycle measure the Dew point values and compare with BHEL standard norms. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0068 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | carried out before filling of filtered oil under vacuum in Transformer Main Tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0069 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, AIS | NOT VERIFIED | Installation | AIS | INSTALLATION | Note: If the dew point values were not achieved as per BHEL standard norms in 2 dry out cycle and higher content of moisture was noticed as per Dry out process carried out in 2 cycle, than further Dry out process shall be carried out in consultation with BHEL Transformer Services Deptt. However for improving Dry out values it is suggested that Nitrogen Dry out cycle associated with heating cycle shall be carried out. In this process after vacuuming cycle pressurized Dry Nitrogen in Main Transformer Tank shall be heated externally to raise the temperature of Transformer upto 55-65°C during 24 hours duration followed by measurement of Dew point after completion of heated Nitrogen Dry out process. These Dew point values shall be compared with BHEL standard norms and the process of vacuum followed by insertion of Dry Nitrogen and heating is to be repeated till the dew point values were not achieved as per BHEL standards. | Note: If the dew point values were not achieved as per BHEL standard norms in 2 dry out cycle and higher content of moisture was noticed as per Dry out process carried out in 2 cycle, than further Dry out process shall be carried out in consultation with BHEL Transformer Services Deptt. However for improving Dry out values it is suggested that Nitrogen Dry out cycle associated with heating cycle shall be carried out. In this process after vacuuming cycle pressurized Dry Nitrogen in Main Transformer Tank shall be heated externally to raise the temperature of Transformer upto 55-65°C during 24 hours duration followed by measurement of Dew point after completion of heated Nitrogen Dry out process. These Dew point values shall be compared with BHEL standard norms and the process of vacuum followed by insertion of Dry Nitrogen and heating is to be repeated till the dew point values were not achieved as per BHEL standards. | NOT VERIFIED | 55-65°C; 24 hours | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0070 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY | The equipment required for vacuum treatment and oil-filling under vacuum should generally be as per Annexure 2.2. The transformer tank and electrical terminals shall be earthed for safety reasons. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The equipment required for vacuum treatment and oil-filling under vacuum should generally be as per Annexure 2.2. The transformer tank and electrical terminals shall be earthed for safety reasons. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0071 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The transformer/reactor shall be filled under vacuum with oil which has been purified and degassed according to Clause 2.4 | The transformer/reactor shall be filled under vacuum with oil which has been purified and degassed according to Clause 2.4 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0072 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | For main tank, the oil shall be heated to a temperature of 50°- 60°C measured at the filter outlet valve. The pressure during the filling shall be max. 1 torr. During the oil- filling, a transparent plastic tube (5) can be used as an oil-level gauge. The tube which | NOT COVERED | NOT VERIFIED | 60°C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 205 | 38 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0073 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Oil-filling of the tank is done through valve (12) at a low level on the transformer and at a maximum rate of 4-5 kL/hour. The pressure in the oil pipes shall be kept positive and shall be checked by a manometer 13 (if provided).Oil filling to be done as per cl. 2.6.9. | Oil-filling of the tank is done through valve (12) at a low level on the transformer and at a maximum rate of 4-5 kL/hour. The pressure in the oil pipes shall be kept positive and shall be checked by a manometer 13 (if provided).Oil filling to be done as per cl. 2.6.9. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 206 | 39 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0074 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Separate vacuum-proof cooler system/radiators can be evacuated for about 1-2 hours and filled separately with purified and degassed oil. The oil is then circulated through the vacuum filter at least twice via drain valves as near as possible to the transformer. Oil circulation is considered completed until the oil parameters as per table 2.3 is achieved. Care should be taken to keep all air release plugs and valves open to allow escape of trapped air during oil filling operation. These valves/plugs should be closed after completion of oil filling. | NOT COVERED | NOT VERIFIED | 1-2 hours | Separate vacuum-proof cooler system/radiators can be evacuated for about 1-2 hours and filled separately with purified and degassed oil. The oil is then circulated through the vacuum filter at least twice via drain valves as near as possible to the transformer. Oil circulation is considered completed until the oil parameters as per table 2.3 is achieved. Care should be taken to keep all air release plugs and valves open to allow escape of trapped air during oil filling operation. These valves/plugs should be closed after completion of oil filling. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 206 | 39 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0075 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 2.5.7 HOT OIL CIRCULATION/ DRYING OUT, OIL RINSING, PARTICLE REDUCTION AND PARTCLE COUNTING | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 206 | 39 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0076 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | To facilitate oil-penetration and absorption of possible gas bubbles, the temperature of transformer shall-after completed oil-filling-be increased by circulating the oil through the vacuum filter and with circulation direction according to Fig. 2.4. | To facilitate oil-penetration and absorption of possible gas bubbles, the temperature of transformer shall-after completed oil-filling-be increased by circulating the oil through the vacuum filter and with circulation direction according to Fig. 2.4. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 206 | 39 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0077 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The oil will be circulated through a high vacuum filter machine at 57 °C to 60 °C of transformer oil temperature for minimum 3 days. The start time for hot oil circulation is considered after achieving the stabilized temperature of oil i.e. Inlet and out let oil temp difference should not be more than 3 degree and the Oil temperature to be achieved in the process is between 57- 60 degree centigrade and record the IR value at an interval of 4 hrs after achieving the stabilized oil temperature values. Also record the IR value along with temperature, vacuum of M/c & IR value till oil parameter achieved as per table 2.3. Polarisation Index should be preferably more than 1.75. Other than this limit please refer the case to BHEL Bhopal. | The oil will be circulated through a high vacuum filter machine at 57 °C to 60 °C of transformer oil temperature for minimum 3 days. The start time for hot oil circulation is considered after achieving the stabilized temperature of oil i.e. Inlet and out let oil temp difference should not be more than 3 degree and the Oil temperature to be achieved in the process is between 57- 60 degree centigrade and record the IR value at an interval of 4 hrs after achieving the stabilized oil temperature values. Also record the IR value along with temperature, vacuum of M/c & IR value till oil parameter achieved as per table 2.3. Polarisation Index should be preferably more than 1.75. Other than this limit please refer the case to BHEL Bhopal. | NOT VERIFIED | 57 °C; 60 °C; 3 days | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 206 | 39 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0078 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Method of test for Electric Strength and moisture content shall be as per IS: 335. / IEC-60296 | Method of test for Electric Strength and moisture content shall be as per IS: 335. / IEC-60296 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 206 | 39 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0079 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The temperature during oil circulation should not increase beyond 70°C otherwise this may cause oxidation of oil. | NOT COVERED | NOT VERIFIED | 70°C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 207 | 40 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0080 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Transformer Oil | SAFETY | For transformer & reactor of 400 kV class or above, after completion of the hot oil circulation in main tank and cooler/radiator system separately, the valves between main tank and cooler/radiator system to be opened to allow the mixing of oil. The oil rinsing shall be carried out by connecting transformer/reactor to the oil rinsing plant connected with particle counter. Initially the oil inlet is connected to the lower portion of the tank and the outlet to the upper portion and start rinsing plant for circulation and creating turbulence of oil for approx. 1 hour. Thereafter the connection to be reversed (Oil inlet to the top of tank and oil outlet to the bottom of tank) and start rinsing plant. This process to be continued till the 3 consecutive readings at the interval of 1 hour of particle content of the insulation oil is achieved as per below: | NOT COVERED | NOT VERIFIED | 400 kV; 1 hour | For transformer & reactor of 400 kV class or above, after completion of the hot oil circulation in main tank and cooler/radiator system separately, the valves between main tank and cooler/radiator system to be opened to allow the mixing of oil. The oil rinsing shall be carried out by connecting transformer/reactor to the oil rinsing plant connected with particle counter. Initially the oil inlet is connected to the lower portion of the tank and the outlet to the upper portion and start rinsing plant for circulation and creating turbulence of oil for approx. 1 hour. Thereafter the connection to be reversed (Oil inlet to the top of tank and oil outlet to the bottom of tank) and start rinsing plant. This process to be continued till the 3 consecutive readings at the interval of 1 hour of particle content of the insulation oil is achieved as per below: | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 207 | 40 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0081 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Commissioning | DGA | COMMISSIONING | Oil sampling at various stages shall be done in accordance with IS: 6855 / IEC-60475. When samples are taken from transformer tank, oil will be drawn from Top & bottom of the tank. When it is desired to know gas content and composition of dissolved gases in transformer oil before commissioning for reference purposes (required for interpretation of Dissolved Gas Analysis results during service), sampling shall be done as per IS 9434 / IEC: 60567. | Oil sampling at various stages shall be done in accordance with IS: 6855 / IEC-60475. When samples are taken from transformer tank, oil will be drawn from Top & bottom of the tank. When it is desired to know gas content and composition of dissolved gases in transformer oil before commissioning for reference purposes (required for interpretation of Dissolved Gas Analysis results during service), sampling shall be done as per IS 9434 / IEC: 60567. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 207 | 40 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0082 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Standing time is the time between 'finished oil circulation' and 'energization'. The time appears from table 2.2. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Standing time is the time between 'finished oil circulation' and 'energization'. The time appears from table 2.2. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 207 | 40 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0083 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Smaller transformers/reactors are often factory-filled with degassed oil up to about 10% below the cover and transported in this condition. The final filling up to the correct level in the conservator is made at site. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 207 | 40 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0084 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Previously degassed oil (e.g., at the factory) stored in tight drums may be used for the filling. Check the dielectric strength of the oil which should be as per Clause 2.4.4. If accepted, the oil is pumped into the conservator and in this way fed into the transformer / reactor. To prevent any free water in the drums from entering the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 207 | 40 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0085 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Safety | Transformer Oil | SAFETY | transformer / reactor the opening of the suction tube must lie 0.1 m above the lowest point in the drum. A suitable valve on the cover and/or valves or upper tightening nuts at the bushings have to be opened for complete removal of air below the cover and in the bushings. When the oil is seeping out at these points, shut the valves and tighten the nuts at the bushings. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | transformer / reactor the opening of the suction tube must lie 0.1 m above the lowest point in the drum. A suitable valve on the cover and/or valves or upper tightening nuts at the bushings have to be opened for complete removal of air below the cover and in the bushings. When the oil is seeping out at these points, shut the valves and tighten the nuts at the bushings. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0086 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The filling is performed as described above, but at least a paper filter must be used for drying the oil. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0087 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | In all transformers specially in high voltage class, maintenance of insulating oil notably its dielectric property forms one of the determining factors of reliability of equipment in service. Oxidation and contamination of transformers/reactor oil can be avoided in a simple and effective way by use of above oil preservation system. The complete system is known as "Conservator with Air Cell". In this oil preservation system a flexible air cell made of oil resistant | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0088 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Nitrile rubber is placed inside the conservator and floats on the oil surface. The air cell inflates or deflates as the oil level in the conservator falls or rises depending on the ambient temperature and load on the reactor. The inside of the rubber bag (Air Cell) is put into communication with atmosphere by means of a silica gel breather which ensures dry atmosphere inside the air cell. In addition to the above this system provides following advantages. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0089 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | ii. As no gas is used in this system, which operates at constant pressure, this formation of gas bubbles at low ambient temperature and load is eliminated. The system thus preserves the oil quality particularly its dielectric properties. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0090 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The conservator with air cell is provided with a magnetic oil gauge having one electrical contact. The indication shown on the dial physically corresponds to the oil level in the conservator which is due to balance of static pressure between the oil of the conservator and the atmospheric air inside the air cell. This system is also provided sometimes with a set of pressure and vacuum valves. These valves operate to pass either oil or air in the event of over filling or under filling the conservator during installation. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0091 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | When oil is to be filled by taking vacuum through conservator refer section 2.6.9 whereas when conservator is to be isolated during oil filling in transformer refers section 2.6.2. For deciding the applicability of either process consult OGA drawing / BHEL representative | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0092 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Figure 2.5 indicates the general arrangement of oil preservation system. The oil connection between conservator and transformer tank is made through Buchholz relay and valves are provided in between. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 208 | 41 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0093 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The flexible air cell is connected to the top of the conservator through gasket joint. Under normal condition air cell is completely surrounded by oil and floats in the conservator. The air cell inflates/deflates as the oil volume changes. The float of the MOG which is always in contact with under side of the air cell moves up and down and indicates the oil level. The cell will sink in the remote event if it is damaged and MOG alarm will operate. The conservator then functions as a conventional conservator without affecting the performance of the transformers/reactor. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0094 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Transformer Oil | SAFETY | This system is shipped separately from main tank. The air cell is shipped fitted in the conservator. A low positive pressure of less than.07 kg/sq.cm (1 psi) is maintained to avoid excessive movement of air cell in the conservator during transit. MOG is also shipped fitted on the conservator. Install the conservator and associate parts except breather as per transformers/reactor outline drawings and assemble oil pipe work. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | This system is shipped separately from main tank. The air cell is shipped fitted in the conservator. A low positive pressure of less than.07 kg/sq.cm (1 psi) is maintained to avoid excessive movement of air cell in the conservator during transit. MOG is also shipped fitted on the conservator. Install the conservator and associate parts except breather as per transformers/reactor outline drawings and assemble oil pipe work. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0095 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | i. Close and blank the valve (14) to isolate the conservator from main tank. Fill the oil in transformer under vacuum upto Buchholz level as per instructions given elsewhere. ' | i. Close and blank the valve (14) to isolate the conservator from main tank. Fill the oil in transformer under vacuum upto Buchholz level as per instructions given elsewhere. ' | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0096 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | ii. After filling the oil in transformer and breaking the vacuum, oil can be filled in the conservator either through reactor or by drain valve (4). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0097 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | iii. Remove the inspection cover (11) provided on the side of the conservator and check the air cell assuring that it is inflated. The air cell must remain in fully inflated condition during oil filling operation. If the air cell is found deflated fit the inspection cover and inflate the air cell with dry air/nitrogen gas to 0.035 kg/sq.cm max. through connection (8). A gauge may be put by removing plug (10). After filling close these connections. | iii. Remove the inspection cover (11) provided on the side of the conservator and check the air cell assuring that it is inflated. The air cell must remain in fully inflated condition during oil filling operation. If the air cell is found deflated fit the inspection cover and inflate the air cell with dry air/nitrogen gas to 0.035 kg/sq.cm max. through connection (8). A gauge may be put by removing plug (10). After filling close these connections. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0098 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | v. Slowly pump the oil through the main reactor/drain valve (4). Temporarily stop filling operation when oil starts coming from opening (5) and (6) after ensuring that no air bubbles come out through these air release holes. Fit the two air release plugs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0099 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | vi. Continue oil filling till oil start coming from air release plug (7) stop oil after ensuring that no air bubbles come out. Fit the plug (7). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0100 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | vii. Now release the air pressure held inside the air cell from point (8) and continue oil filling until magnetic oil gauge (3) indicates 35°C level. | NOT COVERED | NOT VERIFIED | 35°C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0101 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | viii. Remove oil pump and connect air cell to breather (9) from point (8). Also remove pressure gauge and put plug (10). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 209 | 42 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0102 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | i. Oil filling in the conservator and also draining whenever required must be done very slowly. During oil filling, pressure in the air cell should not exceed 0.1kg/sq.cm (1.5 psi). | i. Oil filling in the conservator and also draining whenever required must be done very slowly. During oil filling, pressure in the air cell should not exceed 0.1kg/sq.cm (1.5 psi). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0103 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Reactor | NOT VERIFIED | Installation | General | INSTALLATION | ii. If a pressure or vacuum is ever applied to the main reactor tank the conservator must be disconnected and a blanking plate fitted on shut off valve. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0104 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | iv. Once all the air has been driven out during oil filling in the conservator do not remove air release plugs (5), (6) and (7). Otherwise air will be sucked inside the conservator. | iv. Once all the air has been driven out during oil filling in the conservator do not remove air release plugs (5), (6) and (7). Otherwise air will be sucked inside the conservator. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0105 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | Little maintenance work will normally be required except routine visual inspection. However, it is desirable to check the breather opening to ensure it is not blocked. Further silica gel should be regenerated/replaced when its colour changes from blue to pink. | Little maintenance work will normally be required except routine visual inspection. However, it is desirable to check the breather opening to ensure it is not blocked. Further silica gel should be regenerated/replaced when its colour changes from blue to pink. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0106 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Air cell is made from Nylon fabric coated with Nitrile rubber, In the event it becomes necessary to replace or test the air cell for leaks the following method is recommended. | Air cell is made from Nylon fabric coated with Nitrile rubber, In the event it becomes necessary to replace or test the air cell for leaks the following method is recommended. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0107 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | iii. Drain the oil from the conservator through the valve (4) by removing air release plugs (5) and (6). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0108 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | iv. Remove inspection cover (11) if necessary, Install the pressure gauge on point (10). | iv. Remove inspection cover (11) if necessary, Install the pressure gauge on point (10). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0109 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | Transformer Oil | TESTING | Oil pressure test on fully erected Transformer / Reactor to be conducted as per annexure 2.3 before hot oil circulation. | Oil pressure test on fully erected Transformer / Reactor to be conducted as per annexure 2.3 before hot oil circulation. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 210 | 43 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0110 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 2.6.9 INSTRUCTION FOR EVACUATING OF THE TRANSFORMER / REACTOR VIA THE CONSERVATOR FOR FILLING OIL. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 211 | 44 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0111 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Installation | General | INSTALLATION | 3. Open the shut off valve (14) and (16) between conservator and transformer. Open the bypass pipe valve (20) between conservator and Air cell and valve (21). Connect the Vacuum pump to pipe flange (11) hanging down from conservator. | 3. Open the shut off valve (14) and (16) between conservator and transformer. Open the bypass pipe valve (20) between conservator and Air cell and valve (21). Connect the Vacuum pump to pipe flange (11) hanging down from conservator. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 211 | 44 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0112 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 4. Filling of the oil through the tank can start when vacuum has reached below 1 torr. When the oil level reaches the Buchholz relay in the pipe between tank and conservator, the Shut off valve (14) located in same pipe to be closed. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 211 | 44 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0113 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | 5. End the vacuum and close the bypass pipe valve (20) between conservator and Air cell and open the plug 5 and 6 on top of conservator. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 211 | 44 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0114 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 9. Open the Shut off valve (14) between conservator and transformer and press up oil slowly. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 212 | 45 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0115 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 12. When the pressure in the Air cell has decreased to atmospheric pressure, the pressure gauges (16) shows no detection open the Shut off valve (14) again and continue oil filling until the oil level specified has been reached and MOG shows 35 °C reading. | NOT COVERED | NOT VERIFIED | 35 °C | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 212 | 45 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0116 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Note: The above Oil Filling under Vacuum to be followed for 765 kV & above transformers /reactors in case of specific requirement. | NOT COVERED | NOT VERIFIED | 765 kV | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 212 | 45 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0117 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The un tanking must be done indoors. If there is no suitable hall available, lifting can be done in the temporarily arranged room. e.g. a tent. The oil & the internal parts of the transformer must not in any case be exposed to rain or humidity. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 212 | 45 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0118 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, CT, Bushing | Current Transformer | Inspection | Transformer Oil | INSPECTION | Open all inspection covers for observation. Disconnect leads to bushings, current transformers, winding temperature devices, Oil temperature devices and earthing leads (common CC-CL-G) between active part and cover or tank side from earthing terminal board and any other connections like fiber optic probes from feed through plate welded on tank wall. Disconnections mentioned above can usually be made through hand holes in cover or tank side. | Open all inspection covers for observation. Disconnect leads to bushings, current transformers, winding temperature devices, Oil temperature devices and earthing leads (common CC-CL-G) between active part and cover or tank side from earthing terminal board and any other connections like fiber optic probes from feed through plate welded on tank wall. Disconnections mentioned above can usually be made through hand holes in cover or tank side. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 212 | 45 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0119 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Remove all large bushings, tank cover or top tank mounted conservator, lightning arrestors (if provided), thermo siphon (if provided), PRV pipe work, heavy gate valves (150 NB, 200 NB, 250 NB), neutral grounding arrangement: post insulator, copper strips & connectors (if provided). Break all connections between tank cover or top tank and tank-piping to oil conservator and cooler thermometers etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Remove all large bushings, tank cover or top tank mounted conservator, lightning arrestors (if provided), thermo siphon (if provided), PRV pipe work, heavy gate valves (150 NB, 200 NB, 250 NB), neutral grounding arrangement: post insulator, copper strips & connectors (if provided). Break all connections between tank cover or top tank and tank-piping to oil conservator and cooler thermometers etc. | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 213 | 46 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0120 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Place the cover on suitable wooden supports and in such a way that thermometer pockets, small bushing etc. underneath the cover are not damaged. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 213 | 46 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0121 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer, CT, Bushing | Current Transformer | Inspection | Bushing | INSPECTION | Reassemble bolts nuts of supporting devices. Weld the cover when the welded construction is used. Reassemble Bushings, conservator etc., and reconnect pipings, leads to bushings, current transformers, etc. Reassemble inspection covers. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 214 | 47 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0122 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | After the transformer is completely assembled, it may be necessary to dry it before oil fining- see clause 2.5. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 214 | 47 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0123 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The gaskets have a circular/flat cross-section and are made of oil and heat- resistant synthetic nitrile rubber/nitrile rubber bonded cork. For small gaskets, O-rings are used with diameter 3,5.0 or 8.0 mm, while round rubber cords with diameters 8,12 or 19 mm are used for large gaskets. | NOT COVERED | NOT VERIFIED | 8.0 mm; 19 mm | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 214 | 47 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0124 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Transformer | NOT VERIFIED | Inspection | Inspection | INSPECTION | Above description is followed generally for turrets, inspection cover etc. For main tank rim joint, LV turrets of Generator Transformers where metallic stops are provided, nitrile rubber bonded cork is used, for which following instructions shall apply. | Above description is followed generally for turrets, inspection cover etc. For main tank rim joint, LV turrets of Generator Transformers where metallic stops are provided, nitrile rubber bonded cork is used, for which following instructions shall apply. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 214 | 47 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0125 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | iii. Gaskets are best stored in hermetically sealed containers in a cool place. They must be protected from damp, oil and grease- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 215 | 48 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0126 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | iv. To make a gasket joint, first clean the metal surfaces by thinner to ensure that they are free from oil, rust, scale etc. Using one of the flanges as a template, punch the necessary bolt holes. Insert the bolts and tighten the bolts sequentially, a little every time so that uniform pressure is exerted on the gasket until the gasket is compressed to about 2/3 of its original thickness. Joints should not be subjected to pressure until tightening is complete. If care is taken in making joints, and in handling the gasket, it is possible to break and remake a joint several times, using the same gasket. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 215 | 48 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0127 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | When welding, a fire-extinguishing equipment should be available, and the work supervised by fire-protection personnel. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 216 | 49 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0128 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The terminals are protected by a cover. The cover can be removed with the tank oil- filled. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 216 | 49 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0129 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | For the core-insulation test, remove the cover. Disconnect the closing link that connects the two terminals CL-G. Use preferably 1000V mega direct voltage between CL and CC + G. The tank shall be grounded during the test. The insulation value after | For the core-insulation test, remove the cover. Disconnect the closing link that connects the two terminals CL-G. Use preferably 1000V mega direct voltage between CL and CC + G. The tank shall be grounded during the test. The insulation value after | NOT VERIFIED | 1000V | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 216 | 49 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0130 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 1 min. test- time shall be minimum 1000 k-ohms. There is no general requirement on the insulation level CC-G. | 1 min. test- time shall be minimum 1000 k-ohms. There is no general requirement on the insulation level CC-G. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 217 | 50 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0131 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | ii. oil heaters and vacuum-proof hoses with independent vacuum pumping system for tank evacuation. Capacity: 6000 LPH | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 219 | 52 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0132 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Corrective Action | Transformer Oil | CORRECTIVE_ACTION | iii. Oil-storage tanks provided with silica-gel breathers and inlet/outlet valves for oil circulation. Recommended capacity 20 kL -30 kL (Clause2.4) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | iii. Oil-storage tanks provided with silica-gel breathers and inlet/outlet valves for oil circulation. Recommended capacity 20 kL -30 kL (Clause2.4) | BHEL-specific transformer/reactor procedure | PDF p. 219 | 52 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D07-C0133 | D07 | Tender_Part-1-2025-03-25-05_57_06.pdf | Procedure for Transformer / Reactor Installation, Testing and Commissioning | Bharat Heavy Electricals Limited (BHEL) | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | ix. Transparent vacuum-proof tubes for checking of oil-level during oil filling. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | BHEL-specific transformer/reactor procedure | PDF p. 219 | 52 ¦ P a g e | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0001 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Annexure–B: Technical Parameters of Bushing Current Transformers & Neutral Current Transformers | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 10 | VI-46 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0002 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure–J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test | Annexure–J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 10 | VI-46 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0003 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | Standard GA Drawings and Limits of Supply Between Suppliers of Transformer and Dry-Type Cable/GIS Termination for Hydro Plants Annexure–R: 1100 V Grade Power and Control Cable | NOT COVERED | NOT VERIFIED | 1100 V | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 11 | 1100 V Grade Power and Control Cable | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0004 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Annexure–U: Specification for On-line Insulating Oil Drying System (Cartridge type) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 11 | 1100 V Grade Power and Control Cable | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0005 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | General | SAFETY | The transformer and reactor are vital and expensive assets in a power system. The increase in demand for energy will require enhancement in transformation capacity as well as reactive compensation requirement. Reliability and availability of such important assets plays an important role in the smooth operation of a power system. Emphasis needs to be laid on improved design, quality control during manufacturing, use of right components/accessories, maintenance and safety during operation of such vital assets. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The transformer and reactor are vital and expensive assets in a power system. The increase in demand for energy will require enhancement in transformation capacity as well as reactive compensation requirement. Reliability and availability of such important assets plays an important role in the smooth operation of a power system. Emphasis needs to be laid on improved design, quality control during manufacturing, use of right components/accessories, maintenance and safety during operation of such vital assets. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 13 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0006 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Generally, due to poor quality of raw material, workmanship, and manufacturing techniques or due to normal and abnormal stresses of the system during the operation (like frequent system faults, over loading, environmental effect, unexpected continuous operating voltage and over voltage stresses), and poor maintenance practice, transformers/reactors fail much before their expected life span (expected life span of about 35 years). The failure of such vital equipment can have significant economic impact due to high cost, long lead time in procurement, manufacturing and installation. Long repair time is a matter of concern in many cases of failure of transformer/reactor. Restoration of transformer/reactor takes about 3 to 6 months after major repair at manufacturer’s works depending on the type of repair and procurement of | NOT COVERED | NOT VERIFIED | 35 years; 6 months | NOT COVERED | Generally, due to poor quality of raw material, workmanship, and manufacturing techniques or due to normal and abnormal stresses of the system during the operation (like frequent system faults, over loading, environmental effect, unexpected continuous operating voltage and over voltage stresses), and poor maintenance practice, transformers/reactors fail much before their expected life span (expected life span of about 35 years). The failure of such vital equipment can have significant economic impact due to high cost, long lead time in procurement, manufacturing and installation. Long repair time is a matter of concern in many cases of failure of transformer/reactor. Restoration of transformer/reactor takes about 3 to 6 months after major repair at manufacturer’s works depending on the type of repair and procurement of | Transformers and reactors, 66 kV and above voltage class | PDF p. 13 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0007 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | Power Transformer | Testing | OLTC | TESTING | a) To adopt country wide standard designs of Power transformers for each class ratings and performance parameter wise (including losses); b) To reduce lead time, human efforts & errors during the transformer procurement process by adopting standard losses and detailed guaranteed technical particular (GTP) format; c) To adopt specifications and application guides for various fittings and accessories for the selection and maintenance of transformer components; d) To follow the Guidelines for preparation and checking of standard contract drawings preferred cooler and OLTC control schemes; e) To adopt standard Manufacturing Quality Plan (MQP) for manufacturing, testing and packing of transformers to define and ensure quality for reliability; f) To enhance the overall efficiency, quality and productivity in the entire value chain of transformer procurement and operation; g) To achieve interchangeability of transformers of different make, procured by different utilities – by standardizing the losses, lay out and foundation plan of transformers; and h) To achieve shorter deliveries of power transformers for timely and speedier completion of projects. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 15 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0008 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | This document/guidelines shall be applicable to new transformers/reactors of 66 kV and above voltage class. The document does not cover transformers suitable for Static Var Compensator (SVC), Static Compensator (STATCOM), traction transformers, welding transformers, testing transformers, mining transformers, furnace transformers and inverter transformer for Renewable generators. | This document/guidelines shall be applicable to new transformers/reactors of 66 kV and above voltage class. The document does not cover transformers suitable for Static Var Compensator (SVC), Static Compensator (STATCOM), traction transformers, welding transformers, testing transformers, mining transformers, furnace transformers and inverter transformer for Renewable generators. | NOT VERIFIED | 66 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 15 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0009 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | This document covers only technical aspects pertaining to manufacturing, transportation, erection, testing, commissioning and condition monitoring of transformer/reactor. The commercial aspects, contractual terms, scope of works for OEM/contractor etc. may be defined by the utility as per its requirement and practice. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 15 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0010 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance | General | MAINTENANCE | 1. The purpose of this document is: (a) to standardize the ratings; (b) bring uniformity in the design by fixing major technical parameters including maximum permissible losses, eliminating the need for capitalisation of losses; (c) facilitate physical inter-changeability of different makes by standardizing the common mounting arrangement/foundation plan; (d) improve manufacturing facility, reliability & quality of supply of Transformer/Reactor from all manufacturers; (e) achieve cost effective production & faster delivery; and (f) adoption of Condition Based Maintenance (CBM) practices across the utilities in the country to assess the health of assets. 2. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 16 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0011 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | Auto Transformer | Design / Technical Reference | General | DESIGN_REFERENCE | Attempt has been made to standardize and restrict the number of ratings of Power Transformers and Reactors at different voltage levels so that the manufacturers shall have to design and manufacturer fewer ratings resulting in requirement of less inventory of components and faster delivery. In the process the focus will be on quality of production which will be in overall interest of utilities, manufacturers and the system. 3. Following ratings of power/auto transformers, Generator Transformers and reactors have been standardized based on general practice and most commonly used ratings in India. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 16 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0012 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | 4. The fixation of maximum permissible loss values for transformers (No-load loss, Load loss, I2R loss and auxiliary loss) and reactors (I2R loss and total loss) has been done in consultation with utilities and manufacturers. The method of calculation of losses has been given along with a typical example for verifying the guaranteed values and for measurement at manufacturer works so that all utilities across the country get transformer and reactor of similar quality and efficiency. Manufacturer shall be penalized if losses measured during Factory Acceptance Test (FAT)/Routine tests are within +2% tolerance on maximum specified values, beyond which transformer/reactor would be liable for rejection. However, no incentive would be given to manufacturer for maintaining the losses less than the specified values. | 4. The fixation of maximum permissible loss values for transformers (No-load loss, Load loss, I2R loss and auxiliary loss) and reactors (I2R loss and total loss) has been done in consultation with utilities and manufacturers. The method of calculation of losses has been given along with a typical example for verifying the guaranteed values and for measurement at manufacturer works so that all utilities across the country get transformer and reactor of similar quality and efficiency. Manufacturer shall be penalized if losses measured during Factory Acceptance Test (FAT)/Routine tests are within +2% tolerance on maximum specified values, beyond which transformer/reactor would be liable for rejection. However, no incentive would be given to manufacturer for maintaining the losses less than the specified values. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 18 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0013 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | It is proposed to review the loss figures periodically based on the feedback from utilities and the manufacturers. 5. Tamil Nadu has 230 kV and 110 kV system and Karnataka has 110kV system which is different from the other States in the Country. Keeping in view the requirement of these two States, it was decided that loss figures for 400/230/33kV, 400/110/33kV, | NOT COVERED | NOT VERIFIED | 230 kV; 110 kV; 110kV; 33kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 18 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0014 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Failure / Failure Analysis | Bushing | FAILURE_ANALYSIS | 220(or 230)/110kV, 230/33kV & 110/33kV transformers shall be same as that of 400/220/33 kV, 400/132/33 kV, 220/132kV, 220/33kV & 132/33kV transformers of identical MVA ratings respectively. However, the parameters for Bushing Current Transformers (BCTs) for these ratings have not been specified, utility may select BCT parameters as per their requirement. 6. In general, the tertiary windings have been removed in case of 3 limbed transformers (i.e. up to 200 MVA, 220 kV class transformer) to eliminate the possible failure due to tertiary winding, improve reliability and reduce overall cost. Unless there is special requirement like loading the tertiary, utilities are advised to avoid tertiary winding in transformers up to above mentioned ratings. | NOT COVERED | NOT VERIFIED | 110kV; 33kV; 33 kV; 132kV; 200 MVA; 220 kV | NOT COVERED | 220(or 230)/110kV, 230/33kV & 110/33kV transformers shall be same as that of 400/220/33 kV, 400/132/33 kV, 220/132kV, 220/33kV & 132/33kV transformers of identical MVA ratings respectively. However, the parameters for Bushing Current Transformers (BCTs) for these ratings have not been specified, utility may select BCT parameters as per their requirement. 6. In general, the tertiary windings have been removed in case of 3 limbed transformers (i.e. up to 200 MVA, 220 kV class transformer) to eliminate the possible failure due to tertiary winding, improve reliability and reduce overall cost. Unless there is special requirement like loading the tertiary, utilities are advised to avoid tertiary winding in transformers up to above mentioned ratings. | Transformers and reactors, 66 kV and above voltage class | PDF p. 19 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0015 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | The tertiary winding shall be capable of withstanding mechanical & thermal stress due to short circuit on its terminals and suitable for continuous thermal rating of 5MVA. 7. Keeping in view the infrequent use of OLTC and no significant voltage control/variation is being achieved by such use at 400 kV and 765 kV levels, it has been decided to have tap less 765/400/33kV ICTs to start with in order to simplify the design, eliminate failure due to OLTC, reduce the overall cost of transformer and improve the reliability of transformers. Based on the experience & feedback of the manufacturers and utilities, further initiative can be taken to have tap less transformers for lower voltage class transformers depending on system operation requirement. | NOT COVERED | NOT VERIFIED | 5MVA; 400 kV; 765 kV; 33kV | NOT COVERED | The tertiary winding shall be capable of withstanding mechanical & thermal stress due to short circuit on its terminals and suitable for continuous thermal rating of 5MVA. 7. Keeping in view the infrequent use of OLTC and no significant voltage control/variation is being achieved by such use at 400 kV and 765 kV levels, it has been decided to have tap less 765/400/33kV ICTs to start with in order to simplify the design, eliminate failure due to OLTC, reduce the overall cost of transformer and improve the reliability of transformers. Based on the experience & feedback of the manufacturers and utilities, further initiative can be taken to have tap less transformers for lower voltage class transformers depending on system operation requirement. | Transformers and reactors, 66 kV and above voltage class | PDF p. 19 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0016 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC, Bushing, Fire Protection | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | Reduction in tap range in case of other voltage class transformer will definitely simplify the lead design & the tap changer as number of lead connections gets reduced. Since many utilities did not like to reduce the tap range considering the system operating condition, no action could be taken in that direction. However, utilities are advised to explore the possibility of reduction in the tap range in OLTC as indicated at Annexure-A depending on their requirement and system condition. 8. During discussion in Standing Committee meetings relating to failure of sub-station equipment, it has been observed that bushing is one of the major cause of failure of transformer and in many cases this has led to severe consequences like fire/burning of transformer/reactors and explosion. Hence RIP/RIS bushings have been specified at various voltage levels in place of conventional OIP bushings. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | Reduction in tap range in case of other voltage class transformer will definitely simplify the lead design & the tap changer as number of lead connections gets reduced. Since many utilities did not like to reduce the tap range considering the system operating condition, no action could be taken in that direction. However, utilities are advised to explore the possibility of reduction in the tap range in OLTC as indicated at Annexure-A depending on their requirement and system condition. 8. During discussion in Standing Committee meetings relating to failure of sub-station equipment, it has been observed that bushing is one of the major cause of failure of transformer and in many cases this has led to severe consequences like fire/burning of transformer/reactors and explosion. Hence RIP/RIS bushings have been specified at various voltage levels in place of conventional OIP bushings. | Transformers and reactors, 66 kV and above voltage class | PDF p. 19 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0017 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | RIS would have been a better/preferred alternative to OIP, but due to limited manufacturer in the world, both RIP & RIS options have been considered. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 19 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0018 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | 9. Emphasis has been given to Design Review, which is the most important task to be carried out before commencement of the manufacturing of transformer/reactor to ensure its quality. The design review may be carried out by the purchaser or a consultant appointed by the purchaser. Design Review carried out by one utility for a specific transformer of a particular make, can also be used by another utility for the same design with the consent of the manufacturer. The Guaranteed and other technical particulars submitted by the manufacturer to the purchaser/ utility, would be used for technical evaluation, design review and verification of similarity criteria with reference to the Short Circuit tested transformer. 10. The requirement of SC testing has been emphasized in line with the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 20 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0019 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | provision of CEA (Technical Standards for Construction of Electric Plants and Electric lines) Regulations and repetition of SC test within validity period is not required provided the similarity can be established with reference to the SC tested transformer. 11. Customer/Purchaser always wishes that transformer/reactor manufactured and delivered must perform trouble free service for its “Specified Design Life”. It is always a challenge for supplier/manufacturer to keep consistency in material used & manufacturing process, which are main cause for variation in quality of transformer/reactor. Customer practically cannot monitor them and is not expected to do so. The change in sub-vendors and skilled manpower (in the factory) from time to time also require due diligence to control and maintain the consistency of manufacturing process. | provision of CEA (Technical Standards for Construction of Electric Plants and Electric lines) Regulations and repetition of SC test within validity period is not required provided the similarity can be established with reference to the SC tested transformer. 11. Customer/Purchaser always wishes that transformer/reactor manufactured and delivered must perform trouble free service for its “Specified Design Life”. It is always a challenge for supplier/manufacturer to keep consistency in material used & manufacturing process, which are main cause for variation in quality of transformer/reactor. Customer practically cannot monitor them and is not expected to do so. The change in sub-vendors and skilled manpower (in the factory) from time to time also require due diligence to control and maintain the consistency of manufacturing process. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 20 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0020 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | It is also equally very important that transformer/reactor is manufactured in a clean dust free environment with humidity control. Any compromise on this aspect will have adverse effect on expected design life of transformer/reactor, no matter how good is the workmanship and quality of material used. The manufacturers are expected to develop their manufacturing facility at par with the global practices/standards to improve quality and manufacturing processes for transformer and reactor. This would enhance export potential & international acceptability of product. The broad list of facilities the manufacturers should have are provided in Annexure-G. In case the manufacturer(s) do not have such facilities, it is to be ensured that such facilities are in place/developed within a period of two (2) years of release of this document. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 20 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0021 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | inspection and testing has been introduced as an alternative to conventional practice of physical presence of representative of utility at manufacturer’s works during inspection & testing. 13. The manufacturers have different arrangement of jacking and | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 21 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0022 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | different spacing between jacking pads. Hence, it was difficult to standardize the civil foundation drawing based on jacking pad locations/arrangement. Design of block foundation based on maximum weight of transformer/reactor for a particular MVA/MVAR rating along with specified no. of rails with standard gauge (1676mm) and provision of suitable size of portable metal plate for jacking have been suggested to facilitate the physical interchangeability of transformers/reactors of different make on same foundation block. Thus, the outage time of replacement of spare/new transformer or reactor of different makes would be minimized as it can be accommodated in the same space with no or minor modification in foundation. The design requirement of soak pit and oil collecting pit for transformer/reactor has been clearly specified so that foundation design takes into account such provision. 14. It is a fact that during initial 5 years of operation many transformers/ | NOT COVERED | NOT VERIFIED | 1676mm; 5 years | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 21 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0023 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | reactors have failed. Therefore, during deliberation, utilities were insisting for inclusion of extended warranty/defect liability period for transformer/reactor up to 5 years to ensure supply of quality product by manufacturer. Manufacturers were of the opinion that utilities also have a major role to play in long and trouble free service of such assets. Good maintenance practice and regular monitoring of health of assets is equally important. Successful operation of transformer/reactor depends on operating conditions and O&M practices being followed by the utility. The extended warrantee period beyond normal period of warranty would have implication on overall cost of transformer/reactor. All utilities may not like to bear the extra burden on account of extended warranty, rather such utility may prefer to maintain the health of their assets properly for a long & trouble free service. | NOT COVERED | NOT VERIFIED | 5 years | NOT COVERED | reactors have failed. Therefore, during deliberation, utilities were insisting for inclusion of extended warranty/defect liability period for transformer/reactor up to 5 years to ensure supply of quality product by manufacturer. Manufacturers were of the opinion that utilities also have a major role to play in long and trouble free service of such assets. Good maintenance practice and regular monitoring of health of assets is equally important. Successful operation of transformer/reactor depends on operating conditions and O&M practices being followed by the utility. The extended warrantee period beyond normal period of warranty would have implication on overall cost of transformer/reactor. All utilities may not like to bear the extra burden on account of extended warranty, rather such utility may prefer to maintain the health of their assets properly for a long & trouble free service. | Transformers and reactors, 66 kV and above voltage class | PDF p. 21 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0024 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Being a commercial issue, utilities and manufacturer may mutually decide about extended warranty/defect liability period. Leakage of Oil from transformer / reactor is construed as a serious quality lapse on the part of the Original Equipment Manufacturer (OEM). No leakage of oil is expected during the operating life of the transformer / reactor and accordingly OEM should ensure design & construction of tank & other gasketted joints. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Being a commercial issue, utilities and manufacturer may mutually decide about extended warranty/defect liability period. Leakage of Oil from transformer / reactor is construed as a serious quality lapse on the part of the Original Equipment Manufacturer (OEM). No leakage of oil is expected during the operating life of the transformer / reactor and accordingly OEM should ensure design & construction of tank & other gasketted joints. | Transformers and reactors, 66 kV and above voltage class | PDF p. 21 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0025 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | However, the responsibilities of manufacturer and utility have been highlighted clearly & briefly in the document. In general, all necessary steps should be taken to ensure that proper condition assessment/monitoring and maintenance of transformer/reactor is carried out effectively for a long & trouble free service. The condition monitoring tests include measurement of Insulation Resistance (IR), capacitance & tan-delta for winding & bushing, magnetic balance, winding resistance, turns ratio, oil Break Down Voltage (BDV), Dissolved Gas Analysis (DGA), thermal scanning, and Sweep Frequency Response Analysis (SFRA) etc. The frequency of tests and threshold values of various diagnostic parameters has been given to assess the condition of transformer or reactor for reference and guidance of utility. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 22 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0026 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Substation | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | The frequency of tests may be increased depending on the condition assessment of transformer/reactor. The Pre-commissioning test results and the results of various tests carried out subsequently at sites shall be recorded religiously by the utilities. The trend analysis shall be carried out to take further course of action. The utility may procure and employ diagnostic equipment like DGA, winding resistance meter, SFRA, capacitance and tan delta measuring units etc. as per CEA (Grid Standards) Regulations either for each substation or cluster of substations depending on their assessment or requirement. 15. The management of such vital assets, when they are in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 22 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0027 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, AIS | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | For the oil-filled transformers, particularly which are in service for more than 15 years, it is advisable that the residual life should be estimated by assessing the extent of degradation of solid cellulosic paper insulation through Furan content analysis of oil and degree of polymerization of paper insulation. This would help utilities in making optimum use of transformers / reactors and also taking timely decision regarding Run-Refurbish-Replacement of transformers / reactors. Transformer Assessment Indices (TAIs) method may be used to identify the transformers which most urgently need attention or intervention. | NOT COVERED | NOT VERIFIED | 15 years | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 22 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0028 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | mineral insulating oil, utilities may use Ester (synthetic/natural) fluid for Transformer/Reactor as per their requirement. New generation insulating oils may also be considered provided any National or International standard is available for such oil. Accordingly, the temperature rise of oil over ambient temperature may be modified. 17. The specifications for firefighting system have not been included. But, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 23 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0029 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Transformer Oil | SAFETY | the utilities shall ensure that adequate fire protection system including soak pit/oil collecting pits, fire separation walls (wherever required) and water hydrant system etc. are provided in line with CEA (Measures Relating to Safety and Electric Supply) Regulations. 18. As per CEA (Technical Standard for construction of Electrical Plants | NOT COVERED | NOT VERIFIED | NOT VERIFIED | the utilities shall ensure that adequate fire protection system including soak pit/oil collecting pits, fire separation walls (wherever required) and water hydrant system etc. are provided in line with CEA (Measures Relating to Safety and Electric Supply) Regulations. 18. As per CEA (Technical Standard for construction of Electrical Plants | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 23 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0030 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Transformer Oil | TESTING | This Chapter broadly covers the technical specification including broad construction features for winding, core, tank, bushings, other fittings & accessories, performance parameters like hot spot temperature, suitability to withstand various over voltages (TOV, over voltage due to Lightning and switching operations), thermal & dynamic SC withstand capability, and requirement of SC testing, the maximum temperature rise of oil & winding, cooling & on load tap changing system and associated digital control integrated with BCU/ SCADA system and the information to be provided on rating & diagram plate etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 23 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0031 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | This Chapter covers typical Manufacturer’s Quality Program (MQP), Inspection and testing including Stage inspection, Factory Acceptance Tests, testing of fittings and accessories, Tank tests and pre-shipment checks at manufacturer’s works etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 24 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0032 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | The key issues relating to transportation, handling, loading-unloading, Erection, Testing and commissioning; checks after receipt at site; storage at site; precautions during erection including oil filling; pre-commissioning checks/tests; and final commissioning checks before energization are covered in this Chapter. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The key issues relating to transportation, handling, loading-unloading, Erection, Testing and commissioning; checks after receipt at site; storage at site; precautions during erection including oil filling; pre-commissioning checks/tests; and final commissioning checks before energization are covered in this Chapter. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 24 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0033 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, AIS | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | This Chapter briefly highlights about various maintenance practices, benefit of Condition Based Maintenance (CBM), on-line monitoring (measurement of Partial Discharge, On-line DGA, Hot spot monitoring, on- line dry out system, thermo-vision scanning etc.) and off-line monitoring (measurement of winding resistance, voltage ratio, magnetizing current, Polarization Index (PI), capacitance & Tan delta measurement, Short circuit impedance, oil parameters and Frequency Response Analysis etc.), Reliability Centered Maintenance (RCM) and Transformer Assessment Indices (TAIs) method as per CIGRE document (WG A2.49)..). The frequency of tests to be carried out using various diagnostic tools and acceptance norms/threshold values corresponding to various diagnostic parameters like capacitance & Tan delta values, contact resistance and PI etc. has been given to assess the condition of transformer or reactor for reference and guidance of utility to take further course of action. The frequency of tests may be increased depending on the condition assessment of transformer/reactor. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 24 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0034 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | The purpose of various diagnostic tests for condition monitoring & health assessment and acceptance norms for various diagnostic parameters for transformers/reactors has been explained briefly in this Chapter. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 24 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0035 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, CT, Bushing | Current Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | The major technical parameters like BILs of winding & bushings, temperature rise, losses etc. of single phase & three phase transformer & reactors and technical parameters of Bushing Current Transformers have been included as Annexure– A & B respectively. The insulation level of terminal bushings has been considered as one step higher than corresponding winding insulation level. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 25 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0036 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | A typical test plan and test procedures for Transformers/Reactors have been listed in Annexure-D. A typical Manufacturer’s Quality Plan (MQP) have been listed in Annexure- E. | A typical test plan and test procedures for Transformers/Reactors have been listed in Annexure-D. A typical Manufacturer’s Quality Plan (MQP) have been listed in Annexure- E. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 25 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0037 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The painting procedure, parameters of unused inhibited/uninhibited Insulating Oil are given in Annexure – K, Annexure - L respectively. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 25 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0038 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | A typical connection arrangement for bringing spare unit into the circuit in case of failure/outage of one of the other healthy units has been included in Annexure-N. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | A typical connection arrangement for bringing spare unit into the circuit in case of failure/outage of one of the other healthy units has been included in Annexure-N. | Transformers and reactors, 66 kV and above voltage class | PDF p. 25 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0039 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Annexure-P covers the aspects related to the physical interchangeability of transformers and reactors of different makes on same foundation block (designed based on maximum weight) using portable metal plate for jacking and the design requirement of soak pit and oil collecting pit for taking into account in foundation design for transformer/reactor. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 26 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0040 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | The details of 1100 V grade power and control cable, Specification for Oil Storage Tank, Breakdown Voltage (BDV) test set, portable DGA kit for transformer oil, online insulating oil drying system, Oil sampling bottles, Oil Syringe and has been included in Annexure-R, S, T & U & V for the reference of the utility. | NOT COVERED | NOT VERIFIED | 1100 V | NOT COVERED | The details of 1100 V grade power and control cable, Specification for Oil Storage Tank, Breakdown Voltage (BDV) test set, portable DGA kit for transformer oil, online insulating oil drying system, Oil sampling bottles, Oil Syringe and has been included in Annexure-R, S, T & U & V for the reference of the utility. | Transformers and reactors, 66 kV and above voltage class | PDF p. 26 | Chapter-1: Introduction | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0041 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Grounding | COMMISSIONING | 1.0 GENERAL 1.1 This chapter covers specification for design, engineering, manufacture, testing, delivery at site including all materials, accessories, unloading, handling, proper storage at site, erection, testing and commissioning of the Transformer, Shunt Reactor and Neutral Grounding Reactor (NGR) specified. 1.2 The design and workmanship shall be in accordance with the best engineering practices to ensure satisfactory performance throughout the service life. 1.3 Any material and equipment not specifically stated in this specification but which are necessary for satisfactory operation of the equipment shall be deemed to be included unless specifically excluded and shall be supplied without any extra cost. 1.4 Components having identical rating shall be interchangeable. 2.0 SPECIFIC TECHNICAL REQUIREMENTS | 1.0 GENERAL 1.1 This chapter covers specification for design, engineering, manufacture, testing, delivery at site including all materials, accessories, unloading, handling, proper storage at site, erection, testing and commissioning of the Transformer, Shunt Reactor and Neutral Grounding Reactor (NGR) specified. 1.2 The design and workmanship shall be in accordance with the best engineering practices to ensure satisfactory performance throughout the service life. 1.3 Any material and equipment not specifically stated in this specification but which are necessary for satisfactory operation of the equipment shall be deemed to be included unless specifically excluded and shall be supplied without any extra cost. 1.4 Components having identical rating shall be interchangeable. 2.0 SPECIFIC TECHNICAL REQUIREMENTS | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 28 | Chapter-2: Technical Specification for Transformer and Reactor Page II-1 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0042 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | 5.1.2 Transformers shall be capable of operating under natural cooled condition up to the specified load. The forced cooling equipment, wherever specified, shall come into operation by pre-set contacts of winding temperature indicator and the transformer shall operate in forced cooling mode initially as ONAF (or ONAF1, as specified) up to specified load and then as OFAF (ONAF2 or ODAF or ODWF, as specified). Generator transformer with unit coolers shall operate at OFAF/ODAF cooling. The Cooling system shall be so designed that the transformer shall be able to operate at full load for at least ten (10) minutes in the event of total failure of power supply to cooling fans and oil pumps without the calculated winding hot spot temperature exceeding 140 deg C. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 5.1.2 Transformers shall be capable of operating under natural cooled condition up to the specified load. The forced cooling equipment, wherever specified, shall come into operation by pre-set contacts of winding temperature indicator and the transformer shall operate in forced cooling mode initially as ONAF (or ONAF1, as specified) up to specified load and then as OFAF (ONAF2 or ODAF or ODWF, as specified). Generator transformer with unit coolers shall operate at OFAF/ODAF cooling. The Cooling system shall be so designed that the transformer shall be able to operate at full load for at least ten (10) minutes in the event of total failure of power supply to cooling fans and oil pumps without the calculated winding hot spot temperature exceeding 140 deg C. | Transformers and reactors, 66 kV and above voltage class | PDF p. 29 | Chapter-2: Technical Specification for Transformer and Reactor Page II-2 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0043 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | If the Transformer is fitted with two cooler banks, each capable of dissipating 50 per cent of the loss at continuous maximum rating, it shall be capable of operating for 20 minutes at full load /continuous maximum rating in the event of failure of the oil circulating pump or fans/blowers associated with one cooler bank without the calculated winding hot spot temperature exceeding 140 deg C. The contractor shall submit supporting calculations for the above and the same shall be reviewed during design review. | NOT COVERED | NOT VERIFIED | 20 minutes | NOT COVERED | If the Transformer is fitted with two cooler banks, each capable of dissipating 50 per cent of the loss at continuous maximum rating, it shall be capable of operating for 20 minutes at full load /continuous maximum rating in the event of failure of the oil circulating pump or fans/blowers associated with one cooler bank without the calculated winding hot spot temperature exceeding 140 deg C. The contractor shall submit supporting calculations for the above and the same shall be reviewed during design review. | Transformers and reactors, 66 kV and above voltage class | PDF p. 29 | Chapter-2: Technical Specification for Transformer and Reactor Page II-2 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0044 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 5.1.3 The transformer shall be free from any Electrostatic Charging Tendency (ECT) under all operating conditions and maximum oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 29 | Chapter-2: Technical Specification for Transformer and Reactor Page II-2 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0045 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | 5.1.4 The transformers shall be capable of operating continuously at the rated MVA without danger, at any tapping with voltage variation of 10% corresponding to the voltage of that tapping. 5.1.5 The transformers shall be capable of being over loaded in accordance with IEC 60076-7. There shall be no limitation imposed by bushings, tap changers etc. or any other associated equipment. 5.1.6 The hotspot temperature in any location of the tank shall not exceed 110 degree Celsius at rated MVA. This shall be measured during temperature rise test at manufacturer’s works. 5.1.7 The maximum flux density in any part of the core and yoke at the rated MVA, voltage and frequency shall be such that under 10 % continuous over-voltage condition it does not exceed 1.9 Tesla at all tap positions. 5.1.8 The transformer and all its accessories including bushing/built in CTs etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 5.1.4 The transformers shall be capable of operating continuously at the rated MVA without danger, at any tapping with voltage variation of 10% corresponding to the voltage of that tapping. 5.1.5 The transformers shall be capable of being over loaded in accordance with IEC 60076-7. There shall be no limitation imposed by bushings, tap changers etc. or any other associated equipment. 5.1.6 The hotspot temperature in any location of the tank shall not exceed 110 degree Celsius at rated MVA. This shall be measured during temperature rise test at manufacturer’s works. 5.1.7 The maximum flux density in any part of the core and yoke at the rated MVA, voltage and frequency shall be such that under 10 % continuous over-voltage condition it does not exceed 1.9 Tesla at all tap positions. 5.1.8 The transformer and all its accessories including bushing/built in CTs etc. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 30 | Chapter-2: Technical Specification for Transformer and Reactor Page II-3 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0046 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | shall be designed to withstand the thermal and mechanical effects of any external short circuit to earth and of short circuits at the terminals of any winding without damage. The transformer shall be designed to withstand the thermal stress due to short circuit for a duration of 2 seconds and the same shall be verified during design review. However, generator transformer and associated auxiliary transformer shall be designed to withstand the thermal stress due to short circuit for a duration of 3 seconds. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 30 | Chapter-2: Technical Specification for Transformer and Reactor Page II-3 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0047 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 5.1.9 The following short circuit level shall be considered for the HV & IV System to which the transformers will be connected: 765kV system - 63 kA for 1 sec (sym, rms, 3 phase fault) 400kV system - 63 kA for 1 sec (sym, rms, 3 phase fault) 220kV system - 50 kA for 1 sec (sym, rms, 3 phase fault) 132kV system - 40 kA for 1 sec (sym, rms, 3 phase fault) 66kV system - 31.5 kA for 1 sec (sym, rms, 3 phase fault) However, for transformer design purpose, the through fault current shall be considered limited by the transformer self-impedance only (i.e. Zs = 0). | NOT COVERED | NOT VERIFIED | 765kV; 400kV; 220kV; 132kV; 66kV | NOT COVERED | 5.1.9 The following short circuit level shall be considered for the HV & IV System to which the transformers will be connected: 765kV system - 63 kA for 1 sec (sym, rms, 3 phase fault) 400kV system - 63 kA for 1 sec (sym, rms, 3 phase fault) 220kV system - 50 kA for 1 sec (sym, rms, 3 phase fault) 132kV system - 40 kA for 1 sec (sym, rms, 3 phase fault) 66kV system - 31.5 kA for 1 sec (sym, rms, 3 phase fault) However, for transformer design purpose, the through fault current shall be considered limited by the transformer self-impedance only (i.e. Zs = 0). | Transformers and reactors, 66 kV and above voltage class | PDF p. 30 | Chapter-2: Technical Specification for Transformer and Reactor Page II-3 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0048 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | Mechanical strength of the transformer shall be such that it can withstand 3-phase and 1- phase through fault with rated voltage applied to HV and/or IV terminals of transformer. The short circuit shall alternatively be considered to be applied to each of the HV, IV and tertiary (LV) transformer terminals as applicable. The tertiary terminals shall be considered not connected to system source. For short circuit on the tertiary terminals, the in-feed from both HV & IV system shall be limited by the transformer self-impedance only and the rated voltage of HV and IV terminals shall be considered. 5.1.11 Transformers shall withstand, without damage, heating due to the combined voltage and frequency fluctuations which produce the following over fluxing conditions: 110 % continuously 125 % for 1 minute 140 % for 5 seconds | NOT COVERED | NOT VERIFIED | 1 minute | NOT COVERED | Mechanical strength of the transformer shall be such that it can withstand 3-phase and 1- phase through fault with rated voltage applied to HV and/or IV terminals of transformer. The short circuit shall alternatively be considered to be applied to each of the HV, IV and tertiary (LV) transformer terminals as applicable. The tertiary terminals shall be considered not connected to system source. For short circuit on the tertiary terminals, the in-feed from both HV & IV system shall be limited by the transformer self-impedance only and the rated voltage of HV and IV terminals shall be considered. 5.1.11 Transformers shall withstand, without damage, heating due to the combined voltage and frequency fluctuations which produce the following over fluxing conditions: 110 % continuously 125 % for 1 minute 140 % for 5 seconds | Transformers and reactors, 66 kV and above voltage class | PDF p. 31 | Chapter-2: Technical Specification for Transformer and Reactor Page II-4 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0049 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Maintenance Schedule | Grounding | SCHEDULE | 5.3 Shunt Reactor and Neutral Grounding Reactor (NGR) 5.3.1 Shunt reactors will be connected to the transmission system for reactive compensation and shall be capable of controlling the over voltages occurring in the system. 5.3.2 The neutral grounding reactor is required for grounding of the neutral point of shunt reactor (for line reactor only) to limit the secondary arc current and the recovery voltage to a minimum value. 5.3.3 765 kV shunt reactors shall be designed for switching surge overvoltage of 1.9 p.u. and temporary over voltage of the order of 1.4 p.u. for about 15 cycles followed by power frequency overvoltage upto 830 kVrms for about five minutes. The reactor shall withstand the stress due to above transient conditions which may cause additional current flow as a result of changed saturation characteristics/slope beyond 1.25 p.u. voltage. | NOT COVERED | NOT VERIFIED | 765 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 32 | Chapter-2: Technical Specification for Transformer and Reactor Page II-5 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0050 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 5.3.4 420 kV and below shunt reactors shall be designed for switching surge overvoltage of 2.5 p.u. and temporary overvoltage of the order of 2.3 p.u. for few cycles followed by power frequency overvoltage upto 1.5 p.u. The reactor must withstand the stress due to above transient conditions which may cause additional current flow as a result of changed saturation characteristics/ slope beyond 1.5 p.u. 5.3.5 The thermal and cooling system shall be designed for maximum continuous operating voltage Um (where Um= 800/√3 kV for 765/√3 kV reactor; 420 kV for 420 kV reactor & 245 kV for 245 kV reactor). 5.3.6 In addition, the reactors shall be designed to withstand the following over-voltages repeatedly without risk of failure (w.r.t. | NOT COVERED | NOT VERIFIED | 420 kV; 3 kV; 245 kV | NOT COVERED | 5.3.4 420 kV and below shunt reactors shall be designed for switching surge overvoltage of 2.5 p.u. and temporary overvoltage of the order of 2.3 p.u. for few cycles followed by power frequency overvoltage upto 1.5 p.u. The reactor must withstand the stress due to above transient conditions which may cause additional current flow as a result of changed saturation characteristics/ slope beyond 1.5 p.u. 5.3.5 The thermal and cooling system shall be designed for maximum continuous operating voltage Um (where Um= 800/√3 kV for 765/√3 kV reactor; 420 kV for 420 kV reactor & 245 kV for 245 kV reactor). 5.3.6 In addition, the reactors shall be designed to withstand the following over-voltages repeatedly without risk of failure (w.r.t. | Transformers and reactors, 66 kV and above voltage class | PDF p. 32 | Chapter-2: Technical Specification for Transformer and Reactor Page II-5 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0051 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Hotspot temperature of 140 oC & core saturation): 1.05 Um Continuous (for 765 kV & 420 kV reactor) 1.10 Um Continuous (for 245 kV reactor) 1.50 Um for 5 seconds 1.25 Um for 1 minute 5.3.7 The winding hot spots shall be calculated considering the maximum localized losses, insulation thickness at the maximum loss and the oil flow patterns in the winding. The oil temperature rise in the windings shall be used to determine hot spots rather than the bulk top oil temperature. The hot spot for all leads shall be calculated and it shall not exceed the calculated hot spot of the windings. | NOT COVERED | NOT VERIFIED | 765 kV; 420 kV; 245 kV; 1 minute | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 32 | Chapter-2: Technical Specification for Transformer and Reactor Page II-5 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0052 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Maintenance | General | MAINTENANCE | 5.3.8 Tank hotspot temperature under over voltage condition specified above shall not exceed 110 deg C considering maximum ambient temperature as 50 deg C. 5.3.9 Also, the most onerous temperature of any part of the core and its supporting structure in contact with insulation or non-metal material shall not exceed the safe operating temperature of that material. Adequate temperature margins shall be provided to maintain long life expectancy of these materials. 5.3.10 The magnetic circuit shall be designed such that the magnetic characteristic of reactor is linear upto voltage specified at Annexure– A. | 5.3.8 Tank hotspot temperature under over voltage condition specified above shall not exceed 110 deg C considering maximum ambient temperature as 50 deg C. 5.3.9 Also, the most onerous temperature of any part of the core and its supporting structure in contact with insulation or non-metal material shall not exceed the safe operating temperature of that material. Adequate temperature margins shall be provided to maintain long life expectancy of these materials. 5.3.10 The magnetic circuit shall be designed such that the magnetic characteristic of reactor is linear upto voltage specified at Annexure– A. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 33 | Chapter-2: Technical Specification for Transformer and Reactor Page II-6 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0053 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Maintenance Schedule | GIS | SCHEDULE | The noise level of transformer, when energised at normal voltage and frequency with fans and pumps running shall not exceed the values specified at Annexure- A, when measured under standard conditions. 6.0 MAXIMUM LOSSES | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 33 | Chapter-2: Technical Specification for Transformer and Reactor Page II-6 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0054 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | The maximum permissible losses (No load loss, I2R loss, auxiliary loss and load loss) at rated voltage/current (at 75 deg C) have been specified in Annexure-A for various ratings of transformers/ reactors covered under this specification. Following penalties shall be levied on the manufacturer/contractor (as the case may be) if losses measured during routine test are found to be within +2% tolerance of the losses specified in Annexure–A, beyond which the transformer/reactor shall be liable for rejection. No benefit shall be given for supply of transformer/reactor, with losses (measured during routine tests) less than the losses specified in Annexure –A. | The maximum permissible losses (No load loss, I2R loss, auxiliary loss and load loss) at rated voltage/current (at 75 deg C) have been specified in Annexure-A for various ratings of transformers/ reactors covered under this specification. Following penalties shall be levied on the manufacturer/contractor (as the case may be) if losses measured during routine test are found to be within +2% tolerance of the losses specified in Annexure–A, beyond which the transformer/reactor shall be liable for rejection. No benefit shall be given for supply of transformer/reactor, with losses (measured during routine tests) less than the losses specified in Annexure –A. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 33 | Chapter-2: Technical Specification for Transformer and Reactor Page II-6 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0055 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | 7.0 DYNAMIC SHORT CIRCUIT TEST REQUIREMENT AND VALIDITY The transformer, the design of which is similar to the offered transformer, should have been successfully tested for short circuit withstand capability as per IS 2026 Part-5 in line with the requirement of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations. The criteria for similar transformer is specified in Annexure-J. The relevant Test Report/certificate shall be enclosed along with bid. Further, design review of offered transformer shall be carried out based on the design of reference transformer, which has already been subjected to Short circuit tests in lieu of repetition of Short circuit tests. In case, manufacturer has not conducted short circuit test earlier, the same shall be carried out on offered transformer. | 7.0 DYNAMIC SHORT CIRCUIT TEST REQUIREMENT AND VALIDITY The transformer, the design of which is similar to the offered transformer, should have been successfully tested for short circuit withstand capability as per IS 2026 Part-5 in line with the requirement of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations. The criteria for similar transformer is specified in Annexure-J. The relevant Test Report/certificate shall be enclosed along with bid. Further, design review of offered transformer shall be carried out based on the design of reference transformer, which has already been subjected to Short circuit tests in lieu of repetition of Short circuit tests. In case, manufacturer has not conducted short circuit test earlier, the same shall be carried out on offered transformer. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 34 | Chapter-2: Technical Specification for Transformer and Reactor Page II-7 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0056 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Testing | Bushing | TESTING | A format (forms part of Annexure-J) filled with data of a typical sample case has been prepared for reference and guidance of utility to compare a Short Circuit tested transformer with the offered transformer in order to verify the similarity criteria as per Annexure J. 8.0 TYPE TESTS REQUIREMENT AND VALIDITY The offered transformer/reactor or the transformer/reactor, the design of which is similar to the offered transformer/reactor, should have been successfully type tested within last 5 years as on the last date of submission of bid. Manufacturer may use same or different approved make of Bushings, Tap changer and other accessories used in type tested or short circuit tested unit in their transformer/reactor. Further, type test report of transformer/reactor shall only be acceptable provided the offered transformer/reactor has been manufactured from the same plant. | A format (forms part of Annexure-J) filled with data of a typical sample case has been prepared for reference and guidance of utility to compare a Short Circuit tested transformer with the offered transformer in order to verify the similarity criteria as per Annexure J. 8.0 TYPE TESTS REQUIREMENT AND VALIDITY The offered transformer/reactor or the transformer/reactor, the design of which is similar to the offered transformer/reactor, should have been successfully type tested within last 5 years as on the last date of submission of bid. Manufacturer may use same or different approved make of Bushings, Tap changer and other accessories used in type tested or short circuit tested unit in their transformer/reactor. Further, type test report of transformer/reactor shall only be acceptable provided the offered transformer/reactor has been manufactured from the same plant. | NOT VERIFIED | 5 years | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 34 | Chapter-2: Technical Specification for Transformer and Reactor Page II-7 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0057 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Central Electricity Authority’s “Guidelines for the validity period of type tests conducted on major electrical equipment in power transmission system” shall be followed for details regarding the validity of type tests. | Central Electricity Authority’s “Guidelines for the validity period of type tests conducted on major electrical equipment in power transmission system” shall be followed for details regarding the validity of type tests. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 34 | Chapter-2: Technical Specification for Transformer and Reactor Page II-7 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0058 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | General | SAFETY | accordance with the best international engineering practices under strict quality control to meet the requirement stipulated in the technical specification. Adequate safety margin w.r.t. thermal, mechanical, dielectric and electrical stress etc. shall be maintained during design, selection of raw material, manufacturing process etc. in order to achieve long life of transformer/reactor with least maintenance. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | accordance with the best international engineering practices under strict quality control to meet the requirement stipulated in the technical specification. Adequate safety margin w.r.t. thermal, mechanical, dielectric and electrical stress etc. shall be maintained during design, selection of raw material, manufacturing process etc. in order to achieve long life of transformer/reactor with least maintenance. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 35 | Chapter-2: Technical Specification for Transformer and Reactor Page II-8 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0059 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | General | INSPECTION | consultant during the procurement process; however, the entire responsibility of design shall be with the manufacturer. Purchaser may also visit the manufacturers works to inspect design, manufacturing and test facilities. | consultant during the procurement process; however, the entire responsibility of design shall be with the manufacturer. Purchaser may also visit the manufacturers works to inspect design, manufacturing and test facilities. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 35 | Chapter-2: Technical Specification for Transformer and Reactor Page II-8 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0060 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | adequate safety margins for thermal, mechanical, dielectric and vibration etc. in design to take into account the uncertainties of his design and manufacturing processes. The scope of such design review shall include but not limited to the requirement as mentioned at Annexure – I. 9.6 Each page of the design review document shall be duly signed by the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | adequate safety margins for thermal, mechanical, dielectric and vibration etc. in design to take into account the uncertainties of his design and manufacturing processes. The scope of such design review shall include but not limited to the requirement as mentioned at Annexure – I. 9.6 Each page of the design review document shall be duly signed by the | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 35 | Chapter-2: Technical Specification for Transformer and Reactor Page II-8 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0061 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, GIS | NOT VERIFIED | Maintenance Schedule | GIS | SCHEDULE | In addition to the above, utilities may specify additional site conditions separately in tender documents [example: restricted ventilation (tunnels, enclosed area etc.), presence of fumes, vapours, steams, dripping of waters, salt spray and corrosive environment, excessive & abrasive dust, superimposed DC current in neutral of the transformer/reactor, high frequency switching transients, frequent energisation (>24 times a year), high solar radiation, frequent Short Circuits etc.]. 11.0 CONSTRUCTION DETAILS The construction details and features of transformer/reactor shall be in accordance with the requirement stated hereunder. 11.1 Tank & tank cover 11.1.1 The tank shall be of proven design of either Bell type with bolted/ welded joint or conventional (preferable) with bolted/welded top cover. Bell type tank, if provided, shall have joint as close as possible to the bottom of the tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 36 | Chapter-2: Technical Specification for Transformer and Reactor Page II-9 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0062 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 11.1.8 Tank stiffeners shall be provided for general rigidity and welded to the tank continuously along its ends and sides (Intermittent welds will not be accepted). These shall be designed to prevent retention of water. Sharp edges on stiffeners should be avoided for better paint adhesion. 11.1.9 Tank MS plates of thickness >12 mm should undergo Ultrasonic Test (UT) to check lamination defect, internal impurities in line with ASTM 435 & ASTM 577. 11.1.10 After fabrication of tank and before painting, Non-destructive test (dye penetration test) is mandatory on the load bearing members such as base plate joints, jacking pads and lifting devices etc. 11.1.11 Suitable guides shall be provided for positioning the various parts during assembly or dismantling. Adequate space shall be provided between the covers & windings and the bottom of the tank for collection of any sediment. | NOT COVERED | NOT VERIFIED | 12 mm | NOT COVERED | 11.1.8 Tank stiffeners shall be provided for general rigidity and welded to the tank continuously along its ends and sides (Intermittent welds will not be accepted). These shall be designed to prevent retention of water. Sharp edges on stiffeners should be avoided for better paint adhesion. 11.1.9 Tank MS plates of thickness >12 mm should undergo Ultrasonic Test (UT) to check lamination defect, internal impurities in line with ASTM 435 & ASTM 577. 11.1.10 After fabrication of tank and before painting, Non-destructive test (dye penetration test) is mandatory on the load bearing members such as base plate joints, jacking pads and lifting devices etc. 11.1.11 Suitable guides shall be provided for positioning the various parts during assembly or dismantling. Adequate space shall be provided between the covers & windings and the bottom of the tank for collection of any sediment. | Transformers and reactors, 66 kV and above voltage class | PDF p. 38 | Chapter-2: Technical Specification for Transformer and Reactor Page II-11 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0063 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Inspection | Bushing | INSPECTION | 11.1.12 Tank should be provided with adequately sized inspection covers, either in circular shape or in rectangular shape, preferably at diagonally opposite sides of the tank to access the active part and one at each end of the tank cover for easy access of the lower end of the bushings, earthing connections and tap changers etc. for inspection. Inspection covers shall be bolted type and shall not weigh more than 25 kgs. Handles shall be provided on the inspection cover to facilitate its lifting. | 11.1.12 Tank should be provided with adequately sized inspection covers, either in circular shape or in rectangular shape, preferably at diagonally opposite sides of the tank to access the active part and one at each end of the tank cover for easy access of the lower end of the bushings, earthing connections and tap changers etc. for inspection. Inspection covers shall be bolted type and shall not weigh more than 25 kgs. Handles shall be provided on the inspection cover to facilitate its lifting. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 38 | Chapter-2: Technical Specification for Transformer and Reactor Page II-11 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0064 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | 11.1.13 The tank cover shall be provided with pockets for oil and winding temperature indicators. The location of pockets (for OTI, WTI & RTDs including two spare pockets) shall be in the position where oil reaches maximum temperature. Further, it shall be possible to remove bulbs/probes of OTI/WTI/RTD without lowering the oil in the tank. The thermometer shall be fitted with a captive screw to prevent the ingress of water. 11.1.14 It should be possible to inspect Buchholz relay or Oil surge relay, standing on tank cover or suitable arrangement shall be made to access Buchholz relay safely. 11.1.15 The tank cover shall be designed to prevent retention of rain water Bushing turrets, covers of inspection openings, thermometer pockets etc. shall be designed to prevent ingress of water into or leakage of oil from the tank. | 11.1.13 The tank cover shall be provided with pockets for oil and winding temperature indicators. The location of pockets (for OTI, WTI & RTDs including two spare pockets) shall be in the position where oil reaches maximum temperature. Further, it shall be possible to remove bulbs/probes of OTI/WTI/RTD without lowering the oil in the tank. The thermometer shall be fitted with a captive screw to prevent the ingress of water. 11.1.14 It should be possible to inspect Buchholz relay or Oil surge relay, standing on tank cover or suitable arrangement shall be made to access Buchholz relay safely. 11.1.15 The tank cover shall be designed to prevent retention of rain water Bushing turrets, covers of inspection openings, thermometer pockets etc. shall be designed to prevent ingress of water into or leakage of oil from the tank. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 38 | Chapter-2: Technical Specification for Transformer and Reactor Page II-11 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0065 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, AIS | NOT VERIFIED | Safety | Transformer Oil | SAFETY | 11.1.16 Minimum four symmetrically placed lifting lugs of adequate size shall be provided so that it will be possible to lift the complete transformer/reactor when filled with oil & without structural damage to any part of the transformer/reactor. The factor of safety at any lug shall not be less than 2. Suitable haulage holes shall also be provided. 11.1.17 A minimum of four jacking pads (not fouling with rail, rollers or other accessories) shall be provided in accessible position to enable the transformer complete with oil to be raised or lowered using hydraulic jacks. The location shall be such that it should not interfere with loading & unloading from trailer. | NOT COVERED | NOT VERIFIED | 1.17 A | 11.1.16 Minimum four symmetrically placed lifting lugs of adequate size shall be provided so that it will be possible to lift the complete transformer/reactor when filled with oil & without structural damage to any part of the transformer/reactor. The factor of safety at any lug shall not be less than 2. Suitable haulage holes shall also be provided. 11.1.17 A minimum of four jacking pads (not fouling with rail, rollers or other accessories) shall be provided in accessible position to enable the transformer complete with oil to be raised or lowered using hydraulic jacks. The location shall be such that it should not interfere with loading & unloading from trailer. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 39 | Chapter-2: Technical Specification for Transformer and Reactor Page II-12 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0066 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY | 11.1.18 Each jacking pad shall be designed with an adequate factor of safety to support at least half of the total mass of the transformer filled with oil in addition to maximum possible misalignment of the jacking force to the centre of the working surface. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 11.1.18 Each jacking pad shall be designed with an adequate factor of safety to support at least half of the total mass of the transformer filled with oil in addition to maximum possible misalignment of the jacking force to the centre of the working surface. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 39 | Chapter-2: Technical Specification for Transformer and Reactor Page II-12 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0067 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | 11.1.20 The tank cover and bushing turret shall be fixed to the transformer using copper links in such a way that good electrical contact is maintained around the perimeter of the tank and turrets. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 11.1.20 The tank cover and bushing turret shall be fixed to the transformer using copper links in such a way that good electrical contact is maintained around the perimeter of the tank and turrets. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 39 | Chapter-2: Technical Specification for Transformer and Reactor Page II-12 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0068 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | 11.1.21 The transformer/reactor shall be provided with a suitable diameter pipe flange, butterfly valve, bolted blanking plate and gasket at the highest point of the transformer / reactor for maintaining vacuum in the tank. | 11.1.21 The transformer/reactor shall be provided with a suitable diameter pipe flange, butterfly valve, bolted blanking plate and gasket at the highest point of the transformer / reactor for maintaining vacuum in the tank. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 39 | Chapter-2: Technical Specification for Transformer and Reactor Page II-12 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0069 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | 11.1.22 Gas venting: The transformer/reactor cover and generally the internal spaces of the transformer/reactor and all pipe connections shall be designed so as to provide efficient venting of any gas in any part of the transformer/reactor to the Buchholz relay. The space created under inspection /manhole covers shall be filled with suitable material to avoid inadvertent gas pockets. The Covers shall be vented at least at both longitudinal ends. The design for gas venting shall take into accounts the slopes of the plinth (if any) on which the transformer/reactor is being mounted. | 11.1.22 Gas venting: The transformer/reactor cover and generally the internal spaces of the transformer/reactor and all pipe connections shall be designed so as to provide efficient venting of any gas in any part of the transformer/reactor to the Buchholz relay. The space created under inspection /manhole covers shall be filled with suitable material to avoid inadvertent gas pockets. The Covers shall be vented at least at both longitudinal ends. The design for gas venting shall take into accounts the slopes of the plinth (if any) on which the transformer/reactor is being mounted. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 39 | Chapter-2: Technical Specification for Transformer and Reactor Page II-12 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0070 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | All gasketed joints shall be designed, manufactured and assembled to ensure long-term leak proof and maintenance free operation. All gasketed joints shall preferably be O-ring and designed with gasket-in-groove arrangement. If gasket/O-rings is compressible, | All gasketed joints shall be designed, manufactured and assembled to ensure long-term leak proof and maintenance free operation. All gasketed joints shall preferably be O-ring and designed with gasket-in-groove arrangement. If gasket/O-rings is compressible, | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 39 | Chapter-2: Technical Specification for Transformer and Reactor Page II-12 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0071 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | metallic stops/other suitable means shall be provided to prevent over- compression. All bolted connections shall be fitted with weather proof, hot oil resistant, resilient gasket in between for complete oil tightness. All matching flanges of gasket sealing joints should be machined (except curb joints). Gasket with intermediate stops are not acceptable. To the extent possible, the seamless gasket should be used for openings on tank/cover such as turrets, bushing, inspection covers etc. All tank gaskets/O-rings used shall be of NBR (Acrylonitrile Butadiene Rubber) suitable for temperature conditions expected to be encountered during operation. The gasket material and additives should be fully compatible with transformer insulating fluid/oil. The gasket should not contain oil soluble sulphur compounds. The properties of all the above gaskets/O-Rings shall comply with the requirements of type-IV rubber of IS-11149. Gaskets and O-rings shall be replaced every time whenever the joints are opened. 11.3 Foundation, Roller Assembly and Anti Earthquake Clamping Device | metallic stops/other suitable means shall be provided to prevent over- compression. All bolted connections shall be fitted with weather proof, hot oil resistant, resilient gasket in between for complete oil tightness. All matching flanges of gasket sealing joints should be machined (except curb joints). Gasket with intermediate stops are not acceptable. To the extent possible, the seamless gasket should be used for openings on tank/cover such as turrets, bushing, inspection covers etc. All tank gaskets/O-rings used shall be of NBR (Acrylonitrile Butadiene Rubber) suitable for temperature conditions expected to be encountered during operation. The gasket material and additives should be fully compatible with transformer insulating fluid/oil. The gasket should not contain oil soluble sulphur compounds. The properties of all the above gaskets/O-Rings shall comply with the requirements of type-IV rubber of IS-11149. Gaskets and O-rings shall be replaced every time whenever the joints are opened. 11.3 Foundation, Roller Assembly and Anti Earthquake Clamping Device | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 40 | Chapter-2: Technical Specification for Transformer and Reactor Page II-13 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0072 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Design / Technical Reference | Fire Protection | DESIGN_REFERENCE | 11.3.6 For foundation of separately mounted cooler bank of transformer/reactor, fixing of cooler support shall be through Anchor Fastener with chemical grouting and no pockets for bolting shall be provided. 11.3.7 For support of cooler pipes, Buchholz pipe (if required) and fire-fighting pipe pylon supports, Pre-fabricated metallic support from pit shall be provided which shall be further encased with concrete to prevent rusting. 11.3.8 All control cubicles shall be mounted at least one meter above Finished Ground Level (FGL) to take care of water logging during flooding. Suitable arrangement (ladder and platform) shall be provided for safe access to control cubicles. 11.4 Conservator | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 41 | Chapter-2: Technical Specification for Transformer and Reactor Page II-14 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0073 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 11.4.1 The conservator of main tank shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator shall be fitted with magnetic oil level gauge with potential free high and low oil level alarm contacts and prismatic oil level gauge. 11.4.2 The conservator shall preferably be on the left side of the tank while viewing from HV side. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 41 | Chapter-2: Technical Specification for Transformer and Reactor Page II-14 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0074 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, AIS | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | 11.4.3 Conservator tank shall have adequate capacity with highest and lowest visible-levels to meet the requirements of expansion of total cold oil volume in the transformer and cooling equipment from minimum ambient temperature to top oil temperature of 100 deg C. The capacity of the conservator tank shall be such that the transformer shall be able to carry the specified overload without overflowing of oil. 11.4.4 The conservator shall be fitted with lifting lugs in such a position so that it can be removed for cleaning purposes. Suitable provision shall be kept to replace air cell and cleaning of the conservator as applicable. 11.4.5 The conservator shall be positioned so as not to obstruct any electrical connection to transformer. 11.4.6 Contact of the oil with atmosphere is prohibited by using a flexible air cell of nitrile rubber reinforced with nylon cloth. The temperature of oil in the conservator is likely to raise up to 100 Deg C during operation. As such air cell used shall be suitable for operating continuously at this temperature. | 11.4.3 Conservator tank shall have adequate capacity with highest and lowest visible-levels to meet the requirements of expansion of total cold oil volume in the transformer and cooling equipment from minimum ambient temperature to top oil temperature of 100 deg C. The capacity of the conservator tank shall be such that the transformer shall be able to carry the specified overload without overflowing of oil. 11.4.4 The conservator shall be fitted with lifting lugs in such a position so that it can be removed for cleaning purposes. Suitable provision shall be kept to replace air cell and cleaning of the conservator as applicable. 11.4.5 The conservator shall be positioned so as not to obstruct any electrical connection to transformer. 11.4.6 Contact of the oil with atmosphere is prohibited by using a flexible air cell of nitrile rubber reinforced with nylon cloth. The temperature of oil in the conservator is likely to raise up to 100 Deg C during operation. As such air cell used shall be suitable for operating continuously at this temperature. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 41 | Chapter-2: Technical Specification for Transformer and Reactor Page II-14 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0075 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 11.4.7 The connection of air cell to the top of the conservator is by air proof seal preventing entrance of air into the conservator. The main conservator tank shall be stencilled on its underside with the words “Caution: Air cell fitted”. Lettering of at least 150 mm size shall be used in such a way to ensure clear legibility from ground level when the transformer/reactor is fully installed. To prevent oil filling into the air cell, the oil filling aperture shall be clearly marked. The transformer/reactor rating and diagram plate shall bear a warning statement that the “Main conservator is fitted with an air cell”. 11.4.8 The transformer/reactor manual shall give clear instructions on the operation, maintenance, testing and replacement of the air cell. It shall also indicate shelf life, life expectancy in operation, and the recommended replacement intervals. | 11.4.7 The connection of air cell to the top of the conservator is by air proof seal preventing entrance of air into the conservator. The main conservator tank shall be stencilled on its underside with the words “Caution: Air cell fitted”. Lettering of at least 150 mm size shall be used in such a way to ensure clear legibility from ground level when the transformer/reactor is fully installed. To prevent oil filling into the air cell, the oil filling aperture shall be clearly marked. The transformer/reactor rating and diagram plate shall bear a warning statement that the “Main conservator is fitted with an air cell”. 11.4.8 The transformer/reactor manual shall give clear instructions on the operation, maintenance, testing and replacement of the air cell. It shall also indicate shelf life, life expectancy in operation, and the recommended replacement intervals. | NOT VERIFIED | 150 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 42 | Chapter-2: Technical Specification for Transformer and Reactor Page II-15 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0076 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 11.4.9 The conservator tank and piping shall be designed for complete vacuum/ filling of the main tank and conservator tank. Provision must be made for equalising the pressure in the conservator tank and the air cell during vacuum/ filling operations to prevent rupturing of the air cell. 11.4.10 The contractor shall furnish the leakage rates of the rubber bag/ air cell for oxygen and moisture. It is preferred that the leakage rate for oxygen from the air cell into the oil will be low enough so that the oil will not generally become saturated with oxygen. Air cells with well proven long life characteristics shall be preferred. 11.4.11 OLTC shall have conventional type conservator (without aircell) with magnetic oil level gauge with potential free oil level alarm contact and prismatic oil level gauge. | 11.4.9 The conservator tank and piping shall be designed for complete vacuum/ filling of the main tank and conservator tank. Provision must be made for equalising the pressure in the conservator tank and the air cell during vacuum/ filling operations to prevent rupturing of the air cell. 11.4.10 The contractor shall furnish the leakage rates of the rubber bag/ air cell for oxygen and moisture. It is preferred that the leakage rate for oxygen from the air cell into the oil will be low enough so that the oil will not generally become saturated with oxygen. Air cells with well proven long life characteristics shall be preferred. 11.4.11 OLTC shall have conventional type conservator (without aircell) with magnetic oil level gauge with potential free oil level alarm contact and prismatic oil level gauge. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 42 | Chapter-2: Technical Specification for Transformer and Reactor Page II-15 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0077 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 11.4.12 Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be externally installed on the top of conservator to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 42 | Chapter-2: Technical Specification for Transformer and Reactor Page II-15 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0078 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | on the conservator side of the relay. This pipe shall rise towards the oil conservator, through the Buchholz relay, at an angle of not less than 3 degrees. The feed pipe diameter for the main conservator shall be not less than 80mm. The Gas-venting pipes shall be connected to the final rising pipe between the transformer/reactor and Buchholz relay as near as possible in an axial direction and preferably not less than five times pipe diameters from the Buchholz relay. 11.5.3 No metal corrugated bellow (Flexible metal system) should be used in the feed pipe connecting main tank to conservator. 11.5.4 A double flange valve of preferably 50 mm and 25 mm size shall be provided to fully drain the oil from the main tank conservator and OLTC conservator tank respectively. 11.5.5 Pipe work shall neither obstruct the removal of tap changers for maintenance or the opening of inspection or manhole covers. | on the conservator side of the relay. This pipe shall rise towards the oil conservator, through the Buchholz relay, at an angle of not less than 3 degrees. The feed pipe diameter for the main conservator shall be not less than 80mm. The Gas-venting pipes shall be connected to the final rising pipe between the transformer/reactor and Buchholz relay as near as possible in an axial direction and preferably not less than five times pipe diameters from the Buchholz relay. 11.5.3 No metal corrugated bellow (Flexible metal system) should be used in the feed pipe connecting main tank to conservator. 11.5.4 A double flange valve of preferably 50 mm and 25 mm size shall be provided to fully drain the oil from the main tank conservator and OLTC conservator tank respectively. 11.5.5 Pipe work shall neither obstruct the removal of tap changers for maintenance or the opening of inspection or manhole covers. | NOT VERIFIED | 80mm; 5.4 A; 50 mm; 25 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 43 | Chapter-2: Technical Specification for Transformer and Reactor Page II-16 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0079 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Conservator of Main Tank and OLTC shall be fitted with dehydrating silica gel filter breathers of adequate size. Connection shall be made to a point in the oil conservator not less than 50 mm above the maximum working oil level by means of a pipe with a minimum diameter of 25 mm. Breathers and connecting pipes shall be securely clamped and supported to the transformer/reactor, or other structure supplied by the manufacturer, in such a manner so as to eliminate undesirable vibration and noise. The design shall be such that: | NOT COVERED | NOT VERIFIED | 50 mm; 25 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 43 | Chapter-2: Technical Specification for Transformer and Reactor Page II-16 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0080 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | a) Passage of air is through silica gel. b) Silica gel is isolated from atmosphere by an oil seal. c) Moisture absorption indicated by a change in colour of the crystals. d) Breather is mounted approximately 1200 mm above rail top level. e) To minimise the ingress of moisture three breathers (of identical size) for 220kV and above voltage class transformer/reactor and two breathers (of identical size) for below 220kV class transformer/reactor shall be connected in series for main tank conservator. Manufacturer shall provide flexible connection pipes to be used during replacement of any silica gel breather. f) To minimise the ingress of moisture, two breather in series of identical size shall be connected to OLTC Conservator. Manufacturer shall provide flexible connection pipes to be used during replacement of any silica gel breather. | NOT COVERED | NOT VERIFIED | 1200 mm; 220kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 43 | Chapter-2: Technical Specification for Transformer and Reactor Page II-16 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0081 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | Note: Regenerative maintenance free breather may also be used if desired by the utility. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 44 | Chapter-2: Technical Specification for Transformer and Reactor Page II-17 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0082 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | One PRD of 150 mm Diameter is required for every 30000 Litres of oil. However, at least two numbers PRDs shall be provided. Its mounting should be either in vertical or horizontal orientation, preferably close to bushing turret or cover. PRD operating pressure selected shall be verified during design review. PRD shall be provided with special shroud to direct the hot oil in case of fault condition. It shall be provided with an outlet pipe which shall be taken right up to the soak pit of the transformer/reactor. The size (Diameter) of shroud shall be such that it should not restrict rapid release of any pressure that may be generated in the tank, which may result in damage to equipment. Oil shroud should be kept away from control cubicle and clear of any operating position to avoid injury to personnel in the event of PRD operation. | NOT COVERED | NOT VERIFIED | 150 mm; 30000 Litres | NOT COVERED | One PRD of 150 mm Diameter is required for every 30000 Litres of oil. However, at least two numbers PRDs shall be provided. Its mounting should be either in vertical or horizontal orientation, preferably close to bushing turret or cover. PRD operating pressure selected shall be verified during design review. PRD shall be provided with special shroud to direct the hot oil in case of fault condition. It shall be provided with an outlet pipe which shall be taken right up to the soak pit of the transformer/reactor. The size (Diameter) of shroud shall be such that it should not restrict rapid release of any pressure that may be generated in the tank, which may result in damage to equipment. Oil shroud should be kept away from control cubicle and clear of any operating position to avoid injury to personnel in the event of PRD operation. | Transformers and reactors, 66 kV and above voltage class | PDF p. 44 | Chapter-2: Technical Specification for Transformer and Reactor Page II-17 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0083 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The device shall maintain its oil tightness under static oil pressure equal to the static operating head of oil plus 20 kPa. It shall be capable of withstanding full internal vacuum at mean sea level. It shall be mounted directly on the tank. Suitable canopy shall be provided to prevent ingress of rain water. One set of potential free contacts (with plug & socket type arrangement) per device shall be provided for tripping. Following routine tests shall be conducted on PRD: | The device shall maintain its oil tightness under static oil pressure equal to the static operating head of oil plus 20 kPa. It shall be capable of withstanding full internal vacuum at mean sea level. It shall be mounted directly on the tank. Suitable canopy shall be provided to prevent ingress of rain water. One set of potential free contacts (with plug & socket type arrangement) per device shall be provided for tripping. Following routine tests shall be conducted on PRD: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 44 | Chapter-2: Technical Specification for Transformer and Reactor Page II-17 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0084 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | a) Air pressure test b) Liquid pressure test c) Leakage test d) Contact operation test e) Dielectric test on contact terminals | a) Air pressure test b) Liquid pressure test c) Leakage test d) Contact operation test e) Dielectric test on contact terminals | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 44 | Chapter-2: Technical Specification for Transformer and Reactor Page II-17 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0085 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Pressurised water ingress test for Terminal Box (routine tests) shall be conducted on Sudden Pressure Relay/ Rapid Pressure Rise Relay. | Pressurised water ingress test for Terminal Box (routine tests) shall be conducted on Sudden Pressure Relay/ Rapid Pressure Rise Relay. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 45 | Chapter-2: Technical Specification for Transformer and Reactor Page II-18 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0086 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Double float, reed type Buchholz relay complying with IS:3637 shall be connected through pipe between the oil conservator and the transformer/reactor tank with minimum distance of five times pipe diameters between them. Any gas evolved in the transformer/reactor shall be collected in this relay. The relay shall be provided with a test cock suitable for a flexible pipe connection for checking its operation and taking gas sample. A copper tube shall be connected from the gas collector to a valve located about 1200 mm above ground level to facilitate sampling while the transformer/reactor in service. Suitable canopy shall be provided to prevent ingress of rain water. It shall be provided with two potential free contacts (Plug & socket type arrangement), one for alarm/trip on gas accumulation and the other for tripping on sudden rise of pressure. | NOT COVERED | NOT VERIFIED | 1200 mm | Double float, reed type Buchholz relay complying with IS:3637 shall be connected through pipe between the oil conservator and the transformer/reactor tank with minimum distance of five times pipe diameters between them. Any gas evolved in the transformer/reactor shall be collected in this relay. The relay shall be provided with a test cock suitable for a flexible pipe connection for checking its operation and taking gas sample. A copper tube shall be connected from the gas collector to a valve located about 1200 mm above ground level to facilitate sampling while the transformer/reactor in service. Suitable canopy shall be provided to prevent ingress of rain water. It shall be provided with two potential free contacts (Plug & socket type arrangement), one for alarm/trip on gas accumulation and the other for tripping on sudden rise of pressure. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 45 | Chapter-2: Technical Specification for Transformer and Reactor Page II-18 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0087 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | The Buchholz relay shall not operate during starting/stopping of the transformer oil circulation under any oil temperature conditions. The pipe or relay aperture baffles shall not be used to decrease the sensitivity of the relay. The relay shall not mal-operate for through fault conditions or be influenced by the magnetic fields around the transformer/reactor during the external fault conditions. Pressurised water ingress test for Terminal Box (routine tests) shall be conducted on Buchholz relay. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The Buchholz relay shall not operate during starting/stopping of the transformer oil circulation under any oil temperature conditions. The pipe or relay aperture baffles shall not be used to decrease the sensitivity of the relay. The relay shall not mal-operate for through fault conditions or be influenced by the magnetic fields around the transformer/reactor during the external fault conditions. Pressurised water ingress test for Terminal Box (routine tests) shall be conducted on Buchholz relay. | Transformers and reactors, 66 kV and above voltage class | PDF p. 45 | Chapter-2: Technical Specification for Transformer and Reactor Page II-18 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0088 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | Transformer Oil | TESTING | The transformer/reactor shall be provided with a dial type thermometer of about 150mm diameter for top oil temperature indication with angular sweep of 270°. Range of temperature should be 0-150°C with accuracy of ±1.5% (or better) of full scale deflection. The instruments should be capable of withstanding high voltage of 2.5kV AC rms, 50Hz for 1 minute. The terminal provided for auxiliary wiring should be Press-fit type. The thermometer shall have adjustable, potential free alarm and trip contacts besides that required for control of cooling equipment (if any), maximum reading pointer and resetting device, switch testing knob & anti-vibration mounting grommets (for projection mounting). Type of switch (NO/NC) shall be heavy duty micro switch of 5A at 240V AC/DC. Adjustable range shall be 20-90% of full scale range. The instruments case should be weather proof with epoxy coating at all sides. | The transformer/reactor shall be provided with a dial type thermometer of about 150mm diameter for top oil temperature indication with angular sweep of 270°. Range of temperature should be 0-150°C with accuracy of ±1.5% (or better) of full scale deflection. The instruments should be capable of withstanding high voltage of 2.5kV AC rms, 50Hz for 1 minute. The terminal provided for auxiliary wiring should be Press-fit type. The thermometer shall have adjustable, potential free alarm and trip contacts besides that required for control of cooling equipment (if any), maximum reading pointer and resetting device, switch testing knob & anti-vibration mounting grommets (for projection mounting). Type of switch (NO/NC) shall be heavy duty micro switch of 5A at 240V AC/DC. Adjustable range shall be 20-90% of full scale range. The instruments case should be weather proof with epoxy coating at all sides. | NOT VERIFIED | 150mm; 0-150°C; 2.5kV; 50Hz; 1 minute; 5A; 240V | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 45 | Chapter-2: Technical Specification for Transformer and Reactor Page II-18 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0089 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Instruments should meet degree of protection of IP55 as per IS/IEC- 60529. A temperature sensing bulb located in a thermometer pocket on tank cover should be provided to sense top oil. This shall be connected to the OTI instrument by means of flexible stainless steel armour to protect capillary tubing. Temperature indicator dials shall have linear gradations to clearly read at least every 2 deg C. The setting of alarm and tripping contacts shall be adjustable at site. The OTI shall be so mounted that the dials are about 1200 mm from ground level. Glazed door of suitable size shall be provided for convenience of reading. | NOT COVERED | NOT VERIFIED | 1200 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 46 | Chapter-2: Technical Specification for Transformer and Reactor Page II-19 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0090 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | In addition to the above, the following accessories shall be provided for remote indication of oil temperature: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 46 | Chapter-2: Technical Specification for Transformer and Reactor Page II-19 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0091 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | The transformer/reactor shall be provided with a dial type hot spot indicator of about 150mm diameter for measuring the hot spot temperature of each winding [HV, IV & Tertiary (if applicable)]. It shall have angular sweep of 270o. Range of temperature should be 0- 150°C with accuracy of ±1.5% (or better) of full scale deflection. The instruments should be capable of withstanding high voltage of 2.5kV AC rms, 50Hz for 1 minute. The terminal provided for auxiliary wiring should be Press-fit type. The thermometer shall have adjustable, potential free alarm, trip contacts besides that required for control of cooling equipment, if any. Instrument should be provided with maximum reading pointer and resetting device, switch testing knob & anti-vibration mounting grommets (for projection mounting). Type of switch (NO/NC) shall be | The transformer/reactor shall be provided with a dial type hot spot indicator of about 150mm diameter for measuring the hot spot temperature of each winding [HV, IV & Tertiary (if applicable)]. It shall have angular sweep of 270o. Range of temperature should be 0- 150°C with accuracy of ±1.5% (or better) of full scale deflection. The instruments should be capable of withstanding high voltage of 2.5kV AC rms, 50Hz for 1 minute. The terminal provided for auxiliary wiring should be Press-fit type. The thermometer shall have adjustable, potential free alarm, trip contacts besides that required for control of cooling equipment, if any. Instrument should be provided with maximum reading pointer and resetting device, switch testing knob & anti-vibration mounting grommets (for projection mounting). Type of switch (NO/NC) shall be | NOT VERIFIED | 150mm; 0- 150°C; 2.5kV; 50Hz; 1 minute | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 46 | Chapter-2: Technical Specification for Transformer and Reactor Page II-19 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0092 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | heavy duty micro switch of 5A at 240V AC/DC. Adjustable range shall be 20-90% of full scale range. The instruments case should be weather proof and epoxy coating at all sides. Instruments should meet degree of protection of IP55 as per IEC60529. A temperature sensing bulb located in a thermometer pocket on tank cover should be provided to sense top oil. This shall be connected to the WTI instrument by means of flexible stainless steel armour to protect capillary tubing. WTI shall have image coil and auxiliary CTs, if required to match the image coil mounted in local control box. The setting of alarm and tripping contacts shall be adjustable at site. The WTI shall be so mounted that the dials are about 1200 mm from ground level. Glazed door of suitable size shall be provided for convenience of reading. | NOT COVERED | NOT VERIFIED | 5A; 240V; 1200 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 47 | Chapter-2: Technical Specification for Transformer and Reactor Page II-20 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0093 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | 11.12.1 Two (2) earthing pads (each complete with two (2) nos. holes, M16 bolts, plain and spring washers) suitable for connection to 75 x 12 mm galvanised steel grounding flat shall be provided each at position close to earth of the two (2) diagonally opposite bottom corners of the tank. | NOT COVERED | NOT VERIFIED | 12 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 47 | Chapter-2: Technical Specification for Transformer and Reactor Page II-20 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0094 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | DGA | SAFETY | 11.12.2 Two earthing terminals suitable for connection to 75 x 12 mm galvanised steel flat shall also be provided on each cooler, individual/common marshalling box and any other equipment mounted separately. For the tank-mounted equipment like online drying/Online DGA/Optical Sensor Box etc., (if provided), double earthing shall be provided through the tank for which provision shall be made through tank and connected through two flexible insulated copper link. 11.12.3 Equipotential flexible copper links of suitable size shall be provided between turret & tank, between tank & cover or between Bell & lower tank. Other components like - pipes, conservator support etc. connected to tank may also be provided with equipotential flexible copper link. 11.12.4 Each transformer/reactor unit should have provision for earthing and connection to grounding mat when not in service. 11.13 Core | NOT COVERED | NOT VERIFIED | 12 mm | 11.12.2 Two earthing terminals suitable for connection to 75 x 12 mm galvanised steel flat shall also be provided on each cooler, individual/common marshalling box and any other equipment mounted separately. For the tank-mounted equipment like online drying/Online DGA/Optical Sensor Box etc., (if provided), double earthing shall be provided through the tank for which provision shall be made through tank and connected through two flexible insulated copper link. 11.12.3 Equipotential flexible copper links of suitable size shall be provided between turret & tank, between tank & cover or between Bell & lower tank. Other components like - pipes, conservator support etc. connected to tank may also be provided with equipotential flexible copper link. 11.12.4 Each transformer/reactor unit should have provision for earthing and connection to grounding mat when not in service. 11.13 Core | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 48 | Chapter-2: Technical Specification for Transformer and Reactor Page II-21 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0095 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Installation | INSTALLATION | 11.13.2 The design of the magnetic circuit shall be such as to avoid static discharges, development of short circuit paths within itself or to the earthed clamping structure and production of flux component at right angles to the plane of laminations which may cause local heating. The step-lap construction arrangement is preferred for better performance in respect of noise, no-load current and no-load loss. 11.13.3 The hot spot temperature and surface temperatures in the core shall be calculated for over voltage conditions specified in the document and it shall not exceed 125 deg C and 120 deg C respectively. 11.13.4 Core and winding shall be capable of withstanding the shock during transport, installation and service. Adequate provision shall be made to prevent movement of core and winding relative to tank during these conditions. 11.13.5 All steel sections used for supporting the core shall be thoroughly sand/ shot blasted after cutting, drilling and welding. | 11.13.2 The design of the magnetic circuit shall be such as to avoid static discharges, development of short circuit paths within itself or to the earthed clamping structure and production of flux component at right angles to the plane of laminations which may cause local heating. The step-lap construction arrangement is preferred for better performance in respect of noise, no-load current and no-load loss. 11.13.3 The hot spot temperature and surface temperatures in the core shall be calculated for over voltage conditions specified in the document and it shall not exceed 125 deg C and 120 deg C respectively. 11.13.4 Core and winding shall be capable of withstanding the shock during transport, installation and service. Adequate provision shall be made to prevent movement of core and winding relative to tank during these conditions. 11.13.5 All steel sections used for supporting the core shall be thoroughly sand/ shot blasted after cutting, drilling and welding. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 48 | Chapter-2: Technical Specification for Transformer and Reactor Page II-21 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0096 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 11.13.6 Each core lamination shall be insulated with a material that will not deteriorate due to pressure and hot oil. 11.13.7 The supporting frame work of the core shall be so designed as to avoid presence of pockets which would prevent complete emptying of tank through drain valve or cause trapping of air during oil filling. 11.13.8 Adequate lifting lugs shall be provided to enable lifting of active part (core & winding). 11.13.9 Core assembly shall be manufactured in such a way that lamination shall remain flat and finally assembled core shall be free from distortion. 11.13.10 Single point core earthing should be ensured to avoid circulating | 11.13.6 Each core lamination shall be insulated with a material that will not deteriorate due to pressure and hot oil. 11.13.7 The supporting frame work of the core shall be so designed as to avoid presence of pockets which would prevent complete emptying of tank through drain valve or cause trapping of air during oil filling. 11.13.8 Adequate lifting lugs shall be provided to enable lifting of active part (core & winding). 11.13.9 Core assembly shall be manufactured in such a way that lamination shall remain flat and finally assembled core shall be free from distortion. 11.13.10 Single point core earthing should be ensured to avoid circulating | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 49 | Chapter-2: Technical Specification for Transformer and Reactor Page II-22 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0097 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Earthing | SAFETY | current. Core earth should be brought separately on the top of the tank to facilitate testing after installation on all transformers. The removable links shall have adequate section to carry ground fault current. Separate identification name plate/labels shall be provided for the ‘Core’ and ‘Core clamp’. Cross section of Core earthing connection shall be of minimum size 80 sq.mm copper with exception of the connections inserted between laminations which may be reduced to a cross- sectional area of 20 sq. mm tinned copper where they are clamped between the laminations. 11.13.11 In case core laminations are divided into sections by insulating barriers | NOT COVERED | NOT VERIFIED | NOT VERIFIED | current. Core earth should be brought separately on the top of the tank to facilitate testing after installation on all transformers. The removable links shall have adequate section to carry ground fault current. Separate identification name plate/labels shall be provided for the ‘Core’ and ‘Core clamp’. Cross section of Core earthing connection shall be of minimum size 80 sq.mm copper with exception of the connections inserted between laminations which may be reduced to a cross- sectional area of 20 sq. mm tinned copper where they are clamped between the laminations. 11.13.11 In case core laminations are divided into sections by insulating barriers | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 49 | Chapter-2: Technical Specification for Transformer and Reactor Page II-22 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0098 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | or cooling ducts parallel to the plane of the lamination, tinned copper bridging strips shall be inserted to maintain electrical continuity between sections. 11.13.12 Insulation of core to clamp/frame shall be tested at 2.5 kV DC for | NOT COVERED | NOT VERIFIED | 2.5 kV | or cooling ducts parallel to the plane of the lamination, tinned copper bridging strips shall be inserted to maintain electrical continuity between sections. 11.13.12 Insulation of core to clamp/frame shall be tested at 2.5 kV DC for | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 49 | Chapter-2: Technical Specification for Transformer and Reactor Page II-22 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0099 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Insulation Resistance | FAILURE_ANALYSIS | 1 minute without breakdown after the transformer is filled with liquid and insulation resistance should be at least 1 giga ohm for new transformer. 11.13.13 In addition to above following additional provisions for reactors | NOT COVERED | NOT VERIFIED | 1 minute | NOT COVERED | 1 minute without breakdown after the transformer is filled with liquid and insulation resistance should be at least 1 giga ohm for new transformer. 11.13.13 In addition to above following additional provisions for reactors | Transformers and reactors, 66 kV and above voltage class | PDF p. 49 | Chapter-2: Technical Specification for Transformer and Reactor Page II-22 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0100 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | maximum temperatures that will occur in the magnetic circuit and for the full expected life. Vacuum impregnation is preferred. The contractor shall present data on the characteristics of the packets at the time of design review. c) Material with high temperature withstand capability such as ceramic/ slate spacers shall be used to separate the packets. High temperature, mechanically stable material shall be used between the end packets and the top and bottom yokes. Special care shall be taken not to impede the cooling in these areas. d) Means shall be provided to distribute the flux from the “cheeses” and the windings to the top and bottom yokes to prevent concentrations of flux with resulting high temperatures in the yokes. e) The yokes shall be designed such that high temperatures resulting from unequal distribution of the flux in the yokes will not occur. | maximum temperatures that will occur in the magnetic circuit and for the full expected life. Vacuum impregnation is preferred. The contractor shall present data on the characteristics of the packets at the time of design review. c) Material with high temperature withstand capability such as ceramic/ slate spacers shall be used to separate the packets. High temperature, mechanically stable material shall be used between the end packets and the top and bottom yokes. Special care shall be taken not to impede the cooling in these areas. d) Means shall be provided to distribute the flux from the “cheeses” and the windings to the top and bottom yokes to prevent concentrations of flux with resulting high temperatures in the yokes. e) The yokes shall be designed such that high temperatures resulting from unequal distribution of the flux in the yokes will not occur. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 50 | Chapter-2: Technical Specification for Transformer and Reactor Page II-23 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0101 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | f) The spaces between “cheeses” will be designed so that high temperatures will not result due to fringing of flux at the oil gaps between them. The designer shall calculate the temperatures resulting from fringing. g) The structural design shall be made so that pressure will be maintained to prevent loosening resulting from thermal expansion and contraction during all loading cycles. h) The design shall be made in such a way that excessive vibration does not occur in the windings, structural supports of the windings and magnetic circuit and this will be subjected to design review. i) The structure shall be designed to withstand the clamping and magnetic forces. The calculated magnetic forces will be furnished at the time of design review. | f) The spaces between “cheeses” will be designed so that high temperatures will not result due to fringing of flux at the oil gaps between them. The designer shall calculate the temperatures resulting from fringing. g) The structural design shall be made so that pressure will be maintained to prevent loosening resulting from thermal expansion and contraction during all loading cycles. h) The design shall be made in such a way that excessive vibration does not occur in the windings, structural supports of the windings and magnetic circuit and this will be subjected to design review. i) The structure shall be designed to withstand the clamping and magnetic forces. The calculated magnetic forces will be furnished at the time of design review. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 50 | Chapter-2: Technical Specification for Transformer and Reactor Page II-23 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0102 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Epoxy bonded Continuously Transposed Conductor (CTC) shall be used in main winding for rated current of 400 A or more. 11.14.3 The conductor shall be transposed at sufficient intervals in order to minimize eddy currents and to equalise the distribution of currents and temperature along the winding. 11.14.4 The conductor insulation shall be made from high-density (at least 0.75 gm/cc) paper having high mechanical strength. The characteristics for the paper will be reviewed at the time of design review. 11.14.5 The insulation of transformer windings and connections shall be free from insulating compounds which are liable to soften, ooze out, shrink or collapse and shall be non-catalytic and chemically inactive in transformer oil during service. 11.14.6 Coil assembly and insulating spacers shall be so arranged as to ensure free circulation of oil and to reduce the hot spot of the winding. | NOT COVERED | NOT VERIFIED | 400 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 51 | Chapter-2: Technical Specification for Transformer and Reactor Page II-24 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0103 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | 11.14.7 The coils would be made up, shaped and braced to provide for expansion and contraction due to temperature changes. 11.14.8 The windings shall be designed to withstand the dielectric tests specified. The type of winding used shall be of time tested. An analysis shall be made of the transient voltage distribution in the windings, and the clearances used to withstand the various voltages. Margins shall be used in recognition of manufacturing tolerances and considering the fact that the system will not always be in the new factory condition. 11.14.9 The barrier insulation including spacers shall be made from high- density pre-compressed pressboard (1.15 gm/cc minimum for load bearing and 0.95 gm/cc minimum for non-load bearing) to minimize dimensional changes. Kraft insulating paper used on conductor should have density of >0.75 g/cc. | 11.14.7 The coils would be made up, shaped and braced to provide for expansion and contraction due to temperature changes. 11.14.8 The windings shall be designed to withstand the dielectric tests specified. The type of winding used shall be of time tested. An analysis shall be made of the transient voltage distribution in the windings, and the clearances used to withstand the various voltages. Margins shall be used in recognition of manufacturing tolerances and considering the fact that the system will not always be in the new factory condition. 11.14.9 The barrier insulation including spacers shall be made from high- density pre-compressed pressboard (1.15 gm/cc minimum for load bearing and 0.95 gm/cc minimum for non-load bearing) to minimize dimensional changes. Kraft insulating paper used on conductor should have density of >0.75 g/cc. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 51 | Chapter-2: Technical Specification for Transformer and Reactor Page II-24 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0104 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | 11.16.1 Winding termination interfaces with bushings shall be designed to allow for repeatable and safe connection under site conditions to ensure the integrity of the transformer/reactor in service. 11.16.2 The winding end termination, insulation system and transport fixings shall be so designed that the integrity of the insulation system generally remains intact during repeated work in this area. 11.16.3 Allowances shall be made on the winding ends for accommodating tolerances on the axial dimensions of the set of bushings and also for the fact that bushings may have to be rotated to get oil level inspection gauges to face in a direction for ease of inspection from ground level. | 11.16.1 Winding termination interfaces with bushings shall be designed to allow for repeatable and safe connection under site conditions to ensure the integrity of the transformer/reactor in service. 11.16.2 The winding end termination, insulation system and transport fixings shall be so designed that the integrity of the insulation system generally remains intact during repeated work in this area. 11.16.3 Allowances shall be made on the winding ends for accommodating tolerances on the axial dimensions of the set of bushings and also for the fact that bushings may have to be rotated to get oil level inspection gauges to face in a direction for ease of inspection from ground level. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 52 | Chapter-2: Technical Specification for Transformer and Reactor Page II-25 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0105 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | 11.16.4 In particular, rotation or straining of insulated connections shall be avoided during the fastening of conductor pads (or other methods) on the winding ends onto the termination surfaces of the bushing. 11.16.5 Suitable inspection and access facilities into the tank in the bushing oil-end area shall be provided to minimize the possibility of creating faults during the installation of bushings. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 11.16.4 In particular, rotation or straining of insulated connections shall be avoided during the fastening of conductor pads (or other methods) on the winding ends onto the termination surfaces of the bushing. 11.16.5 Suitable inspection and access facilities into the tank in the bushing oil-end area shall be provided to minimize the possibility of creating faults during the installation of bushings. | Transformers and reactors, 66 kV and above voltage class | PDF p. 53 | Chapter-2: Technical Specification for Transformer and Reactor Page II-26 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0106 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The typical painting details for transformer/reactor main tank, pipes, conservator tank, radiator, control cabinet/ marshalling box / oil storage tank etc. shall be as given in Annexure–K. The proposed paint system shall generally be similar or better than this. The quality of paint should be such that its colour does not fade during drying process and shall be able to withstand temperature up to 120 deg C. The detailed painting procedure shall be finalized during award of the contract. | The typical painting details for transformer/reactor main tank, pipes, conservator tank, radiator, control cabinet/ marshalling box / oil storage tank etc. shall be as given in Annexure–K. The proposed paint system shall generally be similar or better than this. The quality of paint should be such that its colour does not fade during drying process and shall be able to withstand temperature up to 120 deg C. The detailed painting procedure shall be finalized during award of the contract. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 53 | Chapter-2: Technical Specification for Transformer and Reactor Page II-26 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0107 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Transformer Oil | TESTING | 13.0 INSULATING OIL The insulating oil shall be unused inhibited (Type A, High Grade) (should be preferred) or uninhibited Transformer Oil conforming to IEC-60396-2020 & all parameters specified at Annexure–L, while tested at oil supplier's premises. The contractor shall furnish test certificates from the supplier against the acceptance norms as mentioned at Annexure–L, prior to despatch of oil from refinery to site. Under no circumstances, poor quality oil shall be filled into the transformer and thereafter be brought up to the specified parameter by circulation within the transformer. The Unused Insulating Oil parameters including parameters of oil used at manufacturer’s works, processed oil, oil after filtration and settling are attached at Annexure– L. The oil test results shall form part of equipment test report. | 13.0 INSULATING OIL The insulating oil shall be unused inhibited (Type A, High Grade) (should be preferred) or uninhibited Transformer Oil conforming to IEC-60396-2020 & all parameters specified at Annexure–L, while tested at oil supplier's premises. The contractor shall furnish test certificates from the supplier against the acceptance norms as mentioned at Annexure–L, prior to despatch of oil from refinery to site. Under no circumstances, poor quality oil shall be filled into the transformer and thereafter be brought up to the specified parameter by circulation within the transformer. The Unused Insulating Oil parameters including parameters of oil used at manufacturer’s works, processed oil, oil after filtration and settling are attached at Annexure– L. The oil test results shall form part of equipment test report. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 53 | Chapter-2: Technical Specification for Transformer and Reactor Page II-26 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0108 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | A minimum of 5% of the oil quantity shall be supplied as spare (in addition to first filling) for maintaining required oil level in case of leakage in tank, radiators, conservator etc. Oil used for first filling, testing and impregnation of active parts at manufacturer's works shall be of same type of oil which shall be supplied at site and shall meet parameters as per specification. | A minimum of 5% of the oil quantity shall be supplied as spare (in addition to first filling) for maintaining required oil level in case of leakage in tank, radiators, conservator etc. Oil used for first filling, testing and impregnation of active parts at manufacturer's works shall be of same type of oil which shall be supplied at site and shall meet parameters as per specification. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 53 | Chapter-2: Technical Specification for Transformer and Reactor Page II-26 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0109 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Corrective Action | Transformer Oil | CORRECTIVE_ACTION | The particle analysis shall be carried out in an oil sample taken before carrying out FAT at manufacturer’s works and after completion of the oil filtration at site. The procedure and interpretation shall be in accordance with the recommendation of CIGRE report WG-12.17- “Effect of particles on transformer dielectric strength”. Particle limit as shown below shall be ensured by manufacturer, implying low contamination, as per CIGRE Brochure 157, Table 8. After filtration the oil is to be flushed and particle count to be measured. Limiting value for the particle count are 1000 particle/100 ml with size ≥ 5 μm; 130 particle/100 ml with size ≥ 15 μm. | NOT COVERED | NOT VERIFIED | 100 ml | NOT COVERED | The particle analysis shall be carried out in an oil sample taken before carrying out FAT at manufacturer’s works and after completion of the oil filtration at site. The procedure and interpretation shall be in accordance with the recommendation of CIGRE report WG-12.17- “Effect of particles on transformer dielectric strength”. Particle limit as shown below shall be ensured by manufacturer, implying low contamination, as per CIGRE Brochure 157, Table 8. After filtration the oil is to be flushed and particle count to be measured. Limiting value for the particle count are 1000 particle/100 ml with size ≥ 5 μm; 130 particle/100 ml with size ≥ 15 μm. | Transformers and reactors, 66 kV and above voltage class | PDF p. 54 | Chapter-2: Technical Specification for Transformer and Reactor Page II-27 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0110 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | OIP: Oil Impregnated Paper (with porcelain/polymer housing); RIP: Resin Impregnated Paper (with polymer housing); RIS: Resin Impregnated Synthetic (with polymer housing) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 55 | Chapter-2: Technical Specification for Transformer and Reactor Page II-28 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0111 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing, Substation | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 15.2 Bushings shall be robust and designed for adequate cantilever strength to meet the requirement of seismic condition, substation layout and movement along with the spare transformer/reactor with bushing erected and provided with proper support from one foundation to another foundation within the substation area. The electrical and mechanical characteristics of bushings shall be in accordance with IS/IEC: 60137. All details of the bushing shall be submitted for approval and design review. 15.3 Oil filled condenser type bushing shall be provided with at least following fittings: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 55 | Chapter-2: Technical Specification for Transformer and Reactor Page II-28 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0112 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING | a) Oil level gauge b) Tap for capacitance and tan delta test. Test taps relying on pressure | a) Oil level gauge b) Tap for capacitance and tan delta test. Test taps relying on pressure | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 55 | Chapter-2: Technical Specification for Transformer and Reactor Page II-28 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0113 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | contacts against the outer earth layer of the bushing is not acceptable c) Oil filling plug & drain valve (if not hermetically sealed) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 55 | Chapter-2: Technical Specification for Transformer and Reactor Page II-28 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0114 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Testing | Tan Delta | TESTING | 15.4 Porcelain used in bushing manufacture shall be homogenous, free from lamination, cavities and other flaws or imperfections that might affect the mechanical or dielectric quality and shall be thoroughly vitrified, tough and impervious to moisture. 15.5 Bushing shall be provided with tap for capacitance and tan delta test. Test taps relying on pressure contacts against the outer earth layer of the bushing is not acceptable. 15.6 Where current transformers are specified, the bushings shall be removable without disturbing the current transformers. 15.7 Bushings of identical rating of different makes shall be interchangeable to optimise the requirement of spares. The standard dimensions for lower portion of the condenser bushings shall be as indicated in Annexure-M. 15.8 Polymer insulator shall be seamless sheath of a silicone rubber compound. | 15.4 Porcelain used in bushing manufacture shall be homogenous, free from lamination, cavities and other flaws or imperfections that might affect the mechanical or dielectric quality and shall be thoroughly vitrified, tough and impervious to moisture. 15.5 Bushing shall be provided with tap for capacitance and tan delta test. Test taps relying on pressure contacts against the outer earth layer of the bushing is not acceptable. 15.6 Where current transformers are specified, the bushings shall be removable without disturbing the current transformers. 15.7 Bushings of identical rating of different makes shall be interchangeable to optimise the requirement of spares. The standard dimensions for lower portion of the condenser bushings shall be as indicated in Annexure-M. 15.8 Polymer insulator shall be seamless sheath of a silicone rubber compound. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 55 | Chapter-2: Technical Specification for Transformer and Reactor Page II-28 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0115 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | The housing & weather sheds should have silicon content of minimum 30% by weight. It should protect the bushing against environmental influences, external pollution and humidity. The interface between the housing and the core must be uniform and without voids. The strength of the bond shall be greater than the tearing strength of the polymer. The manufacturer shall follow non-destructive | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 55 | Chapter-2: Technical Specification for Transformer and Reactor Page II-28 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0116 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | technique (N.D.T.) to check the quality of jointing of the housing interface with the core. The technique being followed with detailed procedure and sampling shall be finalized during finalization of MQP. The weather sheds of the insulators shall be of alternate shed profile as per IS 16683-3/IEC 60815-3. The weather sheds shall be vulcanized to the sheath (extrusion process) or moulded as part of the sheath (injection moulding process) and free from imperfections. The vulcanization for extrusion process shall be at high temperature and for injection moulding shall be at high temperature & high pressure. Any seams/ burrs protruding axially along the insulator, resulting from the injection moulding process shall be removed completely without causing any damage to the housing. The track resistance of housing and shed material shall be class 1A4.5 according to IS 9947. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 56 | Chapter-2: Technical Specification for Transformer and Reactor Page II-29 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0117 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | The strength of the weather shed to sheath interface shall be greater than the tearing strength of the polymer. The polymer insulator shall be capable of high pressure washing. 15.9 End fittings shall be free from cracks, seams, shrinks, air holes and rough edges. End fittings should be effectively, sealed to prevent moisture ingress, effectiveness of sealing system must be supported by test documents. All surfaces of the metal parts shall be perfectly smooth with the projecting points or irregularities which may cause corona. All load bearing surfaces shall be smooth and uniform so as to distribute the loading stresses uniformly. 15.10 The hollow silicone composite insulators shall comply with the requirements of IEC-61462 and the relevant parts of IEC-62217. The design of the composite insulators shall be tested and verified according to IEC-61462 (Type & Routine test). | The strength of the weather shed to sheath interface shall be greater than the tearing strength of the polymer. The polymer insulator shall be capable of high pressure washing. 15.9 End fittings shall be free from cracks, seams, shrinks, air holes and rough edges. End fittings should be effectively, sealed to prevent moisture ingress, effectiveness of sealing system must be supported by test documents. All surfaces of the metal parts shall be perfectly smooth with the projecting points or irregularities which may cause corona. All load bearing surfaces shall be smooth and uniform so as to distribute the loading stresses uniformly. 15.10 The hollow silicone composite insulators shall comply with the requirements of IEC-61462 and the relevant parts of IEC-62217. The design of the composite insulators shall be tested and verified according to IEC-61462 (Type & Routine test). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 56 | Chapter-2: Technical Specification for Transformer and Reactor Page II-29 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0118 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | 15.11 Clamps and fittings shall be of hot dip galvanised/stainless steel. 15.12 Bushing turrets shall be provided with vent pipes, to route any gas collection through the Buchholz relay. 15.13 No arcing horns shall be provided on the bushings. 15.14 Corona shield, wherever required, shall be provided at bushing terminal (air end) to minimize corona. 15.15 Bushing shall be specially packed to avoid any damage during transit and suitable for long storage, with non-returnable packing wooden boxes with hinged type cover. Without any gap between wooden planks. Packing Box opening cover with nails/screws type packing arrangement shall not be acceptable. Manufacturer shall submit | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 56 | Chapter-2: Technical Specification for Transformer and Reactor Page II-29 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0119 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | drawing/ documents of packing for approval during detail engineering. Detail method for storage of bushing including accessories shall be brought out in the instruction manual. 15.16 Oil end portion of RIP/RIS type bushings shall be fitted with metal housing with positive dry air pressure and a suitable pressure monitoring device shall be fitted on the metal housing during storage to avoid direct contact with moisture with epoxy. The pressure of dry air need to be maintained in case of leakage. 15.17 The terminal marking and their physical position shall be as per IS 2026. | drawing/ documents of packing for approval during detail engineering. Detail method for storage of bushing including accessories shall be brought out in the instruction manual. 15.16 Oil end portion of RIP/RIS type bushings shall be fitted with metal housing with positive dry air pressure and a suitable pressure monitoring device shall be fitted on the metal housing during storage to avoid direct contact with moisture with epoxy. The pressure of dry air need to be maintained in case of leakage. 15.17 The terminal marking and their physical position shall be as per IS 2026. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 57 | Chapter-2: Technical Specification for Transformer and Reactor Page II-30 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0120 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Maintenance Schedule | Tan Delta | SCHEDULE | 15.18 Tan delta measurement at variable frequency (in the range of 20 Hz to 350 Hz) shall be carried out on each condenser type bushing (OIP & RIP/ RIS) at Transformer manufacturing works as routine test before despatch and the result shall be compared at site during commissioning to verify the healthiness of the bushing. 15.19 Tan δ value of OIP/RIP/RIS condenser bushing shall be 0.005 (max.) in the temperature range of 10°C to 40°C. If tan delta is measured at a temperature beyond above mentioned limit, necessary correction factor as per IEEE shall be applicable. 16.0 LAYOUT ARRANGEMENT AND CONNECTION OF GENERATOR TRANSFORMER IN HYDRO POWER PLANTS: | NOT COVERED | NOT VERIFIED | 20 Hz; 350 Hz; 10°C; 40°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 57 | Chapter-2: Technical Specification for Transformer and Reactor Page II-30 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0121 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS, AIS | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Hydro Power Stations are remotely located in hills where space is always a constraint. Many power stations are underground and generator transformers are placed in underground caverns. The GTs installed in hydropower stations may deviate from standardized layout/architecture due to specific layout and space constraints faced in hydropower station. For standardized layout of GTs at hydropower stations, tentative typical layout and dimensions of generator transformers used in hydropower station have been shown at Annexure–Q. In Hydropower stations, connections of HV side of transformers with cable/ GIS/AIS can be either Oil to SF6 (in case of GIS), Oil to Oil (in case of XLPE cables) or Oil to Air (in case of AIS). HV terminations must have provision to accommodate these interfacings. These interfacing should be as per the provisions of relevant international standards (e.g. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 57 | Chapter-2: Technical Specification for Transformer and Reactor Page II-30 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0122 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | IEC 62271-211 for direct connection of transformer to GIS or EN 50299 for specification of cable box of transformers and reactors). 16.1 Cable Box (if applicable): | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 58 | Chapter-2: Technical Specification for Transformer and Reactor Page II-31 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0123 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Oil filled Cable box shall be designed to match with requirement of the corresponding generator transformer and for ease of access and termination of the cables by the installer. The manufacturer of the cable box shall take into account the total dynamic forces generated during short circuit. The cable box as well as bushings shall be capable of withstanding vacuum during evacuation process. The design of cable box shall be in accordance with EN-50299 and the limit/ scope of supply of cable manufacturer and the transformer manufacturer shall also be in line with EN-50299. The electrical clearances as per prevalent Standards shall be maintained inside the cable box. Transformer manufacturer shall coordinate with the cable manufacturer to resolve any interfacing issues. | Oil filled Cable box shall be designed to match with requirement of the corresponding generator transformer and for ease of access and termination of the cables by the installer. The manufacturer of the cable box shall take into account the total dynamic forces generated during short circuit. The cable box as well as bushings shall be capable of withstanding vacuum during evacuation process. The design of cable box shall be in accordance with EN-50299 and the limit/ scope of supply of cable manufacturer and the transformer manufacturer shall also be in line with EN-50299. The electrical clearances as per prevalent Standards shall be maintained inside the cable box. Transformer manufacturer shall coordinate with the cable manufacturer to resolve any interfacing issues. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 58 | Chapter-2: Technical Specification for Transformer and Reactor Page II-31 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0124 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS, Bushing | Power Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | To avoid any interfacing problem at site, the fitting of dummy cable termination and cable box needs to be checked, preferably at transformer manufacturer’s premise/works. The detailed scope of supply of transformer manufacturer and cable manufacturer as per EN-50299 has been shown at Annexure-Q. 16.2 Transformer – Connection to GIS: Transformer connection enclosure shall be part of gas insulated metal enclosed switchgear and shall house one end of a completely immersed bushing fitted on a power transformer and main circuit end terminal of GIS. The transformer connection with GIS shall be designed in line with IEC 62271-211 and the limit/scope of supply of switchgear manufacturer and the transformer manufacturer shall also be in line with above IEC. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 58 | Chapter-2: Technical Specification for Transformer and Reactor Page II-31 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0125 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS, Bushing | NOT VERIFIED | Installation | Bushing | INSTALLATION | The switchgear manufacturer shall supply connection between the enclosures of different phases as per requirement to limit the circulating current in the transformer tanks. The manufacturer of the connection enclosure shall take into account the total dynamic forces generated during short circuit and the enclosure as well as bushings shall be capable of withstanding vacuum during evacuation process. The Gas Insulated Switchgear manufacturer shall make necessary arrangement to limit the Very Fast Transient (VFT) ground potential rise which may occur during switching operation of disconnectors. The detailed scope of transformer manufacturer and GIS manufacturer as per IEC 62271-211 has been shown at Annexure-Q. | The switchgear manufacturer shall supply connection between the enclosures of different phases as per requirement to limit the circulating current in the transformer tanks. The manufacturer of the connection enclosure shall take into account the total dynamic forces generated during short circuit and the enclosure as well as bushings shall be capable of withstanding vacuum during evacuation process. The Gas Insulated Switchgear manufacturer shall make necessary arrangement to limit the Very Fast Transient (VFT) ground potential rise which may occur during switching operation of disconnectors. The detailed scope of transformer manufacturer and GIS manufacturer as per IEC 62271-211 has been shown at Annexure-Q. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 58 | Chapter-2: Technical Specification for Transformer and Reactor Page II-31 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0126 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Surge Arrester, Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | The neutral of the transformer/reactor shall be brought out through bushing. The neutral of the shunt reactor shall be grounded either directly or through a neutral grounding reactor (NGR) as the case may be. The neutral terminal of transformer/ reactor/NGR shall be brought to the ground level by a brass/tinned copper grounding bar, supported from the tank by using porcelain insulators. The end of the brass/tinned copper bar shall be brought to a convenient location at the bottom of the tank, for making connection (using bimetallic strip of adequate size) to grounding mat through separate earth pits using two (2) numbers 75 x 12 mm galvanised steel flats. Aluminium clamps & connectors of suitable size shall be provided for connection with neutral of the transformer/ reactor, surge arrester and the neutral grounding reactor (NGR). | NOT COVERED | NOT VERIFIED | 12 mm | The neutral of the transformer/reactor shall be brought out through bushing. The neutral of the shunt reactor shall be grounded either directly or through a neutral grounding reactor (NGR) as the case may be. The neutral terminal of transformer/ reactor/NGR shall be brought to the ground level by a brass/tinned copper grounding bar, supported from the tank by using porcelain insulators. The end of the brass/tinned copper bar shall be brought to a convenient location at the bottom of the tank, for making connection (using bimetallic strip of adequate size) to grounding mat through separate earth pits using two (2) numbers 75 x 12 mm galvanised steel flats. Aluminium clamps & connectors of suitable size shall be provided for connection with neutral of the transformer/ reactor, surge arrester and the neutral grounding reactor (NGR). | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 59 | Chapter-2: Technical Specification for Transformer and Reactor Page II-32 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0127 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing, Fire Protection | NOT VERIFIED | Safety | Bushing | SAFETY | The neutral terminals of the single phase transformer/reactor unit shall be brought out through bushing and necessary interconnection have to be made to form 3-phase bank and common neutral bus. The neutrals of 1-phase transformers/reactors can be connected by overhead connection using common brass/tinned copper/Aluminum pipe/ACSR conductor grounding bus, supported on the tank and fire walls by using porcelain insulators. The flexible jumper (wherever required) shall be of twin conductor. The neutral formation shall be such that neutral terminal of single-phase spare unit can be disconnected from or connected with the other single phase units in case of failure/outage of any units. The end of the neutral bus shall be connected to grounding mat through separate earth pits. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The neutral terminals of the single phase transformer/reactor unit shall be brought out through bushing and necessary interconnection have to be made to form 3-phase bank and common neutral bus. The neutrals of 1-phase transformers/reactors can be connected by overhead connection using common brass/tinned copper/Aluminum pipe/ACSR conductor grounding bus, supported on the tank and fire walls by using porcelain insulators. The flexible jumper (wherever required) shall be of twin conductor. The neutral formation shall be such that neutral terminal of single-phase spare unit can be disconnected from or connected with the other single phase units in case of failure/outage of any units. The end of the neutral bus shall be connected to grounding mat through separate earth pits. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 59 | Chapter-2: Technical Specification for Transformer and Reactor Page II-32 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0128 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Typical arrangements for neutral formation has been indicated in Annexure-O. 18.0 DELTA FORMATION (applicable for 1-Phase Transformer): The tertiary winding terminals of the transformer shall be brought out through bushing. The delta formation of tertiary winding of single phase units of a three phase bank shall be done outside the transformer. IPS Aluminium tube of suitable size (e.g. 3” IPS) with heat shrinkable insulating sleeves or cables of suitable voltage class, bus post insulators, support structures, conductors, clamps & connectors of suitable size required for tertiary delta formation shall be provided. The insulation tape or sleeve (wherever used) shall be of at least 52kV class for 33kV tertiary bus. The minimum phase to phase horizontal | NOT COVERED | NOT VERIFIED | 52kV; 33kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 59 | Chapter-2: Technical Specification for Transformer and Reactor Page II-32 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0129 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | Auto Transformer | Safety | Bushing | SAFETY | spacing for delta formation shall be 1.5 meter. Metal sheathed cables shall be avoided for delta formation. More details are given in Annexure-N Delta Formation in case of single phase Generator Transformer: The LV winding of Generator Transformers shall be brought out through bushing and LV side of single phase transformers shall be connected in delta using different configuration of Bus Duct, depending on the rated current of LV winding to form three phase bank. The Transformer and Bus duct manufacturer shall co-ordinate with each other for formation of delta on Low voltage side of Generator Transformer maintaining required spacing between phases and safety clearances. 19.0 COOLING EQUIPMENT AND ITS CONTROL 19.1 Radiator based cooling for Power/Auto transformer & Reactor | NOT COVERED | NOT VERIFIED | NOT VERIFIED | spacing for delta formation shall be 1.5 meter. Metal sheathed cables shall be avoided for delta formation. More details are given in Annexure-N Delta Formation in case of single phase Generator Transformer: The LV winding of Generator Transformers shall be brought out through bushing and LV side of single phase transformers shall be connected in delta using different configuration of Bus Duct, depending on the rated current of LV winding to form three phase bank. The Transformer and Bus duct manufacturer shall co-ordinate with each other for formation of delta on Low voltage side of Generator Transformer maintaining required spacing between phases and safety clearances. 19.0 COOLING EQUIPMENT AND ITS CONTROL 19.1 Radiator based cooling for Power/Auto transformer & Reactor | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 60 | Chapter-2: Technical Specification for Transformer and Reactor Page II-33 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0130 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (a) Cooling Fans, Oil Pumps, Oil Flow Indicator (as applicable) (b) Top and bottom shut off valve of at least 80mm size (c) Drain Valve and sampling valve (d) Top and bottom oil filling valves (e) Air release plug at top (f) Two grounding terminals suitable for termination of two (2) Nos. 75x12 mm galvanised steel flats. (g) Thermometer pockets fitted with captive screw caps at cooler inlet and outlet. | NOT COVERED | NOT VERIFIED | 80mm; 2 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 60 | Chapter-2: Technical Specification for Transformer and Reactor Page II-33 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0131 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | 19.1.7 Two (2) nos., 100% centrifugal or axial in line oil pumps, if applicable, (out of which one pump shall be standby) shall be provided with each radiator bank. Measures shall be taken to prevent mal- operation of Buchholz relay when all oil pumps are simultaneously put into service. The pump shall be so designed that upon failure of power supply to the pump motor, the pump impeller will not limit the natural circulation of oil. 19.1.8 The changeover to standby oil pump in case of failure of service oil pump shall be automatic. 19.1.9 An oil flow indicator shall be provided for the confirmation of the oil flow direction. An indication in the flow indicator and potential free contacts for remote alarm shall be provided. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 19.1.7 Two (2) nos., 100% centrifugal or axial in line oil pumps, if applicable, (out of which one pump shall be standby) shall be provided with each radiator bank. Measures shall be taken to prevent mal- operation of Buchholz relay when all oil pumps are simultaneously put into service. The pump shall be so designed that upon failure of power supply to the pump motor, the pump impeller will not limit the natural circulation of oil. 19.1.8 The changeover to standby oil pump in case of failure of service oil pump shall be automatic. 19.1.9 An oil flow indicator shall be provided for the confirmation of the oil flow direction. An indication in the flow indicator and potential free contacts for remote alarm shall be provided. | Transformers and reactors, 66 kV and above voltage class | PDF p. 61 | Chapter-2: Technical Specification for Transformer and Reactor Page II-34 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0132 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | 19.1.10 Valves shall be provided across the pump and oil flow indicator to avoid oil drain and long outage during maintenance / replacement of pump and oil flow indicator. 19.1.11 Cooling fans and oil pump motors shall be suitable for operation from 415 volts, three phase 50 Hz power supply and shall be of premium efficiency class IE3 conforming to IS: 12615. Each cooling fan and oil pump motors shall be provided with starter, thermal overload and short circuit protection. The motor winding insulation shall be conventional class 'B' type. Motors shall have hose proof enclosure equivalent to IP: 55 as per IS/IEC 60034-5. | 19.1.10 Valves shall be provided across the pump and oil flow indicator to avoid oil drain and long outage during maintenance / replacement of pump and oil flow indicator. 19.1.11 Cooling fans and oil pump motors shall be suitable for operation from 415 volts, three phase 50 Hz power supply and shall be of premium efficiency class IE3 conforming to IS: 12615. Each cooling fan and oil pump motors shall be provided with starter, thermal overload and short circuit protection. The motor winding insulation shall be conventional class 'B' type. Motors shall have hose proof enclosure equivalent to IP: 55 as per IS/IEC 60034-5. | NOT VERIFIED | 50 Hz | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 61 | Chapter-2: Technical Specification for Transformer and Reactor Page II-34 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0133 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Corrective Action | Transformer Oil | CORRECTIVE_ACTION | 19.1.12 The cooler pipes, support structure including radiators and its accessories shall be hot dip galvanised or corrosion resistant paint should be applied to external surface of it. 19.1.13 Air release device and oil plug shall be provided on oil pipe connections. Drain valves shall be provided in order that each section of pipe work can be drained independently. 19.1.14 Automatic operation control of fans/pumps shall be provided (with temperature change) from contacts of winding temperature indicator. The manufacturer shall recommend the setting of WTI for automatic changeover of cooler control over entire operating range depending on types of cooling system like ONAN/ONAF/OFAF (or ODAF) or ONAN/ONAF1/ONAF2. The setting shall be such that hunting i.e. frequent start-up operations for small temperature differential do not occur. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 19.1.12 The cooler pipes, support structure including radiators and its accessories shall be hot dip galvanised or corrosion resistant paint should be applied to external surface of it. 19.1.13 Air release device and oil plug shall be provided on oil pipe connections. Drain valves shall be provided in order that each section of pipe work can be drained independently. 19.1.14 Automatic operation control of fans/pumps shall be provided (with temperature change) from contacts of winding temperature indicator. The manufacturer shall recommend the setting of WTI for automatic changeover of cooler control over entire operating range depending on types of cooling system like ONAN/ONAF/OFAF (or ODAF) or ONAN/ONAF1/ONAF2. The setting shall be such that hunting i.e. frequent start-up operations for small temperature differential do not occur. | Transformers and reactors, 66 kV and above voltage class | PDF p. 62 | Chapter-2: Technical Specification for Transformer and Reactor Page II-35 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0134 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 19.1.15 Suitable manual control facility for cooler fans and oil pumps shall be provided. Selector switches and push buttons shall also be provided in the cooler control cabinet to disconnect the automatic control and start/stop the fans and pump manually. 19.1.16 Following lamp indications shall be provided in cooler control cabinet: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 62 | Chapter-2: Technical Specification for Transformer and Reactor Page II-35 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0135 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | a) Cooler Supply failure (main) b) Cooler supply changeover c) Cooler Supply failure (standby) d) Control Supply failure e) Cooling fan supply failure for each bank f) Cooling pump supply failure for each pump g) Common thermal overload trip h) Thermal overload trip for each fan/pump i) No oil flow/reverse flow for pumps j) Stand by fan/pump ON One potential free initiating contact for all the above conditions shall be wired independently to the terminal blocks of cooler control cabinet and for single phase unit connection shall be extended further to Common Marshalling Box. 19.1.17 The Cooler Control Cabinet/ Individual Marshalling Box shall have all necessary devices meant for cooler control and local temperature indicators. All the contacts of various protective devices mounted on the transformer and all the secondary terminals of the bushing CTs shall also be wired up to the terminal board in the Cooler Control Cabinet/Individual Marshalling Box. All the CT secondary terminals in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | a) Cooler Supply failure (main) b) Cooler supply changeover c) Cooler Supply failure (standby) d) Control Supply failure e) Cooling fan supply failure for each bank f) Cooling pump supply failure for each pump g) Common thermal overload trip h) Thermal overload trip for each fan/pump i) No oil flow/reverse flow for pumps j) Stand by fan/pump ON One potential free initiating contact for all the above conditions shall be wired independently to the terminal blocks of cooler control cabinet and for single phase unit connection shall be extended further to Common Marshalling Box. 19.1.17 The Cooler Control Cabinet/ Individual Marshalling Box shall have all necessary devices meant for cooler control and local temperature indicators. All the contacts of various protective devices mounted on the transformer and all the secondary terminals of the bushing CTs shall also be wired up to the terminal board in the Cooler Control Cabinet/Individual Marshalling Box. All the CT secondary terminals in | Transformers and reactors, 66 kV and above voltage class | PDF p. 62 | Chapter-2: Technical Specification for Transformer and Reactor Page II-35 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0136 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 19.2.2 Total capacity of unit coolers furnished for each transformer shall be minimum 120% of actual requirements. 19.2.3 For generator transformer in thermal plants cooling shall be affected by use of minimum six (6) nos. of tank mounted detachable type unit coolers. Capacity of each unit cooler shall be limited to maximum of 20% of the total cooling requirements. The coolers shall be tank mounted. The orientation of coolers shall be subject to Purchaser’s approval. 19.2.4 Each Unit Cooler shall have its own cooling fans, oil pumps, oil flow indicator, shut off valves of at least 80 mm size at the top and bottom, lifting lugs, top and bottom oil filling valves, air release plug at the top, a drain and sampling valve and thermometer pocket fitted with captive screw cap on the inlet and outlet. | 19.2.2 Total capacity of unit coolers furnished for each transformer shall be minimum 120% of actual requirements. 19.2.3 For generator transformer in thermal plants cooling shall be affected by use of minimum six (6) nos. of tank mounted detachable type unit coolers. Capacity of each unit cooler shall be limited to maximum of 20% of the total cooling requirements. The coolers shall be tank mounted. The orientation of coolers shall be subject to Purchaser’s approval. 19.2.4 Each Unit Cooler shall have its own cooling fans, oil pumps, oil flow indicator, shut off valves of at least 80 mm size at the top and bottom, lifting lugs, top and bottom oil filling valves, air release plug at the top, a drain and sampling valve and thermometer pocket fitted with captive screw cap on the inlet and outlet. | NOT VERIFIED | 80 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 63 | Chapter-2: Technical Specification for Transformer and Reactor Page II-36 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0137 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | 19.2.5 A magnetic type oil flow indicator shall be provided for the confirmation of the oil pump operating in a normal state. An indication shall be provided in the flow indicator to indicate reverse flow of oil/loss of oil flow. 19.2.6 Valves shall be provided across the pump and oil flow indicator to avoid oil drain and long outage during maintenance / replacement of pump and oil flow indicator. | 19.2.5 A magnetic type oil flow indicator shall be provided for the confirmation of the oil pump operating in a normal state. An indication shall be provided in the flow indicator to indicate reverse flow of oil/loss of oil flow. 19.2.6 Valves shall be provided across the pump and oil flow indicator to avoid oil drain and long outage during maintenance / replacement of pump and oil flow indicator. | NOT VERIFIED | 2.5 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 63 | Chapter-2: Technical Specification for Transformer and Reactor Page II-36 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0138 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 19.2.7 Cooling fans and oil pump motors shall be suitable for operation from 415 volts, three phase 50 Hz power supply and shall be of premium efficiency class IE3 conforming to IS: 12615. Each cooling fan and oil pump motors shall be provided with starter, thermal overload and short circuit protection. The motor winding insulation shall be conventional class 'B' or better type. Motors shall have hose proof enclosure equivalent to IP:55 as per IS:IEC:60034-5. The temperature rise of the motor shall be limited to 70 deg. C above ambient of 50 deg. & shall comply with IS:12615. 19.2.8 The cooler, pipes, support structure and its accessories shall be hot dip galvanised or corrosion resistant paint should be applied to external surface of it. 19.2.9 Expansion joint shall be provided on top and bottom cooler pipe connections as per requirement. | NOT COVERED | NOT VERIFIED | 50 Hz | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 64 | Chapter-2: Technical Specification for Transformer and Reactor Page II-37 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0139 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | 19.2.10 Air release device and oil plug shall be provided on oil pipe connections. Drain valves shall be provided in order that each section of pipe work can be drained independently. 19.2.11 Suitable manual control facility for unit cooler shall be provided. 19.2.12 The changeover to standby unit cooler bank oil pump in case of failure of any service unit cooler shall be automatic. 19.2.13 Selector switches and push buttons shall also be provided in the cooler control cabinet to disconnect the automatic control and start/stop the unit cooler manually. 19.2.14 Cooler fans & oil pumps of all unit coolers (except standby cooler) shall operate continuously. The starting of unit cooler shall be done as soon the Circuit Breaker of HV/IV/LV (as applicable) side is switched on. Provision shall be kept to start the coolers by WTI contact. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 19.2.10 Air release device and oil plug shall be provided on oil pipe connections. Drain valves shall be provided in order that each section of pipe work can be drained independently. 19.2.11 Suitable manual control facility for unit cooler shall be provided. 19.2.12 The changeover to standby unit cooler bank oil pump in case of failure of any service unit cooler shall be automatic. 19.2.13 Selector switches and push buttons shall also be provided in the cooler control cabinet to disconnect the automatic control and start/stop the unit cooler manually. 19.2.14 Cooler fans & oil pumps of all unit coolers (except standby cooler) shall operate continuously. The starting of unit cooler shall be done as soon the Circuit Breaker of HV/IV/LV (as applicable) side is switched on. Provision shall be kept to start the coolers by WTI contact. | Transformers and reactors, 66 kV and above voltage class | PDF p. 64 | Chapter-2: Technical Specification for Transformer and Reactor Page II-37 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0140 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | General | SAFETY | 19.2.15 Once started the cooling shall remain in operation as long as the transformer is in service. When the transformer is switched off the cooling shall continue to run for a further duration of 30 minutes. This timer shall be at least adjustable from 15 to 60 minutes. Further, a one-week timer is required to check the healthiness of the complete cooling system on a routine basis for one hour at a time. Spurious operation should however be avoided by appropriate settings. All settings shall be adjustable 19.2.16 Adequate warning/ safety labels are required to indicate that the fans may start at any time. | NOT COVERED | NOT VERIFIED | 30 minutes; 60 minutes | 19.2.15 Once started the cooling shall remain in operation as long as the transformer is in service. When the transformer is switched off the cooling shall continue to run for a further duration of 30 minutes. This timer shall be at least adjustable from 15 to 60 minutes. Further, a one-week timer is required to check the healthiness of the complete cooling system on a routine basis for one hour at a time. Spurious operation should however be avoided by appropriate settings. All settings shall be adjustable 19.2.16 Adequate warning/ safety labels are required to indicate that the fans may start at any time. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 64 | Chapter-2: Technical Specification for Transformer and Reactor Page II-37 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0141 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | a) Cooler Supply failure (main) b) Cooler supply changeover c) Cooler Supply failure (standby) d) Control Supply failure e) Cooler unit failure for each unit cooler f) No oil flow/reverse oil flow for pumps g) Thermal overload trip for each fan / pump | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | a) Cooler Supply failure (main) b) Cooler supply changeover c) Cooler Supply failure (standby) d) Control Supply failure e) Cooler unit failure for each unit cooler f) No oil flow/reverse oil flow for pumps g) Thermal overload trip for each fan / pump | Transformers and reactors, 66 kV and above voltage class | PDF p. 65 | Chapter-2: Technical Specification for Transformer and Reactor Page II-38 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0142 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY | One potential free initiating contact for all the above conditions shall be wired independently to the terminal blocks of cooler control cabinet and for single ph. unit connection shall be extended further to CMB. 19.3 Transformer Cooling System for Generator Transformers in Hydro Plants: 19.3.1 Each transformer shall be equipped with a water/oil cooling system mounted on transformer tank complete with heat exchanger, oil circulating pump, motor and associated control gear, pipes, valves, flow indicators etc. designed to be connected to the common cooling water system. Two complete sets of cooling units each of 100% capacity (one shall be standby), both with 20% margin with necessary pipe- fittings and valves shall be furnished with each transformer. Cooler tube shall be made of Cu-Ni (90-10%). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | One potential free initiating contact for all the above conditions shall be wired independently to the terminal blocks of cooler control cabinet and for single ph. unit connection shall be extended further to CMB. 19.3 Transformer Cooling System for Generator Transformers in Hydro Plants: 19.3.1 Each transformer shall be equipped with a water/oil cooling system mounted on transformer tank complete with heat exchanger, oil circulating pump, motor and associated control gear, pipes, valves, flow indicators etc. designed to be connected to the common cooling water system. Two complete sets of cooling units each of 100% capacity (one shall be standby), both with 20% margin with necessary pipe- fittings and valves shall be furnished with each transformer. Cooler tube shall be made of Cu-Ni (90-10%). | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 65 | Chapter-2: Technical Specification for Transformer and Reactor Page II-38 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0143 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | Double wall type cooler tubes shall be used so that in case of leakage of tube, water is not mixed with oil, and instead get collected in a container. The container shall be equipped with a drain valve and a leakage detector relay. Alarms shall be provided for leakage from the first layer of tube, so that defect is immediately attended. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Double wall type cooler tubes shall be used so that in case of leakage of tube, water is not mixed with oil, and instead get collected in a container. The container shall be equipped with a drain valve and a leakage detector relay. Alarms shall be provided for leakage from the first layer of tube, so that defect is immediately attended. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 65 | Chapter-2: Technical Specification for Transformer and Reactor Page II-38 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0144 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | 19.3.2 Heat exchangers shall be designed for pressure and vacuum conditions specified for the tank and also keeping in view their relative location with respect to tank. 19.3.3 Cooler units shall be connected to the tank by machined steel flanges welded to the cooler units and to the tank provided with gaskets. Inlet and outlet of each cooler connection to tank shall be provided with indicating shut-off valves, which can be locked in either open or closed | 19.3.2 Heat exchangers shall be designed for pressure and vacuum conditions specified for the tank and also keeping in view their relative location with respect to tank. 19.3.3 Cooler units shall be connected to the tank by machined steel flanges welded to the cooler units and to the tank provided with gaskets. Inlet and outlet of each cooler connection to tank shall be provided with indicating shut-off valves, which can be locked in either open or closed | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 65 | Chapter-2: Technical Specification for Transformer and Reactor Page II-38 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0145 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | position. A separate oil tight blank flange shall be provided for each tank connection for use when cooler unit is detached. 19.3.4 A magnetic type oil flow indicator with alarm and trip contacts for outflow of oil from pump shall be provided with each assembly to indicate normal operation and direction of oil flow. Valves shall be provided at the outlet of each cooler for regulating the flow of water. Motorised valves shall be provided on the water inlet side of each cooler so as to ensure automatic changeover of coolers. The outlet of each pump shall be interconnected, using necessary isolating valves, to ensure cross operation of coolers 19.3.5 In addition, necessary instrumentation like pressure gauge, flow indication and isolation valve, non-return valves etc. and following shall be provided with coolers: | NOT COVERED | NOT VERIFIED | 3.4 A | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 66 | Chapter-2: Technical Specification for Transformer and Reactor Page II-39 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0146 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | a) Glycerine filled pressure gauges at oil and water inlet and outlet branches. b) A suitable differential pressure gauge or equivalent suitable device fitted with electrical contacts to give an alarm in case of choking of coolers. c) Suitable thermometers screwed into pockets for outlet & inlet oil and water branches of coolers. d) Each pump shall be provided with a non-return valve on delivery side. e) A water flow indicator with alarm and one potential free contact shall be installed in the discharge pipe of the heat exchanger. Necessary valves for replacement/maintenance of faulty components. 19.3.6 The necessary piping, fittings, all type of valves shall be provided for connecting each transformer to the cooler and oil pumps. The oil piping shall be provided with machined flanged joints. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | a) Glycerine filled pressure gauges at oil and water inlet and outlet branches. b) A suitable differential pressure gauge or equivalent suitable device fitted with electrical contacts to give an alarm in case of choking of coolers. c) Suitable thermometers screwed into pockets for outlet & inlet oil and water branches of coolers. d) Each pump shall be provided with a non-return valve on delivery side. e) A water flow indicator with alarm and one potential free contact shall be installed in the discharge pipe of the heat exchanger. Necessary valves for replacement/maintenance of faulty components. 19.3.6 The necessary piping, fittings, all type of valves shall be provided for connecting each transformer to the cooler and oil pumps. The oil piping shall be provided with machined flanged joints. | Transformers and reactors, 66 kV and above voltage class | PDF p. 66 | Chapter-2: Technical Specification for Transformer and Reactor Page II-39 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0147 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Drain valves/plugs shall be provided in order that each section of the pipe work can be drained independently. 19.3.7 Control equipment for oil circulating pump and motor to be mounted in a marshalling box to be supplied with each transformer shall include the necessary contactors with auto motor control. Provision for automatic/manual control equipment will be made in accordance with the following: a) Locally from the control cabinet through operation of local control switch. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 66 | Chapter-2: Technical Specification for Transformer and Reactor Page II-39 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0148 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | b) From remote UCB/centralized control room after selecting the remote operation from local panel. c) Automatically through the auxiliary contact of starting relay. For this purpose, the selector switch shall be put on auto and the cooler shall start working when the starting relay is energized. d) Changeover of cooler and pump from main to standby shall be achieved via control system logic (based on running period). e) Change over in the event of any pump or heat exchanger not functioning. f) Oil pumps shall stop minimum one hour after stoppage of unit. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 67 | Chapter-2: Technical Specification for Transformer and Reactor Page II-40 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0149 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 19.3.8 Auxiliary contacts shall be provided to indicate the running of all the pumps. Overload and single-phase protection of all motors shall be provided. Transformer manufacturer shall specify the loading capacity of the transformers in case of lesser quantity or pressure of cooling water. Sufficient number of contacts for annunciation and alarms/trips for oil pump running status, pump running hour status, pump overload status, flow status and water leakage in coolers shall be provided on the initiating relay/device for indication/annunciation on respective marshalling box and SCADA. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 67 | Chapter-2: Technical Specification for Transformer and Reactor Page II-40 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0150 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 20.3 Suitable means shall be provided for locking the valves in the open and close positions. Provision is not required for locking individual radiator valves. 20.4 Each valve shall be provided with the indicator to show clearly the position (open/close) of the valve. 20.5 Gland packing/gasket material shall be of “O” ring of nitrile rubber for all the valve’s flanges. All the flanges shall be machined. 20.6 Drain valves/plugs shall be provided in order that each section of pipe work can be drained independently. 20.7 All valves in oil line shall be suitable for continuous operation with transformer oil at 115 deg C. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 68 | Chapter-2: Technical Specification for Transformer and Reactor Page II-41 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0151 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | 20.8 After testing, inside surface of all cast iron valves coming in contact with oil shall be applied with one coat of oil resisting paint/varnish with two coats of red oxide zinc chromate primer followed by two coats of fully glossy finishing paint conforming to IS: 2932 and of a shade (Preferably red or yellow) distinct and different from that of main tank surface. Outside surface except gasket setting surface of butterfly valves shall be painted with two coats of red oxide zinc chromate conforming to IS: 2074 followed by two coats of fully glossy finishing paint. 20.9 The oil sampling point for main tank shall have two identical valves put in series. Oil sampling valve shall have provision to fix rubber hose of 10 mm size to facilitate oil sampling. 20.10 Valves or other suitable means shall be provided to fix various on line condition monitoring systems, if specified, to facilitate continuous monitoring. The location & size of the same shall be finalised during detail design review. 20.11 All hardware used shall be hot dip galvanised/stainless steel. | 20.8 After testing, inside surface of all cast iron valves coming in contact with oil shall be applied with one coat of oil resisting paint/varnish with two coats of red oxide zinc chromate primer followed by two coats of fully glossy finishing paint conforming to IS: 2932 and of a shade (Preferably red or yellow) distinct and different from that of main tank surface. Outside surface except gasket setting surface of butterfly valves shall be painted with two coats of red oxide zinc chromate conforming to IS: 2074 followed by two coats of fully glossy finishing paint. 20.9 The oil sampling point for main tank shall have two identical valves put in series. Oil sampling valve shall have provision to fix rubber hose of 10 mm size to facilitate oil sampling. 20.10 Valves or other suitable means shall be provided to fix various on line condition monitoring systems, if specified, to facilitate continuous monitoring. The location & size of the same shall be finalised during detail design review. 20.11 All hardware used shall be hot dip galvanised/stainless steel. | NOT VERIFIED | 10 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 69 | Chapter-2: Technical Specification for Transformer and Reactor Page II-42 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0152 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | transformer/reactor, flow sensitive valve shall be provided to isolate the conservator oil from the main tank. The valve shall be flow sensitive and shut off when the flow in the pipe is more than the flow expected in the permissible normal operating conditions. It shall not operate when oil pumps are switched on or off. This valve shall be located in the piping between the conservator and the buchholz relay and shall not affect the flow of oil from and to the conservator in normal conditions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 69 | Chapter-2: Technical Specification for Transformer and Reactor Page II-42 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0153 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | normal operating conditions, the valve shall shut off by itself and will have to be reset manually. It shall be provided with valve open/close position indicator along with alarm contact indication in control room during closing operation of valve. This valve shall be provided with locking arrangement for normal position and oil filling / filtration position. A suitable platform or ladder (if required) shall be provided to approach the valve for manual reset. | normal operating conditions, the valve shall shut off by itself and will have to be reset manually. It shall be provided with valve open/close position indicator along with alarm contact indication in control room during closing operation of valve. This valve shall be provided with locking arrangement for normal position and oil filling / filtration position. A suitable platform or ladder (if required) shall be provided to approach the valve for manual reset. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 69 | Chapter-2: Technical Specification for Transformer and Reactor Page II-42 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0154 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | 21.0 CABLING 21.1 All interconnecting control and power cables emanating from various parts of transformer/reactor like turret CT, MBs, Fans, pumps, Buchholz, PRD etc. shall be routed through covered cable tray or GI conduit and shall be properly dressed. All cables shall be armoured type. Un-armoured cables (if provided) in any circuitry, shall be through GI conduit and no part shall be exposed. Cable terminations shall be through stud type TB and ring type lugs. Type tested cables from approved sources shall be provided. Both ends of all the wires (control & power) shall be provided with proper ferrule numbers for tracing and maintenance. Further, any special cables (if required) shall also be considered included in the scope. All cable accessories such as glands, lugs, cable tags/ numbers etc. as required shall be considered included in the scope of supply. Typical technical specification for cables is attached at Annexure-R. The cross section of “control cable” shall be 1.5 sq.mm (minimum) except for CT circuits which should be 2.5 sq.mm (minimum). | 21.0 CABLING 21.1 All interconnecting control and power cables emanating from various parts of transformer/reactor like turret CT, MBs, Fans, pumps, Buchholz, PRD etc. shall be routed through covered cable tray or GI conduit and shall be properly dressed. All cables shall be armoured type. Un-armoured cables (if provided) in any circuitry, shall be through GI conduit and no part shall be exposed. Cable terminations shall be through stud type TB and ring type lugs. Type tested cables from approved sources shall be provided. Both ends of all the wires (control & power) shall be provided with proper ferrule numbers for tracing and maintenance. Further, any special cables (if required) shall also be considered included in the scope. All cable accessories such as glands, lugs, cable tags/ numbers etc. as required shall be considered included in the scope of supply. Typical technical specification for cables is attached at Annexure-R. The cross section of “control cable” shall be 1.5 sq.mm (minimum) except for CT circuits which should be 2.5 sq.mm (minimum). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 70 | Chapter-2: Technical Specification for Transformer and Reactor Page II-43 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0155 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 21.2 Cabling of spare unit of transformer/reactor with isolator switching arrangement shall be in such a way that spare unit can be brought into service in case of failure/ outage of a healthy unit without physically shifting. All control, protection, indication signals of spare unit shall be brought to the Common Marshalling Box (CMB) of all the banks. From CMB all the control, protection and indication signals of R, Y, B and Spare units shall be transferred to Purchaser’s Control panels/SCADA. Change-over of spare unit signals with faulty unit shall be done through Purchaser’s C & R panels / SCADA level. Changeover of RTCC signals shall be carried out in CMB. Plug & socket arrangement shall be provided for quicker transition of faulty unit to spare unit to avoid interconnection errors. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 21.2 Cabling of spare unit of transformer/reactor with isolator switching arrangement shall be in such a way that spare unit can be brought into service in case of failure/ outage of a healthy unit without physically shifting. All control, protection, indication signals of spare unit shall be brought to the Common Marshalling Box (CMB) of all the banks. From CMB all the control, protection and indication signals of R, Y, B and Spare units shall be transferred to Purchaser’s Control panels/SCADA. Change-over of spare unit signals with faulty unit shall be done through Purchaser’s C & R panels / SCADA level. Changeover of RTCC signals shall be carried out in CMB. Plug & socket arrangement shall be provided for quicker transition of faulty unit to spare unit to avoid interconnection errors. | Transformers and reactors, 66 kV and above voltage class | PDF p. 70 | Chapter-2: Technical Specification for Transformer and Reactor Page II-43 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0156 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Tan Delta | TESTING | 22.1.4 Measurement of Tan Delta values of OCTC to be done before installing in the transformer. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 71 | Chapter-2: Technical Specification for Transformer and Reactor Page II-44 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0157 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.1.1 Single/ three phase transformer as specified in Annexure-A shall be provided with voltage control equipment of the tap changing type for varying its effective transformation ratio whilst the transformers are on load. The OLTC shall conform to IS 8468/IEC 60214 (Part 1& 2). The requirement of voltage regulation (on HV or LV sides), location (physical and electrical) of tap winding (end of common/ series winding or at neutral end), range of voltage variation, no. of steps etc. shall be as given in Annexure-A. 22.2.1.2 The OLTC shall be of high speed transition resistor type. OLTC shall be motor operated suitable for local as well as remote operation. The diverter switch or arcing switch shall be designed so as to ensure that its operation once commenced shall be completed independently of the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 71 | Chapter-2: Technical Specification for Transformer and Reactor Page II-44 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0158 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | control relays or switches, failure of auxiliary supplies etc. To meet any contingency which may result in incomplete operation of the diverter switch, adequate means shall be provided to safeguard the transformer and its ancillary equipment. The current diverting contacts shall be housed in a separate oil chamber not communicating with the oil in main tank of the transformer and the chamber shall be designed to withstand the vacuum. The contacts shall be accessible for inspection without lowering oil level in the main tank and the contacts shall be replaceable. 22.2.1.3 The voltage class, maximum tapping current, step voltage of OLTC shall have adequate design margin for safe & reliable service life of both OLTC and transformer. OLTC shall have long contact life, quick & easy to disassemble diverter switch inserts, simple to adjust & control and easy to replace diverter’s contacts etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | control relays or switches, failure of auxiliary supplies etc. To meet any contingency which may result in incomplete operation of the diverter switch, adequate means shall be provided to safeguard the transformer and its ancillary equipment. The current diverting contacts shall be housed in a separate oil chamber not communicating with the oil in main tank of the transformer and the chamber shall be designed to withstand the vacuum. The contacts shall be accessible for inspection without lowering oil level in the main tank and the contacts shall be replaceable. 22.2.1.3 The voltage class, maximum tapping current, step voltage of OLTC shall have adequate design margin for safe & reliable service life of both OLTC and transformer. OLTC shall have long contact life, quick & easy to disassemble diverter switch inserts, simple to adjust & control and easy to replace diverter’s contacts etc. | Transformers and reactors, 66 kV and above voltage class | PDF p. 72 | Chapter-2: Technical Specification for Transformer and Reactor Page II-45 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0159 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 22.2.1.4 Necessary safeguards shall be provided to avoid harmful arcing at the current diverting contacts in the event of operation of the OLTC gear under overload conditions of the transformer. 22.2.1.5 The OLTC oil chamber shall have oil filling and drain valve, oil sampling valve, relief vent and level glass. Oil sampling valve, accessible from ground, shall be provided to take sample of oil from the OLTC chamber. It shall also be fitted with an oil surge relay which shall be connected between OLTC oil chamber and OLTC conservator tank. Provision of a suitable device like tie-in-resistor has to be made, wherever required, to limit the recovery voltage to a safe value. The use of tie-in-resistor (if used) shall be clearly marked in rating and diagram plate of the transformer. | 22.2.1.4 Necessary safeguards shall be provided to avoid harmful arcing at the current diverting contacts in the event of operation of the OLTC gear under overload conditions of the transformer. 22.2.1.5 The OLTC oil chamber shall have oil filling and drain valve, oil sampling valve, relief vent and level glass. Oil sampling valve, accessible from ground, shall be provided to take sample of oil from the OLTC chamber. It shall also be fitted with an oil surge relay which shall be connected between OLTC oil chamber and OLTC conservator tank. Provision of a suitable device like tie-in-resistor has to be made, wherever required, to limit the recovery voltage to a safe value. The use of tie-in-resistor (if used) shall be clearly marked in rating and diagram plate of the transformer. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 72 | Chapter-2: Technical Specification for Transformer and Reactor Page II-45 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0160 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | The whole of the driving mechanism shall be of robust design and capable of giving satisfactory service without undue maintenance. 22.2.1.6 Tap changer shall be so mounted that bell cover of transformer can be lifted without removing connections between windings and tap changer. 22.2.1.7 As an alternative to conventional OLTC with traditional diverter switch immersed in oil (where arcing takes place in oil), vacuum type OLTC (where arcing takes place in a hermetically sealed vacuum interrupter) may also be provided. However, provisions as specified above shall be followed as far as applicable. | The whole of the driving mechanism shall be of robust design and capable of giving satisfactory service without undue maintenance. 22.2.1.6 Tap changer shall be so mounted that bell cover of transformer can be lifted without removing connections between windings and tap changer. 22.2.1.7 As an alternative to conventional OLTC with traditional diverter switch immersed in oil (where arcing takes place in oil), vacuum type OLTC (where arcing takes place in a hermetically sealed vacuum interrupter) may also be provided. However, provisions as specified above shall be followed as far as applicable. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 72 | Chapter-2: Technical Specification for Transformer and Reactor Page II-45 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0161 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.2 Local OLTC Control Cabinet (Drive Mechanism Box) 22.2.2.1 OLTC shall be suitable for manual (handle operated) and electrical (motor operated) operation. For local manual operation from Local | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 72 | Chapter-2: Technical Specification for Transformer and Reactor Page II-45 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0162 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | OLTC Control cabinet (Drive Mechanism Box), an external handle shall be provided. 22.2.2.2 OLTC’s Local control cabinet shall be mounted on the tank in accessible position. The cranking device/handle for manual operation for OLTC gear shall be removable and suitable for operation by a man standing at ground level (preferably at a height less than1800mm). The mechanism shall be complete with the following: | NOT COVERED | NOT VERIFIED | 800mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 73 | Chapter-2: Technical Specification for Transformer and Reactor Page II-46 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0163 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 22.2.2.3 For electrical operation from local as well as remote, motor operated mechanism shall be provided. It shall not be possible to operate the electric drive when the manual operating gear is in use. It shall not be possible for any two controls to be in operation at the same time. Transfer of source in the event of failure of operating AC supply shall not affect the tap changer. Thermal device or other means shall be provided to protect the motor and control circuit. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 22.2.2.3 For electrical operation from local as well as remote, motor operated mechanism shall be provided. It shall not be possible to operate the electric drive when the manual operating gear is in use. It shall not be possible for any two controls to be in operation at the same time. Transfer of source in the event of failure of operating AC supply shall not affect the tap changer. Thermal device or other means shall be provided to protect the motor and control circuit. | Transformers and reactors, 66 kV and above voltage class | PDF p. 73 | Chapter-2: Technical Specification for Transformer and Reactor Page II-46 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0164 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.2.4 The Local OLTC Drive Mechanism Box shall house all necessary devices meant for OLTC control and indication. It shall be complete with the following: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 73 | Chapter-2: Technical Specification for Transformer and Reactor Page II-46 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0165 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Circuit Breaker, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | (a) A circuit breaker/contactor with thermal overload devices for controlling the AC Auxiliary supply to the OLTC motor | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 73 | Chapter-2: Technical Specification for Transformer and Reactor Page II-46 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0166 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.2.5 In case auxiliary power supply requirement for OLTC Drive Mechanism (DM) Box is different than station auxiliary AC supply, then all necessary converters shall be provided. 22.2.2.6 Operating mechanism for on load tap changer shall be designed to go through one step of tap change per command only, until the control switch is returned to the off position between successive operations/ repeat commands. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 74 | Chapter-2: Technical Specification for Transformer and Reactor Page II-47 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0167 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Safety | OLTC | SAFETY | 22.2.2.7 Limit switches shall be provided to prevent overrunning of the mechanism and shall be directly connected in the control circuit of the operating motor provided that a mechanical de-clutching mechanism is incorporated. In addition, a mechanical stop shall be provided to prevent over-running of the mechanism under any condition. An interlock to cut-out electrical control when it tends to operate the gear beyond either of the extreme tap positions. 22.2.2.8 OLTC local control cabinet shall be provided with tap position indication for the transformer. Drive Mechanism shall be equipped with a fixed resistor network capable of providing discrete voltage steps or provide 4-20mA transducer outputs for tap position indication in Common Marshalling Box (CMB) (for single phase unit) and input to digital RTCC/relevant BCU (as applicable)/SCADA system. | NOT COVERED | NOT VERIFIED | 4-20mA | 22.2.2.7 Limit switches shall be provided to prevent overrunning of the mechanism and shall be directly connected in the control circuit of the operating motor provided that a mechanical de-clutching mechanism is incorporated. In addition, a mechanical stop shall be provided to prevent over-running of the mechanism under any condition. An interlock to cut-out electrical control when it tends to operate the gear beyond either of the extreme tap positions. 22.2.2.8 OLTC local control cabinet shall be provided with tap position indication for the transformer. Drive Mechanism shall be equipped with a fixed resistor network capable of providing discrete voltage steps or provide 4-20mA transducer outputs for tap position indication in Common Marshalling Box (CMB) (for single phase unit) and input to digital RTCC/relevant BCU (as applicable)/SCADA system. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 74 | Chapter-2: Technical Specification for Transformer and Reactor Page II-47 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0168 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | The tap position indicator shall also be provided in control room. 22.2.2.9 'Local-remote' selector switch shall be provided in the local OLTC control cabinet. In Local mode, all electrical commands from remote (i.e. from CMB, digital RTCC, SCADA, SAS etc.) shall be cut- off/blocked. Electrical operations to change tap positions shall be possible by using raise/lower push buttons under local mode from Driving Mechanism (DM) Box. In remote mode electrical commands from CMB/ digital RTCC/SCADA/SAS etc. shall be executed. The remote-local selector switch shall be having at-least two spare contacts per position. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 74 | Chapter-2: Technical Specification for Transformer and Reactor Page II-47 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0169 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Safety | OLTC | SAFETY | be provided in DM box: (a) INCOMPLETE STEP (b) OLTC motor overload protection operated (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local / Remote Selector switch positions of DM (f) OLTC upper/lower limits reached (g) 415V Main AC supply ON (h) 415V Standby AC supply ON 22.2.2.11 The following minimum contacts shall be available in DM Box. For three | NOT COVERED | NOT VERIFIED | 415V | be provided in DM box: (a) INCOMPLETE STEP (b) OLTC motor overload protection operated (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local / Remote Selector switch positions of DM (f) OLTC upper/lower limits reached (g) 415V Main AC supply ON (h) 415V Standby AC supply ON 22.2.2.11 The following minimum contacts shall be available in DM Box. For three | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 75 | Chapter-2: Technical Specification for Transformer and Reactor Page II-48 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0170 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Safety | OLTC | SAFETY | (a) INCOMPLETE STEP which shall not operate for momentary loss of auxiliary power. (b) OLTC motor overload protection (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local/Remote Selector switch position (f) OLTC upper/lower limits reached 22.2.2.12 All relays, switches, fuses etc. shall be mounted in the OLTC local | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (a) INCOMPLETE STEP which shall not operate for momentary loss of auxiliary power. (b) OLTC motor overload protection (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local/Remote Selector switch position (f) OLTC upper/lower limits reached 22.2.2.12 All relays, switches, fuses etc. shall be mounted in the OLTC local | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 75 | Chapter-2: Technical Specification for Transformer and Reactor Page II-48 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0171 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | control cabinet and shall be clearly marked/ labelled for the purpose of identification. Both ends of all the wires (control & power) connected to Drive Mechanism Box must be provided with proper ferrule nos. for tracing and maintenance. 22.2.2.13 A permanently legible lubrication chart and control circuit drawing | control cabinet and shall be clearly marked/ labelled for the purpose of identification. Both ends of all the wires (control & power) connected to Drive Mechanism Box must be provided with proper ferrule nos. for tracing and maintenance. 22.2.2.13 A permanently legible lubrication chart and control circuit drawing | NOT VERIFIED | 2.13 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 75 | Chapter-2: Technical Specification for Transformer and Reactor Page II-48 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0172 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Failure / Failure Analysis | OLTC | FAILURE_ANALYSIS | shall be fitted within the OLTC local control cabinet. 22.2.3 OLTC Control from Common Marshalling Box (CMB) (For single phase transformer units) 22.2.3.1 It shall be possible to monitor, control/operate, the OLTC of all the three 1-phase transformers of a transformer bank from Common Marshalling Box (CMB). The control and monitoring terminations of a spare transformer unit (1-Ph) shall be brought to CMB. The necessary switching arrangement through male-female plug-in TB assembly shall be provided for replacing spare unit with any one of the faulty phase unit for monitoring & control from CMB. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | shall be fitted within the OLTC local control cabinet. 22.2.3 OLTC Control from Common Marshalling Box (CMB) (For single phase transformer units) 22.2.3.1 It shall be possible to monitor, control/operate, the OLTC of all the three 1-phase transformers of a transformer bank from Common Marshalling Box (CMB). The control and monitoring terminations of a spare transformer unit (1-Ph) shall be brought to CMB. The necessary switching arrangement through male-female plug-in TB assembly shall be provided for replacing spare unit with any one of the faulty phase unit for monitoring & control from CMB. | Transformers and reactors, 66 kV and above voltage class | PDF p. 75 | Chapter-2: Technical Specification for Transformer and Reactor Page II-48 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0173 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.3.2 'Independent-combined-remote selector switch, raise/lower switch and emergency stop Push Button shall be provided in the common marshalling box for OLTC control. 22.2.3.3 When the selector switch is in ‘independent’ position, the OLTC control shall be possible from individual Local OLTC Control Cabinet (DM Box) only. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 76 | Chapter-2: Technical Specification for Transformer and Reactor Page II-49 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0174 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.3.5 In 'remote’ position control of OLTC shall be possible from digital RTCC/SCADA/SAS etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 76 | Chapter-2: Technical Specification for Transformer and Reactor Page II-49 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0175 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.3.6 From CMB, the operation of OLTC shall be for 3-phases of transformer units without producing phase displacement. Independent operation of each single phase transformer from CMB/digital RTCC/SCADA/SAS will be prevented. 22.2.3.7 Following minimum LED indications shall be provided in CMB: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 76 | Chapter-2: Technical Specification for Transformer and Reactor Page II-49 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0176 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Safety | OLTC | SAFETY | (a) INCOMPLETE STEP (b) OLTC motor overload protection operated (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local / Remote Selector switch positions of DM (f) OLTC upper/lower limits reached (g) 415V Main AC supply ON (h) 415V Standby AC supply ON | NOT COVERED | NOT VERIFIED | 415V | (a) INCOMPLETE STEP (b) OLTC motor overload protection operated (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local / Remote Selector switch positions of DM (f) OLTC upper/lower limits reached (g) 415V Main AC supply ON (h) 415V Standby AC supply ON | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 76 | Chapter-2: Technical Specification for Transformer and Reactor Page II-49 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0177 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.3.8 Following contacts shall be wired to TBs in CMB for further wiring to C & R Panels: (a) 415V Main AC supply Fail (b) 415V Standby AC supply Fail 22.2.3.9 Following contacts shall be wired to TBs in CMB from DM box for further wiring to digital RTCC Panel/relevant BCU (as applicable): (a) INCOMPLETE STEP (b) OLTC motor overload protection operated (c) Supply to DM Motor fail (d) OLTC IN PROGRESS (e) Local / Remote Selector switch positions of DM | NOT COVERED | NOT VERIFIED | 415V | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 76 | Chapter-2: Technical Specification for Transformer and Reactor Page II-49 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0178 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Safety | OLTC | SAFETY | (f) OLTC upper/lower limits reached (g) 'Independent-combined-remote’ selector switch positions of CMB 22.2.3.10 Further, OLTC tap position digital indications for all three 1-Ph | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (f) OLTC upper/lower limits reached (g) 'Independent-combined-remote’ selector switch positions of CMB 22.2.3.10 Further, OLTC tap position digital indications for all three 1-Ph | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 77 | Chapter-2: Technical Specification for Transformer and Reactor Page II-50 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0179 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.4 Remote Control & Monitoring of OLTC (through Bay Control Unit/Digital RTCC Relay, as applicable) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 77 | Chapter-2: Technical Specification for Transformer and Reactor Page II-50 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0180 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Substation | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Requirement of digital RTCC relays may be specified by the utility for existing conventional substations as per its practice. For substations/ power plants having Substation Automation System, Control & monitoring of OLTC shall be carried out through Substation Automation System. All the functionalities specified for digital RTCC shall be realised in soft logic in Substation Automation System. All hardwire signals from/to OLTC shall be wired to Bay Control Units (BCUs) provided by the owner/contractor, as applicable. Wherever, digital RTCC relay is required following specification may be followed. 22.2.4.1 The digital RTCC relay shall have Automatic Tap Changer control and monitoring relay with Automatic Voltage Regulating features to remotely control and monitor OLTC. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 77 | Chapter-2: Technical Specification for Transformer and Reactor Page II-50 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0181 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | location, it could be customized to suit site conditions without sending back to works. The programming shall be menu driven and easily configurable. If it is designed with draw out type modules, it should take care of shorting all CT inputs automatically while drawing out. The CT/VT ratio shall be field programmable and Relay shall display the actual HV Voltage and current considering suitable multiplying factors. The system shall be self-sufficient and shall not require any additional devices like parallel balancing module etc. 22.2.4.6 It shall be possible to communicate/integrate with all digital RTCC relays of different make located at different locations in the substation by making hardwire and using IS/IEC 61850 communication link. The integration of existing conventional RTCC panel with digital RTCC panel of different make shall also be possible. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 78 | Chapter-2: Technical Specification for Transformer and Reactor Page II-51 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0182 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.4.7 The digital RTCC relay shall have Raise/Lower push buttons, Manual/ Automatic mode selection feature, Local/Remote selection feature, Master / Follower/ Independent/ Off mode selection feature for control of OLTC. Touch screen option in the relay (instead of electrical push button/switch) is also acceptable. 22.2.4.8 The digital RTCC Relay shall have multiple selectable set point voltages and it shall be possible to select these set points from SCADA/ SAS, with a facility to have the possibility of additional set points command from SCADA/ SAS. 22.2.4.9 In Manual Mode: In this mode, power system voltage based automatic control from digital RTCC relay shall be blocked and commands shall be executed manually by raise/lower push buttons. 22.2.4.10 In Auto Mode: In Auto mode, digital RTCC relay shall automatically | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 78 | Chapter-2: Technical Specification for Transformer and Reactor Page II-51 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0183 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | control OLTC taps based on power system voltage and voltage set points. An interlock shall be provided to cut off electrical control automatically upon recourse being taken to the manual control in emergency. 22.2.4.11 Master/Follower/Independent/Off mode | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 78 | Chapter-2: Technical Specification for Transformer and Reactor Page II-51 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0184 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Master Position: If the digital RTCC relay is in master position, it shall be possible to control the OLTC units of other parallel operating transformers in the follower mode by operation from the master unit. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0185 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Follower Position: If the digital RTCC relay is in Follower position, control of OLTC shall be possible only from panel where master mode is selected. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0186 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Independent Position: In independent position of selector switch, control of OLTC shall be possible only from the panel where independent mode is selected. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0187 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Suitable interlock arrangement shall be provided to avoid unwanted/inconsistent operation of OLTC of the transformer | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0188 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, AIS, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | provision to raise or lower taps for the complete bank of three 1-phase transformers / 3-Phase Transformers. Individual 1-phase OLTC operation shall not be possible from the remote control panel. 22.2.4.13 Digital RTCC relays shall communicate with SCADA using IS/IEC | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0189 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 61850 through fibre optic port to monitor, parameterise and control the OLTC. Any software required for this purpose shall be supplied. The supplied software shall not have restriction in loading on multiple computers for downloading and analyzing the data. Software shall indicate the current overview of all measured parameters of the connected transformer in real time. 22.2.4.14 Communication between the Digital RTCC relays to execute the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0190 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 22.2.4.16 The relays shall ensure completion of lowering/raising of the OLTC tap, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 79 | Chapter-2: Technical Specification for Transformer and Reactor Page II-52 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0191 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Safety | OLTC | SAFETY | RTCC relay either through relay display panel or through relay LEDs: (a) INCOMPLETE STEP alarm (b) OLTC motor overload protection alarm (c) Supply to DM Motor fail alarm (d) OLTC IN PROGRESS alarm (e) Local / Remote Selector switch positions in DM Box (f) OLTC upper/lower limits reached alarm (g) OLTC Tap position indications for transformer units (h) Independent-combined-remote selector switch positions of CMB (in case of single phase transformer) (i) 415V, AC Mail Supply Fail. (j) 415V, AC Standby Supply Fail | NOT COVERED | NOT VERIFIED | 415V | RTCC relay either through relay display panel or through relay LEDs: (a) INCOMPLETE STEP alarm (b) OLTC motor overload protection alarm (c) Supply to DM Motor fail alarm (d) OLTC IN PROGRESS alarm (e) Local / Remote Selector switch positions in DM Box (f) OLTC upper/lower limits reached alarm (g) OLTC Tap position indications for transformer units (h) Independent-combined-remote selector switch positions of CMB (in case of single phase transformer) (i) 415V, AC Mail Supply Fail. (j) 415V, AC Standby Supply Fail | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 80 | Chapter-2: Technical Specification for Transformer and Reactor Page II-53 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0192 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | 23.0 SCADA INTEGRATION (if applicable) All the online monitoring equipment i.e. Optical Temperature Sensors & Measuring Unit, Online Dissolved Gas (Multi-gas) and Moisture Analyzer, On-line insulating oil drying system (Cartridge type) etc. provided for individual transformer/reactor unit including spare unit (if any), shall be IS/IEC 61850 compliant (either directly or through a Gateway). These monitoring equipment are required to be integrated | 23.0 SCADA INTEGRATION (if applicable) All the online monitoring equipment i.e. Optical Temperature Sensors & Measuring Unit, Online Dissolved Gas (Multi-gas) and Moisture Analyzer, On-line insulating oil drying system (Cartridge type) etc. provided for individual transformer/reactor unit including spare unit (if any), shall be IS/IEC 61850 compliant (either directly or through a Gateway). These monitoring equipment are required to be integrated | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 80 | Chapter-2: Technical Specification for Transformer and Reactor Page II-53 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0193 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Cooling and OLTC of transformers shall also be monitored and controlled from SCADA. List of Signal exchange between Transformer and SCADA may be mutually agreed between the owner and manufacturer. Owner/contractor, as applicable, shall ensure provision of adequate number of redundant Bay control Units (BCUs). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 81 | Chapter-2: Technical Specification for Transformer and Reactor Page II-54 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0194 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 24.0 CONSTRUCTIONAL FEATURES OF COOLER CONTROL CABINET/ INDIVIDUAL MARSHALLING BOX/ COMMON MARSHALLING BOX/ OUTDOOR CUBICLE/DIGITAL RTCC PANEL 24.1 Each transformer unit shall be provided with local OCTC/OLTC Drive Mechanism Box (DMB), Cooler Control Cabinet/Individual Marshalling Box, Digital RTCC panel (as applicable) and Common Marshalling Box (for a bank of three 1-phase units). Each reactor unit shall be provided with Individual Marshalling Box and Common Marshalling Box (for a bank of three single phase unit). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 81 | Chapter-2: Technical Specification for Transformer and Reactor Page II-54 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0195 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | (except OLTC Drive Mechanism box) shall be made of stainless steel sheet of minimum Grade SS 304 and of minimum thickness of 1.6 mm. Digital RTCC panel shall be made of CRCA sheet of minimum thickness of 2.0 mm and shall be painted suitably as per Annexure– K. 24.4 The degree of protection shall be IP: 55 for outdoor and IP: 43 for indoor in accordance with IS/IEC: 60947. 24.5 All doors, removable covers and plates shall be gasketed all around with suitably profiled. All gasketed surfaces shall be smooth straight and reinforced if necessary to minimize distortion to make a tight seal. For Control cubicle/Marshalling Boxes etc. | NOT COVERED | NOT VERIFIED | 1.6 mm; 2.0 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 82 | Chapter-2: Technical Specification for Transformer and Reactor Page II-55 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0196 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Testing | Bushing | TESTING | which are outdoor type, all the sealing gaskets shall be of EPDM rubber or any other (approved) material of better quality, whereas for all indoor control cabinets/Digital RTCC panel, the sealing gaskets shall be of neoprene rubber or any other (approved) material of better quality. The gaskets shall be tested in accordance with approved quality plan and IS: 3400. 24.6 All the contacts of various protective devices mounted on the transformer/reactor and all the secondary terminals of the bushing CTs shall also be wired upto the terminal board in the Marshalling Box. All the CT secondary terminals in the Marshalling Box shall have provision for shorting to avoid CT open circuit while it is not in use. All the necessary terminations for remote connection to Purchaser’s panel shall be wired up to the Common Marshalling Box. | which are outdoor type, all the sealing gaskets shall be of EPDM rubber or any other (approved) material of better quality, whereas for all indoor control cabinets/Digital RTCC panel, the sealing gaskets shall be of neoprene rubber or any other (approved) material of better quality. The gaskets shall be tested in accordance with approved quality plan and IS: 3400. 24.6 All the contacts of various protective devices mounted on the transformer/reactor and all the secondary terminals of the bushing CTs shall also be wired upto the terminal board in the Marshalling Box. All the CT secondary terminals in the Marshalling Box shall have provision for shorting to avoid CT open circuit while it is not in use. All the necessary terminations for remote connection to Purchaser’s panel shall be wired up to the Common Marshalling Box. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 82 | Chapter-2: Technical Specification for Transformer and Reactor Page II-55 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0197 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 24.7 Ventilating Louvers, if provided, shall have screen and filters. The screen shall be fine wire mesh of brass. All the control cabinets shall be provided with suitable lifting arrangement. Thermostat controlled space heater and cubicle lighting with ON-OFF switch shall be provided in each panel. 25.0 AUXILIARY POWER SUPPLY FOR OLTC, COOLER CONTROL AND POWER CIRCUIT 25.1 For Single Phase unit | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 82 | Chapter-2: Technical Specification for Transformer and Reactor Page II-55 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0198 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | extended from nearest CMB only. Suitably rated power contactors, separate MCBs/MCCBs shall be provided in the CMB for each circuit. 25.1.2 For each circuit, suitably rated MCBs/MCCBs as required for further distribution of auxiliary power supply to Drive Mechanism (DM) boxes, Online Gases and moisture monitoring system, Online drying system and Fibre optic sensor Box etc. (as applicable), shall be provided in Individual Marshalling Boxes (IMB)/Cooler Control Cubicle(CCC). Power from CMB (through bus bar at CMB) to IMB (at bus inside) through cable shall be provided. 25.1.3 Auxiliary power supply distribution scheme shall be submitted for approval. | extended from nearest CMB only. Suitably rated power contactors, separate MCBs/MCCBs shall be provided in the CMB for each circuit. 25.1.2 For each circuit, suitably rated MCBs/MCCBs as required for further distribution of auxiliary power supply to Drive Mechanism (DM) boxes, Online Gases and moisture monitoring system, Online drying system and Fibre optic sensor Box etc. (as applicable), shall be provided in Individual Marshalling Boxes (IMB)/Cooler Control Cubicle(CCC). Power from CMB (through bus bar at CMB) to IMB (at bus inside) through cable shall be provided. 25.1.3 Auxiliary power supply distribution scheme shall be submitted for approval. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 83 | Chapter-2: Technical Specification for Transformer and Reactor Page II-56 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0199 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | Supply and laying of Power, Control and special cables from CMB to IMB/CCC (including spare unit) & further distribution from IMB/CCC to all accessories is in the scope of the manufacturer/contractor (as applicable). Further any special cable (if required) from CMB to Owner’s Control Panels is also in the scope of the manufacturer/contractor (as applicable). 25.2 For Three Phase Transformer 25.2.1 Two auxiliary power supplies of 415 volt, three phase four (4) wire shall be provided by the Purchaser at Cooler Control Cabinet / Marshalling Box. All loads shall be fed by one of the two sources through an electrically interlocked automatic transfer scheme housed in the Cooler Control Cabinet/Marshalling Box. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 83 | Chapter-2: Technical Specification for Transformer and Reactor Page II-56 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0200 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | 25.2.2 For each circuit, suitably rated power contactors, MCBs/MCCBs as required for entire auxiliary power supply distribution scheme including distribution to DM boxes, Online Gases and moisture monitoring system, Online drying system and Fibre optic sensor Box etc. (as applicable), shall be provided in cooler control cabinet/ Marshalling Box. 25.2.3 Auxiliary power supply distribution scheme shall be submitted for approval. Supply and laying of Power, Control and special cables from marshalling box to all accessories is in the scope of the manufacturer/contractor (as applicable). Further any special cable (if required) from MB to Owner’s Control Panels/Digital RTCC panels is also in the scope of the manufacturer/contractor (as applicable). 25.2.4 All relays and operating devices shall operate correctly at any voltage within the limits specified below: | 25.2.2 For each circuit, suitably rated power contactors, MCBs/MCCBs as required for entire auxiliary power supply distribution scheme including distribution to DM boxes, Online Gases and moisture monitoring system, Online drying system and Fibre optic sensor Box etc. (as applicable), shall be provided in cooler control cabinet/ Marshalling Box. 25.2.3 Auxiliary power supply distribution scheme shall be submitted for approval. Supply and laying of Power, Control and special cables from marshalling box to all accessories is in the scope of the manufacturer/contractor (as applicable). Further any special cable (if required) from MB to Owner’s Control Panels/Digital RTCC panels is also in the scope of the manufacturer/contractor (as applicable). 25.2.4 All relays and operating devices shall operate correctly at any voltage within the limits specified below: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 83 | Chapter-2: Technical Specification for Transformer and Reactor Page II-56 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0201 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Combine variation of voltage and frequency shall be limited to ±10%. 25.2.5 Design features of the transfer scheme shall include the following: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 84 | Chapter-2: Technical Specification for Transformer and Reactor Page II-57 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0202 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | other as standby. b) Upon failure of the normal source, the loads shall be automatically | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | other as standby. b) Upon failure of the normal source, the loads shall be automatically | Transformers and reactors, 66 kV and above voltage class | PDF p. 84 | Chapter-2: Technical Specification for Transformer and Reactor Page II-57 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0203 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Marshalling Box/Common Marshalling Box for failure of normal source and for transfer to standby source and also for failure to transfer. d) Automatic re-transfer to normal source without any intentional | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Marshalling Box/Common Marshalling Box for failure of normal source and for transfer to standby source and also for failure to transfer. d) Automatic re-transfer to normal source without any intentional | Transformers and reactors, 66 kV and above voltage class | PDF p. 84 | Chapter-2: Technical Specification for Transformer and Reactor Page II-57 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0204 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | DGA | INSTALLATION | AC feeders shall not be paralleled at any time. 25.2.6 For spare unit which is not connected through isolator switching arrangement, 415 volt, three phase four (4) wire AC supply shall be provided for heater, On line drying system, On line DGA etc. as applicable. | AC feeders shall not be paralleled at any time. 25.2.6 For spare unit which is not connected through isolator switching arrangement, 415 volt, three phase four (4) wire AC supply shall be provided for heater, On line drying system, On line DGA etc. as applicable. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 84 | Chapter-2: Technical Specification for Transformer and Reactor Page II-57 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0205 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | 26.0 BUSHING CURRENT TRANSFORMER AND NEUTRAL CURRENT TRANSFORMER 26.1 Current transformers shall comply with IS 16227 (Part 1 & 2)/IEC 61869 (part 1 & 2). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 84 | Chapter-2: Technical Specification for Transformer and Reactor Page II-57 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0206 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Safety | Bushing | SAFETY | precautions shall be taken to minimize eddy currents and local heat generated in the turret. 26.3 Current transformer secondary leads shall be brought out to a weather proof terminal box near each bushing. These terminals shall be wired out to common marshalling box using separate cables for each core. 26.4 For 1-phase Transformer, one number single phase current transformer (outdoor) shall be provided for each bank of transformer for earth fault protection and shall be located in the neutral conductor connecting common neutral point with earth. 26.5 Technical Parameters of Bushing CTs and Neutral CTs are provided at Annexure–B. The CTs used for REF protection must have the identical parameters in order to limit the circulating current under normal condition for stability of protection. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | precautions shall be taken to minimize eddy currents and local heat generated in the turret. 26.3 Current transformer secondary leads shall be brought out to a weather proof terminal box near each bushing. These terminals shall be wired out to common marshalling box using separate cables for each core. 26.4 For 1-phase Transformer, one number single phase current transformer (outdoor) shall be provided for each bank of transformer for earth fault protection and shall be located in the neutral conductor connecting common neutral point with earth. 26.5 Technical Parameters of Bushing CTs and Neutral CTs are provided at Annexure–B. The CTs used for REF protection must have the identical parameters in order to limit the circulating current under normal condition for stability of protection. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 85 | Chapter-2: Technical Specification for Transformer and Reactor Page II-58 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0207 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Bushing Current Transformer parameters indicated in this specification are tentative and liable to change within reasonable limits. Purchaser's approval shall be obtained before proceeding with the design of bushing current transformers. 26.6 Secondary resistance and magnetising current characteristics of PX class (protection) CT of same rating shall be similar. This is applicable for Neutral CT (outdoor) also and shall be reviewed during detail engineering. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 85 | Chapter-2: Technical Specification for Transformer and Reactor Page II-58 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0208 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | 27.0 TOOLS & TACKLES Each transformer/reactor shall be supplied with a full kit of tools & spanners of required sizes; bushing handling & lifting tools with nylon rope/belt, with a rack for holding them; required numbers of hydraulic jacks for lifting the transformers, and for changing the plane of rotation of wheels. All spanners shall be single ended and case hardened. Tirfors with wire rope and slings with grippers etc. for hauling the transformer/reactor to the plinth are to be supplied along with each transformer/reactor. Utility may add / remove tools as per their requirement. 28.0 FITTINGS & ACCESSORIES | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 27.0 TOOLS & TACKLES Each transformer/reactor shall be supplied with a full kit of tools & spanners of required sizes; bushing handling & lifting tools with nylon rope/belt, with a rack for holding them; required numbers of hydraulic jacks for lifting the transformers, and for changing the plane of rotation of wheels. All spanners shall be single ended and case hardened. Tirfors with wire rope and slings with grippers etc. for hauling the transformer/reactor to the plinth are to be supplied along with each transformer/reactor. Utility may add / remove tools as per their requirement. 28.0 FITTINGS & ACCESSORIES | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 85 | Chapter-2: Technical Specification for Transformer and Reactor Page II-58 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0209 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (a) Conservator for main tank with aircell, oil filling hole and cap, isolating valves, drain valve, magnetic oil level gauge, prismatic oil level gauge and dehydrating silica gel filter breather with flexible connection pipes to be used during replacement of any silica gel breather. (b) Conservator for OLTC (for transformer) with drain valve, oil surge relay, filling hole with cap, magnetic oil level gauge, prismatic oil level gauge and dehydrating breather (for transformer only) with flexible connection pipes to be used during replacement of any silica gel breather. (c) Pressure relief devices with special shroud to direct the hot oil (d) Sudden pressure relief relay (for 220 kV and above Transformer/Reactor) (e) Buchholz relay (double float, reed type) with isolating valves on both sides, bleeding pipe with pet cock at the end to collect gases and alarm/trip contacts. | NOT COVERED | NOT VERIFIED | 220 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 86 | Chapter-2: Technical Specification for Transformer and Reactor Page II-59 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0210 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | (f) Conservator air cell rupture detection relay (g) Air release plug (h) Inspection openings and covers (i) Bushing of each type with metal parts and gaskets to suit the termination arrangement (j) Winding & Oil temperature indicators (local & remote) (k) Cover lifting eyes, transformer/reactor lifting lugs, jacking pads, towing holes and core and winding lifting lugs (l) Protected type alcohol in glass thermometer or magnetic or micro- switch type dial type temperature indicator as applicable (mercury should not be used) (m) Rating and diagram plates (in English & Hindi or as specified by the utility) on transformers and auxiliary apparatus | (f) Conservator air cell rupture detection relay (g) Air release plug (h) Inspection openings and covers (i) Bushing of each type with metal parts and gaskets to suit the termination arrangement (j) Winding & Oil temperature indicators (local & remote) (k) Cover lifting eyes, transformer/reactor lifting lugs, jacking pads, towing holes and core and winding lifting lugs (l) Protected type alcohol in glass thermometer or magnetic or micro- switch type dial type temperature indicator as applicable (mercury should not be used) (m) Rating and diagram plates (in English & Hindi or as specified by the utility) on transformers and auxiliary apparatus | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 86 | Chapter-2: Technical Specification for Transformer and Reactor Page II-59 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0211 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | (p) On load tap changing gear, OLTC/Off Circuit Tap Changer (OCTC) DM Box, individual marshalling box/Common Marshalling Box, Cooler control cabinet, and Digital RTCC Panel as applicable | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 87 | Chapter-2: Technical Specification for Transformer and Reactor Page II-60 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0212 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Maintenance Schedule | DGA | SCHEDULE | (q) Cooling equipment including fans & pumps (as applicable) (r) Bushing current transformers, Neutral CT (if applicable) (s) Oil/water flow indicators (if applicable) (t) Terminal marking plates (u) Valves schedule plate (v) Bottom oil sampling valve, Drain valves (provided to drain each section of pipe work independently), Filter valves at top and bottom with threaded male adaptors, Shut off valves on the pipe connection between radiator bank & the main tank, Shut off valves on both sides of Buchholz relay, Sampling gas collectors for Buchholz relay at accessible height, Valves for Radiators, Valve for vacuum application, Valves for cable box (if applicable), Valve for on line DGA (if applicable), valves for Drying out system (if applicable), water inlet and outlet valves (applicable for water cooled transformers), Flow sensitive Conservator Isolation Valve (if applicable), Gate Valve (4 Nos. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 87 | Chapter-2: Technical Specification for Transformer and Reactor Page II-60 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0213 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Testing | Fire Protection | TESTING | of min. 50 NB) for UHF sensors for PD Measurements (applicable for 400kV and above voltage class Transformer only), valves for firefighting system (as applicable) and other valves as specified in the specification. | NOT COVERED | NOT VERIFIED | 400kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 87 | Chapter-2: Technical Specification for Transformer and Reactor Page II-60 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0214 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | (w) Ladder (suitably placed to avoid fouling with bushing or piping) to climb up to the transformer/reactor tank cover with suitable locking arrangement to prevent climbing during charged condition. Additional ladder for conservator in case it is not tank mounted. (x) Suitable platform for safe access of flow sensitive non-return valve and buchholz relay shall be provided, in case these are not accessible from transformer/reactor top. (y) Haulage/ lifting lugs (z) Suitable terminal connectors on bushings | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 87 | Chapter-2: Technical Specification for Transformer and Reactor Page II-60 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0215 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Earthing | SAFETY | (cc) Brass/tinned copper grounding bar supported from the tank by using porcelain insulator and flexible conductor for earthing of neutral, HV & IV terminals as per specification | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (cc) Brass/tinned copper grounding bar supported from the tank by using porcelain insulator and flexible conductor for earthing of neutral, HV & IV terminals as per specification | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 88 | Chapter-2: Technical Specification for Transformer and Reactor Page II-61 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0216 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (dd) On line insulating oil drying system (in 400 kV and above level Transformers/ Reactors) as per Annexure-U | NOT COVERED | NOT VERIFIED | 400 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 88 | Chapter-2: Technical Specification for Transformer and Reactor Page II-61 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0217 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (a) Conservator for NGR main tank with drain valve, isolating valve, vent pipe and prismatic oil level gauge | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 88 | Chapter-2: Technical Specification for Transformer and Reactor Page II-61 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0218 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, CT, Bushing | Current Transformer | Inspection | Transformer Oil | INSPECTION | (b) Pressure relief devices with trip contact (c) Buchholz relay with isolating valves on both sides, bleeding pipe with pet cock at the end to collect gases and alarm/trip contacts (d) Air release plug (e) Inspection openings and covers (f) Bushings with metal parts and gaskets to suit the termination arrangement (g) Oil temperature indicators (h) Cover lifting eyes, reactor lifting lugs, jacking pads, towing holes and core and winding lifting lugs (i) Rating and diagram plates (j) Marshalling Box (Tank mounted) (k) Cooling equipment as applicable (l) Bushing Current Transformers, Neutral CT (if applicable) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 88 | Chapter-2: Technical Specification for Transformer and Reactor Page II-61 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0219 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | (m) Drain valves/plugs shall be provided in order that each section of pipe work can be drained independently (n) Terminal marking plates (o) Valves schedule plate (p) Bottom oil sampling valve with threaded male adaptors, Drain valves, Filter valves at top and bottom, shut off valves on both sides of Buchholz relay at accessible height, Sampling gas collectors for Buchholz relay at accessible height, Valve for vacuum application etc. (q) Suitable terminal connectors on bushings (r) Ladder to climb up to the tank cover with suitable locking arrangement to prevent climbing during charged condition. (s) Haulage/ lifting lugs (t) Two earthing terminals each on tank, marshalling boxes etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 89 | Chapter-2: Technical Specification for Transformer and Reactor Page II-62 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0220 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | (a) Rating and diagram plates (b) Terminal marking plates (c) Suitable terminal connection arrangement (d) Lifting lugs (e) Support structure etc. 29.0 INSPECTION AND TESTING | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 89 | Chapter-2: Technical Specification for Transformer and Reactor Page II-62 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0221 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | The manufacturer shall draw up and carry out a comprehensive inspection and testing programme in the form of detailed quality plan duly approved by Purchaser for necessary implementation during manufacture of the equipment. Details regarding Quality Assurance Programme covering quality assurance, inspection and testing have been covered in Chapter-4: Quality Assurance Programme. 30.0 DRAWINGS/DOCUMENTS/CALCULATIONS The list of drawing/documents/calculations to be submitted by the manufacturer is given in Annexure-H. | The manufacturer shall draw up and carry out a comprehensive inspection and testing programme in the form of detailed quality plan duly approved by Purchaser for necessary implementation during manufacture of the equipment. Details regarding Quality Assurance Programme covering quality assurance, inspection and testing have been covered in Chapter-4: Quality Assurance Programme. 30.0 DRAWINGS/DOCUMENTS/CALCULATIONS The list of drawing/documents/calculations to be submitted by the manufacturer is given in Annexure-H. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 89 | Chapter-2: Technical Specification for Transformer and Reactor Page II-62 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0222 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | Table giving details of OLTC like tap position Nos. and corresponding tapping voltage, tapping current & connection between terminals for different tap positions etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 92 | Chapter-2: Technical Specification for Transformer and Reactor Page II-65 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0223 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Details of Current Transformers (e.g. Bushing CTs, CT for WTI) installed in transformer like the location, core Nos., ratio(s), accuracy class, rated output (VA burden), knee point voltage, magnetizing current, maximum CT secondary resistance, terminal marking and application of the current transformer | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 92 | Chapter-2: Technical Specification for Transformer and Reactor Page II-65 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0224 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | of manufacturing process, installation, operation and maintenance etc. The erection, testing and commissioning of transformer/reactor shall be performed under strict supervision of representative of OEM and provisions specified in Chapter 5– Transportation, erection, testing & commissioning shall be followed. 32.2 Transformer/ Reactor failure generally follows the Bathtub Curve as shown below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of manufacturing process, installation, operation and maintenance etc. The erection, testing and commissioning of transformer/reactor shall be performed under strict supervision of representative of OEM and provisions specified in Chapter 5– Transportation, erection, testing & commissioning shall be followed. 32.2 Transformer/ Reactor failure generally follows the Bathtub Curve as shown below: | Transformers and reactors, 66 kV and above voltage class | PDF p. 97 | Chapter-2: Technical Specification for Transformer and Reactor Page II-70 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0225 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Safety | DGA | SAFETY | 32.3 As can be seen from the Bath Tub curve, the “Infant mortality” failures, which are caused due to manufacturing related defects/issues that occur in the first few years of service (say 1 or 2 years). But continued successful operation of transformer/reactor primarily depends on operating conditions and O&M practices being followed by utilities. Improper maintenance or negligence on the part of user e.g. non- replenishment of saturated silica gel, non-release of air trapped after air-cell commissioning, oil seepages, lack of routine maintenance, failure to check tan-delta & capacitance of winding and bushing, absence of thermal scanning of terminal interfaces, lack of DGA monitoring etc., can also lead to serious consequences. It can therefore be said that the responsibility of manufacturer and maintenance & monitoring obligations of the end user are equally important for a long and trouble free service life of transformer/reactor. Moreover, any abnormality observed during operation needs to be addressed immediately. The transparency in sharing of information, mutual co- | NOT COVERED | NOT VERIFIED | 2 years | 32.3 As can be seen from the Bath Tub curve, the “Infant mortality” failures, which are caused due to manufacturing related defects/issues that occur in the first few years of service (say 1 or 2 years). But continued successful operation of transformer/reactor primarily depends on operating conditions and O&M practices being followed by utilities. Improper maintenance or negligence on the part of user e.g. non- replenishment of saturated silica gel, non-release of air trapped after air-cell commissioning, oil seepages, lack of routine maintenance, failure to check tan-delta & capacitance of winding and bushing, absence of thermal scanning of terminal interfaces, lack of DGA monitoring etc., can also lead to serious consequences. It can therefore be said that the responsibility of manufacturer and maintenance & monitoring obligations of the end user are equally important for a long and trouble free service life of transformer/reactor. Moreover, any abnormality observed during operation needs to be addressed immediately. The transparency in sharing of information, mutual co- | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 97 | Chapter-2: Technical Specification for Transformer and Reactor Page II-70 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0226 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | operation and discussion on issues/problems between user and manufacturer are the only way to resolve many of these problems. The manufacturer can take this as an opportunity to understand the issues and can improve on the design & manufacturing practices. Similarly, the utility has the opportunity to understand the deficiency from their side and should rectify/try to improve on their actions as a responsible user. There is no single conclusive test based on which utility should take drastic steps regarding replacement/rejection of component/equipment. 32.4 The utilities should create their maintenance plans so that they adhere to the recommended O&M procedures of the OEMs. 32.5 When failures or operational problems occur within the warranty period, the manufacturer must take all necessary measures to help minimize operational difficulties and outages whenever possible. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | operation and discussion on issues/problems between user and manufacturer are the only way to resolve many of these problems. The manufacturer can take this as an opportunity to understand the issues and can improve on the design & manufacturing practices. Similarly, the utility has the opportunity to understand the deficiency from their side and should rectify/try to improve on their actions as a responsible user. There is no single conclusive test based on which utility should take drastic steps regarding replacement/rejection of component/equipment. 32.4 The utilities should create their maintenance plans so that they adhere to the recommended O&M procedures of the OEMs. 32.5 When failures or operational problems occur within the warranty period, the manufacturer must take all necessary measures to help minimize operational difficulties and outages whenever possible. | Transformers and reactors, 66 kV and above voltage class | PDF p. 98 | Chapter-2: Technical Specification for Transformer and Reactor Page II-71 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0227 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | The following abnormalities should be brought to the notice of manufacturer and the manufacturer shall respond/ attend immediately, investigate and rectify the problem or advise the utility for further course of action. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 98 | Chapter-2: Technical Specification for Transformer and Reactor Page II-71 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0228 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | migration) involving a shutdown of transformer/reactor at site after commissioning is to be attended by manufacturer immediately. It is the responsibility of the OEM to take immediate necessary action (e.g. any replacement/repair of component required with co- ordination from any third party, if required) for bringing back the transformer/ reactor into service. The root cause analysis shall be undertaken by OEM and details shall be shared with utility for the benefit of both user and OEM. | migration) involving a shutdown of transformer/reactor at site after commissioning is to be attended by manufacturer immediately. It is the responsibility of the OEM to take immediate necessary action (e.g. any replacement/repair of component required with co- ordination from any third party, if required) for bringing back the transformer/ reactor into service. The root cause analysis shall be undertaken by OEM and details shall be shared with utility for the benefit of both user and OEM. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 98 | Chapter-2: Technical Specification for Transformer and Reactor Page II-71 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0229 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | of any fault gas is exceeding the values in Table -2 of IEEE-C57.104 (Refer Chapter 6 of the document) or the abnormal trend in variation of key fault gases is observed, the utility should immediately consult OEM for advice and for further course of action. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | of any fault gas is exceeding the values in Table -2 of IEEE-C57.104 (Refer Chapter 6 of the document) or the abnormal trend in variation of key fault gases is observed, the utility should immediately consult OEM for advice and for further course of action. | Transformers and reactors, 66 kV and above voltage class | PDF p. 98 | Chapter-2: Technical Specification for Transformer and Reactor Page II-71 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0230 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | DGA | SAFETY | The transformer with DGA Status-3 does not necessarily give any conclusive information regarding health of transformer or indicate that transformer is faulty. It can only be concluded that its behaviour is somewhat unusual and warrants additional investigation and/or precautions. The transformer should be placed under increased surveillance. Other diagnostic tests should also be | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The transformer with DGA Status-3 does not necessarily give any conclusive information regarding health of transformer or indicate that transformer is faulty. It can only be concluded that its behaviour is somewhat unusual and warrants additional investigation and/or precautions. The transformer should be placed under increased surveillance. Other diagnostic tests should also be | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 98 | Chapter-2: Technical Specification for Transformer and Reactor Page II-71 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0231 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | conducted to supplement the DGA for taking further course of action in consultation with manufacturer. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 99 | Chapter-2: Technical Specification for Transformer and Reactor Page II-72 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0232 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Commissioning | Tan Delta | COMMISSIONING | than 0.001 per annum w.r.t. pre-commissioning values, the utility is to inform manufacturer for advice and for further course of action. d) In case, the tan delta of bushing(s) goes beyond 0.005 or increases | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 99 | Chapter-2: Technical Specification for Transformer and Reactor Page II-72 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0233 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Tan Delta | COMMISSIONING | more than 0.001 per annum w.r.t. pre-commissioning values when measured in the temperature range of 10°C to 40°C (If tan delta is measured at a temperature beyond above mentioned limit, necessary correction factor as per IEEE shall be applicable.), the utility is to inform manufacturer for advice and for further course of action. e) In case, the moisture content goes above 10 ppm at any temperature | more than 0.001 per annum w.r.t. pre-commissioning values when measured in the temperature range of 10°C to 40°C (If tan delta is measured at a temperature beyond above mentioned limit, necessary correction factor as per IEEE shall be applicable.), the utility is to inform manufacturer for advice and for further course of action. e) In case, the moisture content goes above 10 ppm at any temperature | NOT VERIFIED | 10°C; 40°C; 10 ppm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 99 | Chapter-2: Technical Specification for Transformer and Reactor Page II-72 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0234 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | during operation including full load, the utility is to inform manufacturer for advice and for further course of action. f) Any major deviation in Sweep Frequency Response Analysis (SFRA) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 99 | Chapter-2: Technical Specification for Transformer and Reactor Page II-72 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0235 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | serious quality lapse on the part of the Original Equipment Manufacturer (OEM). No leakage of oil is expected during the operating life of the transformer/reactor and that should be ensured accordingly by OEM during design & construction of tank & other gasketted joints. In case of any leakage of oil during warranty period, the same shall be reported in writing to the OEM immediately and OEM shall have to attend and rectify the leakage within a period of 30 days from the date of notice, at the cost of the OEM. | NOT COVERED | NOT VERIFIED | 30 days | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 99 | Chapter-2: Technical Specification for Transformer and Reactor Page II-72 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0236 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | of warranty period to ensure the healthiness of transformer/reactor and any abnormality in test results shall be informed to the manufacturer for immediate action and advice. 33.0 PHYSICAL INTERCHANGEABILITY OF TRANSFORMER/ REACTOR OF DIFFERENT MAKE Block foundation shall be adopted to facilitate the physical inter- changeability of transformers/reactors of different make on same foundation thereby the outage time of replacement of spare/new transformer or reactor would be minimized. The design shall take into | of warranty period to ensure the healthiness of transformer/reactor and any abnormality in test results shall be informed to the manufacturer for immediate action and advice. 33.0 PHYSICAL INTERCHANGEABILITY OF TRANSFORMER/ REACTOR OF DIFFERENT MAKE Block foundation shall be adopted to facilitate the physical inter- changeability of transformers/reactors of different make on same foundation thereby the outage time of replacement of spare/new transformer or reactor would be minimized. The design shall take into | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 99 | Chapter-2: Technical Specification for Transformer and Reactor Page II-72 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0237 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | account the provision of soak pit and oil collecting pit for transformer/reactor. The details are given at Annexure-P. 34.0 LIST OF CODES/ STANDARDS/ REGULATIONS/ PUBLICATIONS The list of Codes/Standards/Regulations/Publications which are | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 100 | Chapter-2: Technical Specification for Transformer and Reactor Page II-73 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0238 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Installation | INSTALLATION | generally used for manufacturing, testing, installation, maintenance, operation etc. of transformer/reactor is given at Annexure-W. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 100 | Chapter-2: Technical Specification for Transformer and Reactor Page II-73 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0239 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING |  Identify any new (prototype) features introduced by manufacturer and evaluate their reliability and risks.  To understand relevant design margins (calculated design withstand strength versus stress during tests and long service) to meet test requirements and life time performance as per manufacturer’s design practice and experience.  A good opportunity for a clear & mutual understanding and to exchange experiences that can be used to improve the current design and future specifications. |  Identify any new (prototype) features introduced by manufacturer and evaluate their reliability and risks.  To understand relevant design margins (calculated design withstand strength versus stress during tests and long service) to meet test requirements and life time performance as per manufacturer’s design practice and experience.  A good opportunity for a clear & mutual understanding and to exchange experiences that can be used to improve the current design and future specifications. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 102 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0240 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING |  Allow the purchaser to have clear understanding of the design, technical capabilities, experience of manufacturer and the manufacturing & testing facilities of manufacturer.  Clarifications of various tests and mutual agreement on method of tests and special acceptance of tolerance (e.g. Wave shape of impulse wave, connection for switching surge test etc.). |  Allow the purchaser to have clear understanding of the design, technical capabilities, experience of manufacturer and the manufacturing & testing facilities of manufacturer.  Clarifications of various tests and mutual agreement on method of tests and special acceptance of tolerance (e.g. Wave shape of impulse wave, connection for switching surge test etc.). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 102 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0241 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | The design review shall be carried out for the offered design of transformer/shunt reactor under the scope and Manufacturer shall submit all design documents and drawings required for the purpose.  Purchaser in consultation with the manufacturer shall carry out Design Review (DR) of parts and accessories (make, model, specifications for bushing, tap-changer, instruments etc.) as per technical requirements and specifications for enabling the manufacturer to order key raw materials and major accessories.  Review of the electrical design including dielectric, losses, short circuit, noise and thermal performance and mechanical layout design including lead routing and bushing termination after route | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 103 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0242 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | survey (if any) shall be carried out for enabling the manufacturer to order key raw materials and major accessories.  Typical data/parameters indicated in the Annexure-C shall be filled by the manufacturer and reviewed by the purchaser during design review.  Examination of all relevant type test reports of transformers/reactors including its fitting and accessories.  Checking of drawings and documents for the scope listed in Annexure-I. | survey (if any) shall be carried out for enabling the manufacturer to order key raw materials and major accessories.  Typical data/parameters indicated in the Annexure-C shall be filled by the manufacturer and reviewed by the purchaser during design review.  Examination of all relevant type test reports of transformers/reactors including its fitting and accessories.  Checking of drawings and documents for the scope listed in Annexure-I. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 104 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0243 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE |  Design review is initiated by purchaser or appointed representative. Purchaser should ensure that those participating representative in the review on his behalf have the necessary expertise to understand and evaluate the design and production considerations under the proposal.  Minutes of design review will be part of contract documents, but the discussions and information exchanged during design review process shall be kept confidential and purchaser or appointed representative shall not disclose or share design review details to anyone without written consent of Original Equipment Manufacturer (OEM).  After completion of design review, a summary report indicating list of items with actions required to be taken is to be sent to manufacturer for correction and inclusion of any omissions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 104 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0244 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Inspection | General | INSPECTION |  Purchaser may also visit the manufacturer’s works to inspect design, manufacturing and test facilities at any time.  Manufacturer, if desired by purchaser, should give in advance sufficient design data to purchaser to prepare for the design review meetings.  “Guidelines for conducting design reviews for transformers” CIGRE Technical Brochure 529-2013 may be followed. The document/brochure broadly covers the following: |  Purchaser may also visit the manufacturer’s works to inspect design, manufacturing and test facilities at any time.  Manufacturer, if desired by purchaser, should give in advance sufficient design data to purchaser to prepare for the design review meetings.  “Guidelines for conducting design reviews for transformers” CIGRE Technical Brochure 529-2013 may be followed. The document/brochure broadly covers the following: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 104 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0245 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | how it will perform within the operating parameters. Core flux density at rated and maximum voltage and frequency shall be reviewed with special reference to the maximum permissible limit to avoid overfluxing in any part of the core assembly including magnetic shunts and safety margins for the particular core construction type employed.  The manufacturer should describe each of the windings in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | how it will perform within the operating parameters. Core flux density at rated and maximum voltage and frequency shall be reviewed with special reference to the maximum permissible limit to avoid overfluxing in any part of the core assembly including magnetic shunts and safety margins for the particular core construction type employed.  The manufacturer should describe each of the windings in | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 105 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0246 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | designed to withstand the imposed stresses, i.e. indicate insulation structure, corresponding stress and resultant dielectric strength, including safety factors (margins).  The manufacturer will provide a list of the make and type of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | designed to withstand the imposed stresses, i.e. indicate insulation structure, corresponding stress and resultant dielectric strength, including safety factors (margins).  The manufacturer will provide a list of the make and type of | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 105 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0247 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | mechanical features for the core mechanical construction, coil clamping including the clamping pressure used for sizing and providing short circuit withstand capability and maintenance of winding compression during coil drying, core drying and assembly. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 105 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0248 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | tank details, details of gaskets, location of manholes & PRD, external cooling system, conservator/preservation system, provision for fire protection system etc.  The intended shipping process should also be reviewed. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | tank details, details of gaskets, location of manholes & PRD, external cooling system, conservator/preservation system, provision for fire protection system etc.  The intended shipping process should also be reviewed. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 106 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0249 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | For the benefit of the utility the formula for calculation of No-Load loss and Load loss, weight of core and current density of winding conductor has been provided below. In addition, a typical example of calculation of flux density, core quantity/ weight, no-load loss and weight of copper has been provided in Annexure-F. Calculation of no-load losses:  No-Load losses = core loss in W/kg corresponding to flux density as per lamination mill test report (extrapolated) x net weight of core x building factor  Flux density (T) = rated voltage (v) x104/ (4.44 x no. of turns x net core area (cm2) x frequency (Hz))  Net core area = [{0.785x (nominal core diameter)2 x filling factor}- area of cooling duct, insulation] x space factor | NOT COVERED | NOT VERIFIED | NOT VERIFIED | For the benefit of the utility the formula for calculation of No-Load loss and Load loss, weight of core and current density of winding conductor has been provided below. In addition, a typical example of calculation of flux density, core quantity/ weight, no-load loss and weight of copper has been provided in Annexure-F. Calculation of no-load losses:  No-Load losses = core loss in W/kg corresponding to flux density as per lamination mill test report (extrapolated) x net weight of core x building factor  Flux density (T) = rated voltage (v) x104/ (4.44 x no. of turns x net core area (cm2) x frequency (Hz))  Net core area = [{0.785x (nominal core diameter)2 x filling factor}- area of cooling duct, insulation] x space factor | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 106 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0250 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING |  Building factor = extra loss factor over the test report value due to handling and fabrication stress (>1)  Space factor = Reduction factor (depends on thickness) to take care of the insulation provided over the laminations (<1)  Filling factor = per unit area occupied by core material in the nominal core circle area (<1)  Nominal diameter of core = diameter of circle touching the corners of lamination steps Calculation of load-losses at reference temperature & principal tap position:  Load loss at principal tap = I2R loss + Winding Eddy loss + Structural stray losses  I2R loss = Resistance at 75°C x (phase current)2 x no. of phases  Resistance (R)= Resistance of winding (RW) + Resistance of leads (RL) |  Building factor = extra loss factor over the test report value due to handling and fabrication stress (>1)  Space factor = Reduction factor (depends on thickness) to take care of the insulation provided over the laminations (<1)  Filling factor = per unit area occupied by core material in the nominal core circle area (<1)  Nominal diameter of core = diameter of circle touching the corners of lamination steps Calculation of load-losses at reference temperature & principal tap position:  Load loss at principal tap = I2R loss + Winding Eddy loss + Structural stray losses  I2R loss = Resistance at 75°C x (phase current)2 x no. of phases  Resistance (R)= Resistance of winding (RW) + Resistance of leads (RL) | NOT VERIFIED | 75°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 107 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0251 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (a) CIGRE Technical Brochure No. 529 -2013 Guide lines for conducting design reviews for Power Transformers (b) CIGRE Technical Brochure No. 673-2016 Guide on Transformer Transportation (c) IEEE Standard C57.156-2016 Guide for tank rupture mitigation of oil immersed transformers (d) CIGRE Technical Brochure No. 530-2013 Guide for conducting factory capability assessment for Power Transformers (e) IEEE Standard C57.150-2012 Guide for Transformer Transportation (f) IS 2026/IEC 60076 Power Transformers-Part 5 Ability to withstand short circuit | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 108 | Chapter-3: Design Review | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0252 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | Quality of a transformer/reactor can be improved by taking effective steps at the initial stage itself which include ‘use of high quality raw materials’ and ‘improved manufacturing processes’. It is needless to mention that the performance of a transformer/reactor largely depends on the excellence of design. However, all good designs may not yield good end products unless they are well supported by good materials, good and healthy machines and skilled workmen (operators)/ workmanship. To ensure that the equipment and services are in accordance with the specifications, the transformer/reactor manufacturer shall adopt suitable Quality Assurance Programme (QAP) to control such activities at all points, as necessary. Such programmes shall be outlined by the manufacturer and shall be finally accepted by the Purchaser or its authorised representative after discussions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 110 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0253 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | The Quality Assurance programme shall be generally in line with latest ISO-9001 (Quality Management System), ISO-14001 (Environmental Management System) and OHSAS 18001 (Occupational Health and Safety Management System). A Quality Assurance Programme of the manufacturer shall generally cover the following: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The Quality Assurance programme shall be generally in line with latest ISO-9001 (Quality Management System), ISO-14001 (Environmental Management System) and OHSAS 18001 (Occupational Health and Safety Management System). A Quality Assurance Programme of the manufacturer shall generally cover the following: | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 110 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0254 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | a) Organisation structure for the management and implementation of the proposed Quality Assurance Programme b) Quality System Manual c) Design Control System d) Documentation Control System e) Qualification and experience data for key Personnel f) The procedure for purchase of materials, parts, components and selection of sub-supplier’s services including vendor analysis, source inspection, incoming raw material inspection, verification of materials purchased etc. g) List of manufacturing facilities available h) Level of automation achieved and list of areas where manual processing exists | a) Organisation structure for the management and implementation of the proposed Quality Assurance Programme b) Quality System Manual c) Design Control System d) Documentation Control System e) Qualification and experience data for key Personnel f) The procedure for purchase of materials, parts, components and selection of sub-supplier’s services including vendor analysis, source inspection, incoming raw material inspection, verification of materials purchased etc. g) List of manufacturing facilities available h) Level of automation achieved and list of areas where manual processing exists | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 110 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0255 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Inspection | INSTALLATION | i) List of areas in manufacturing process, where stage inspections are normally carried out for quality control and details of such tests and inspections. j) System for shop manufacturing and site erection control including process controls and fabrication and assembly controls k) System for Control of non-conforming items and for corrective & preventive actions based on customers’ feedback. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 111 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0256 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS | NOT VERIFIED | Inspection | AIS | INSPECTION | l) Inspection and test procedure both for manufacture and field activities m) System for Control of calibration of testing and measuring equipment and the indications of calibration status on the instrument n) System for Quality Audits o) System for indication and appraisal of inspection status p) System for authorising release of manufactured product to the Purchaser q) System for handling storage and delivery r) System for maintenance of records s) Furnishing of quality plans for manufacturing and field activities detailing out the specific quality control procedure adopted for controlling the quality characteristics relevant to each item of equipment/component t) System of various field activities i.e. | l) Inspection and test procedure both for manufacture and field activities m) System for Control of calibration of testing and measuring equipment and the indications of calibration status on the instrument n) System for Quality Audits o) System for indication and appraisal of inspection status p) System for authorising release of manufactured product to the Purchaser q) System for handling storage and delivery r) System for maintenance of records s) Furnishing of quality plans for manufacturing and field activities detailing out the specific quality control procedure adopted for controlling the quality characteristics relevant to each item of equipment/component t) System of various field activities i.e. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 111 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0257 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | unloading, receipt at site, proper storage, erection, testing & commissioning The manufacturer shall use state-of-the-art technology and dirt, dust and humidity controlled environment during various processes of manufacturing and testing to ensure that end product is of good quality and will provide uninterrupted service for intended life period. All manufacturers, are expected to develop their manufacturing facility at par with the leading manufacturers with best global practices. An indicative list for facilities needed to be available at manufacturer’s works has been provided at Annexure-G. In case the manufacturers do not have the required facilities as given in Annexure-G, it may be ensured by the manufacturers that the same shall be made available and put into use within two years of release of this document. | unloading, receipt at site, proper storage, erection, testing & commissioning The manufacturer shall use state-of-the-art technology and dirt, dust and humidity controlled environment during various processes of manufacturing and testing to ensure that end product is of good quality and will provide uninterrupted service for intended life period. All manufacturers, are expected to develop their manufacturing facility at par with the leading manufacturers with best global practices. An indicative list for facilities needed to be available at manufacturer’s works has been provided at Annexure-G. In case the manufacturers do not have the required facilities as given in Annexure-G, it may be ensured by the manufacturers that the same shall be made available and put into use within two years of release of this document. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 111 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0258 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS | NOT VERIFIED | Inspection | AIS | INSPECTION | 2.2 Manufacturing Quality Plan will detail out for all the components and equipment, various tests/inspection, to be carried out as per the requirements of purchaser specification and standards mentioned therein and quality practices and procedures followed by Manufacturer’s/Sub-supplier’s/Sub-supplier's Quality Control Organisation, the relevant reference documents and standards, acceptance norms, inspection documents raised etc., during all stages of materials procurement, manufacture, assembly and final testing/performance testing. The Quality Plan shall be submitted to purchaser, for review and approval. Typical Manufacturing Quality Plan (MQP) is provided at Annexure-E for reference. | 2.2 Manufacturing Quality Plan will detail out for all the components and equipment, various tests/inspection, to be carried out as per the requirements of purchaser specification and standards mentioned therein and quality practices and procedures followed by Manufacturer’s/Sub-supplier’s/Sub-supplier's Quality Control Organisation, the relevant reference documents and standards, acceptance norms, inspection documents raised etc., during all stages of materials procurement, manufacture, assembly and final testing/performance testing. The Quality Plan shall be submitted to purchaser, for review and approval. Typical Manufacturing Quality Plan (MQP) is provided at Annexure-E for reference. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 112 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0259 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | Inspection | SCHEDULE | Any change in practice or acceptance norms (with reference to various tests / parameters in respective National / International standard) would be suitably incorporated by manufacturer from time to time and submit the same for approval of purchaser / utility. 2.3 List of testing equipment available with the manufacturer for stage/final testing of transformer/reactor and test plant limitation, if any, for the acceptance and routine tests specified in the relevant standards shall be furnished by the manufacturer. These limitations shall be very clearly brought out in 'The schedule of deviations' for specified test requirements. 2.4 The transformer/reactor manufacturer, along with Quality Plans, shall also furnish copies of the reference documents/plant standards/acceptance norms/tests and inspection procedure etc., as referred in Quality Plans. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 112 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0260 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | These Quality Plans and reference documents/standards etc. will be subject to Purchaser’s approval without which manufacturer shall not proceed. These approved documents shall form a part of the contract. In these approved Quality Plans, Purchaser shall identify Customer Hold Points (CHP), i.e. test/checks which shall be carried out in presence of the Purchaser’s authorised representative and the work will not proceed without consent of Purchaser in writing. All deviations to approved quality plans and applicable standards must be documented and referred to Purchaser along with technical justification for approval and dispositioning. 2.5 All material used for equipment manufacture shall be of tested quality as per relevant codes/standards. | These Quality Plans and reference documents/standards etc. will be subject to Purchaser’s approval without which manufacturer shall not proceed. These approved documents shall form a part of the contract. In these approved Quality Plans, Purchaser shall identify Customer Hold Points (CHP), i.e. test/checks which shall be carried out in presence of the Purchaser’s authorised representative and the work will not proceed without consent of Purchaser in writing. All deviations to approved quality plans and applicable standards must be documented and referred to Purchaser along with technical justification for approval and dispositioning. 2.5 All material used for equipment manufacture shall be of tested quality as per relevant codes/standards. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 112 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0261 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | Details of results of the tests conducted to determine the mechanical properties; chemical analysis and details of heat treatment procedure, if any and actually followed shall be recorded on certificates and time temperature chart, as applicable. Tests shall be carried out as per applicable material standards and/or agreed details. 2.6 No material shall be despatched from the manufacturer’s works before the same is accepted, subsequent to pre-despatch final inspection including verification of records of all previous | Details of results of the tests conducted to determine the mechanical properties; chemical analysis and details of heat treatment procedure, if any and actually followed shall be recorded on certificates and time temperature chart, as applicable. Tests shall be carried out as per applicable material standards and/or agreed details. 2.6 No material shall be despatched from the manufacturer’s works before the same is accepted, subsequent to pre-despatch final inspection including verification of records of all previous | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 112 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0262 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | tests/inspections by Purchaser’s authorised representative and duly authorised for despatch. 2.7 The manufacturer shall list out all major items/equipment/components to be manufactured in house as well as procured from sub-supplier. All the sub-suppliers proposed by the manufacturer for procurement of major bought out items including castings, forging, semi-finished and finished components/equipment etc., list of which shall be drawn up by the manufacturer and finalized with the Purchaser and shall be subject to Purchaser's approval. The manufacturer’s proposal shall include vendor’s facilities established at the respective works, the process capability, process stabilization, quality systems followed, experience list, etc. | tests/inspections by Purchaser’s authorised representative and duly authorised for despatch. 2.7 The manufacturer shall list out all major items/equipment/components to be manufactured in house as well as procured from sub-supplier. All the sub-suppliers proposed by the manufacturer for procurement of major bought out items including castings, forging, semi-finished and finished components/equipment etc., list of which shall be drawn up by the manufacturer and finalized with the Purchaser and shall be subject to Purchaser's approval. The manufacturer’s proposal shall include vendor’s facilities established at the respective works, the process capability, process stabilization, quality systems followed, experience list, etc. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 113 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0263 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | AIS | NOT VERIFIED | Installation | AIS | INSTALLATION | along with his own technical evaluation for identified sub-suppliers enclosed and shall be submitted to the Purchaser for approval in sufficient time so as not to impede the progress of work on the facilities. 2.8 For components/equipment procured by the manufacturer for the purpose of the contract, after obtaining the written approval of the Purchaser, the manufacturer’s purchase specifications and inquiries shall call for quality plans to be submitted by the suppliers. The quality plans called for from the sub-suppliers shall set out, during the various stages of manufacture and installation, the quality practices and procedures followed by the vendor’s quality control organisation, the relevant reference documents/standards used, acceptance level, inspection of documentation raised, etc. | along with his own technical evaluation for identified sub-suppliers enclosed and shall be submitted to the Purchaser for approval in sufficient time so as not to impede the progress of work on the facilities. 2.8 For components/equipment procured by the manufacturer for the purpose of the contract, after obtaining the written approval of the Purchaser, the manufacturer’s purchase specifications and inquiries shall call for quality plans to be submitted by the suppliers. The quality plans called for from the sub-suppliers shall set out, during the various stages of manufacture and installation, the quality practices and procedures followed by the vendor’s quality control organisation, the relevant reference documents/standards used, acceptance level, inspection of documentation raised, etc. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 113 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0264 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | Such quality plans of the successful vendors shall be finalised with the Purchaser and such approved Quality Plans shall form a part of the purchase order/contract between the manufacturer and sub-suppliers. 2.9 Purchaser reserves the right to carry out quality audit and quality surveillance of the systems and procedures of the manufacturer’s or their sub-supplier’s quality management and control activities. The manufacturer shall provide all necessary assistance to enable the Purchaser carry out such audit and surveillance. 2.10 The manufacturer shall carry out an inspection and testing programme during manufacturing in his work and that of his sub- supplier and at site to ensure the mechanical accuracy of components, compliance with drawings, conformance to functional and performance requirements, identity and acceptability of all materials parts and equipment. | Such quality plans of the successful vendors shall be finalised with the Purchaser and such approved Quality Plans shall form a part of the purchase order/contract between the manufacturer and sub-suppliers. 2.9 Purchaser reserves the right to carry out quality audit and quality surveillance of the systems and procedures of the manufacturer’s or their sub-supplier’s quality management and control activities. The manufacturer shall provide all necessary assistance to enable the Purchaser carry out such audit and surveillance. 2.10 The manufacturer shall carry out an inspection and testing programme during manufacturing in his work and that of his sub- supplier and at site to ensure the mechanical accuracy of components, compliance with drawings, conformance to functional and performance requirements, identity and acceptability of all materials parts and equipment. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 113 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0265 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | Manufacturer shall carry out all tests/inspection required to establish that the items/equipment conform to requirements of the specification and the relevant codes/standards specified in the specification, in addition to carrying out tests as per the approved quality plan. | Manufacturer shall carry out all tests/inspection required to establish that the items/equipment conform to requirements of the specification and the relevant codes/standards specified in the specification, in addition to carrying out tests as per the approved quality plan. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 113 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0266 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Troubleshooting | Inspection | TROUBLESHOOTING | 2.11 Quality audit/surveillance/approval of the results of the tests and inspection will not, however, prejudice the right of the Purchaser to reject the equipment if it does not comply with the specification, when erected or does not give complete satisfaction in service and the above shall in no way limit the liabilities and responsibilities of the manufacturer in ensuring complete conformance of the materials/equipment supplied to relevant specification, standard, data sheets, drawings (approved by the Purchaser), and minutes of various meetings with customer / Purchaser etc. 2.12 Any repair/rectification procedures to be adopted to make the job acceptable shall be subject to the approval of the Purchaser/authorised representative. 2.13 The Manufacturer / Sub-suppliers shall carry out routine test on 100% item at manufacturer / sub-supplier's works. | 2.11 Quality audit/surveillance/approval of the results of the tests and inspection will not, however, prejudice the right of the Purchaser to reject the equipment if it does not comply with the specification, when erected or does not give complete satisfaction in service and the above shall in no way limit the liabilities and responsibilities of the manufacturer in ensuring complete conformance of the materials/equipment supplied to relevant specification, standard, data sheets, drawings (approved by the Purchaser), and minutes of various meetings with customer / Purchaser etc. 2.12 Any repair/rectification procedures to be adopted to make the job acceptable shall be subject to the approval of the Purchaser/authorised representative. 2.13 The Manufacturer / Sub-suppliers shall carry out routine test on 100% item at manufacturer / sub-supplier's works. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 2.11 Quality audit/surveillance/approval of the results of the tests and inspection will not, however, prejudice the right of the Purchaser to reject the equipment if it does not comply with the specification, when erected or does not give complete satisfaction in service and the above shall in no way limit the liabilities and responsibilities of the manufacturer in ensuring complete conformance of the materials/equipment supplied to relevant specification, standard, data sheets, drawings (approved by the Purchaser), and minutes of various meetings with customer / Purchaser etc. 2.12 Any repair/rectification procedures to be adopted to make the job acceptable shall be subject to the approval of the Purchaser/authorised representative. 2.13 The Manufacturer / Sub-suppliers shall carry out routine test on 100% item at manufacturer / sub-supplier's works. | Transformers and reactors, 66 kV and above voltage class | PDF p. 114 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0267 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | The quantum of check / test for routine & acceptance test by purchaser shall be generally as per criteria / sampling plan defined in referred standards. Wherever standards have not been mentioned quantum of check / test for routine / acceptance test shall be as agreed during detailed engineering stage. 2.14 The manufacturer/ contractor (as applicable) shall submit to the Purchaser Field Welding Schedule for field welding activities (if applicable) along with all supporting documents, like welding procedures, heat treatment procedures, Non-Destructive Test (NDT) procedures etc. before schedule start of erection work at site. 2.15 Transformer/reactor manufacturer shall also provide Field Quality Plans that will detail out for all the equipment, the quality practices and procedures etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 114 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0268 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | to be followed by the manufacturer’s representative or authorised agency, during various stages of site activities starting from receipt of materials/equipment at site till commissioning. 2.16 All welding and brazing shall be carried out as per procedure drawn and qualified in accordance with requirements of ASME Section IX/BS-4870 or other International equivalent standard acceptable to the Purchaser. All welding / brazing procedures adopted/used at shop, will be made available to purchaser during audit / inspection. Procedures to be adopted at site will be submitted to purchaser for approval. 2.17 All brazers, welders and welding operators employed on any part of the contract either in Manufacturer’s/his sub- supplier’s works or at site or elsewhere shall be qualified as per ASME Section-IX or BS-4871 or other equivalent International Standards acceptable to the Purchaser. | to be followed by the manufacturer’s representative or authorised agency, during various stages of site activities starting from receipt of materials/equipment at site till commissioning. 2.16 All welding and brazing shall be carried out as per procedure drawn and qualified in accordance with requirements of ASME Section IX/BS-4870 or other International equivalent standard acceptable to the Purchaser. All welding / brazing procedures adopted/used at shop, will be made available to purchaser during audit / inspection. Procedures to be adopted at site will be submitted to purchaser for approval. 2.17 All brazers, welders and welding operators employed on any part of the contract either in Manufacturer’s/his sub- supplier’s works or at site or elsewhere shall be qualified as per ASME Section-IX or BS-4871 or other equivalent International Standards acceptable to the Purchaser. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 114 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0269 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | a) Quality Plan for various components and accessories. A typical quality plan for key components of transformer is provided at Annexure-E. b) Material mill test reports on components as specified by the specification and approved Quality Plans. c) Manufacturer’s works test reports/results for testing required as per applicable codes and standard referred in the specification and approved Quality Plans. d) Non-destructive examination results/reports including radiography interpretation reports. Sketches/drawings used for indicating the method of traceability of the radiographs to the location on the equipment. e) Heat Treatment Certificate/Record (Time- temperature Chart), if any. f) All the accepted Non-conformance Reports (Major/Minor)/deviation, including complete technical details /repair procedure). | a) Quality Plan for various components and accessories. A typical quality plan for key components of transformer is provided at Annexure-E. b) Material mill test reports on components as specified by the specification and approved Quality Plans. c) Manufacturer’s works test reports/results for testing required as per applicable codes and standard referred in the specification and approved Quality Plans. d) Non-destructive examination results/reports including radiography interpretation reports. Sketches/drawings used for indicating the method of traceability of the radiographs to the location on the equipment. e) Heat Treatment Certificate/Record (Time- temperature Chart), if any. f) All the accepted Non-conformance Reports (Major/Minor)/deviation, including complete technical details /repair procedure). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 115 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0270 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | g) Customer Hold Points (CHP)/Inspection reports duly signed by the Inspector of the Purchaser and Manufacturer for the agreed Customer Hold Points. h) Certificate of Conformance (COC) wherever applicable. i) Material Dispatch Clearance Certificate (MDCC) 3.4 Similarly, the manufacturer/contractor (as applicable) shall be required to submit hard copies and DVD/ Pen Drive containing soft copy, containing QA Documentation pertaining to field activities as per Approved Field Quality Plans and other agreed manuals/ procedures, prior to commissioning. | g) Customer Hold Points (CHP)/Inspection reports duly signed by the Inspector of the Purchaser and Manufacturer for the agreed Customer Hold Points. h) Certificate of Conformance (COC) wherever applicable. i) Material Dispatch Clearance Certificate (MDCC) 3.4 Similarly, the manufacturer/contractor (as applicable) shall be required to submit hard copies and DVD/ Pen Drive containing soft copy, containing QA Documentation pertaining to field activities as per Approved Field Quality Plans and other agreed manuals/ procedures, prior to commissioning. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 115 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0271 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | General | INSPECTION | 3.5 Before offering for Factory Acceptance Test of any equipment, the Supplier shall make sure that the corresponding quality document or in the case of protracted phased deliveries, the applicable section of the quality document file is completed. The supplier will then notify the Inspector regarding the readiness of the quality document (or applicable section) for review: | 3.5 Before offering for Factory Acceptance Test of any equipment, the Supplier shall make sure that the corresponding quality document or in the case of protracted phased deliveries, the applicable section of the quality document file is completed. The supplier will then notify the Inspector regarding the readiness of the quality document (or applicable section) for review: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 116 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0272 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Inspection | INSTALLATION | endeavour to correct the incompleteness, thus allowing to finalize the quality document (or applicable section) by time compatible with the requirements as per contract documents. When it is done, the quality document (or applicable section) is stamped by the Inspector. Note:- The word ‘Inspector’ shall mean the authorised representative and/or an outside inspection agency acting on behalf of the purchaser to inspect and examine the materials and workmanship of the works during its manufacture or erection. 4.0 QUALITY DURING INSPECTION & TESTING (including virtual inspection) AND INSPECTION CERTIFICATES 4.1 Inspection, audit, assessment, test measurement and comparison all describe the same phenomena of examining carefully to some established criteria. Inspector should be prepared with the following documents: | endeavour to correct the incompleteness, thus allowing to finalize the quality document (or applicable section) by time compatible with the requirements as per contract documents. When it is done, the quality document (or applicable section) is stamped by the Inspector. Note:- The word ‘Inspector’ shall mean the authorised representative and/or an outside inspection agency acting on behalf of the purchaser to inspect and examine the materials and workmanship of the works during its manufacture or erection. 4.0 QUALITY DURING INSPECTION & TESTING (including virtual inspection) AND INSPECTION CERTIFICATES 4.1 Inspection, audit, assessment, test measurement and comparison all describe the same phenomena of examining carefully to some established criteria. Inspector should be prepared with the following documents: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 116 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0273 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Installation | Inspection | INSTALLATION | a) Contract documents together with technical specifications b) Basic guideline regarding the scope of inspection c) Approved drawings and reference standards (ISS/IEC/BS etc.) d) Previous inspection reports of transformers of similar rating (if available) e) Type test certificates (if already conducted). 4.2 The Inspector shall have access at all reasonable times to inspect and examine the materials and workmanship of the works during its manufacture or erection and if part of the works is being manufactured or assembled on other premises or works, the Manufacturer shall obtain for the Inspector permission to inspect as if the works were manufactured or assembled on the Manufacturer’s own premises or works. 4.3 The Manufacturer shall give the Inspector ten (10) days written notice of any material being ready for testing. Such tests shall be to the Manufacturer’s account. The Inspector, unless the witnessing of the tests is virtually waived and confirmed in writing, | a) Contract documents together with technical specifications b) Basic guideline regarding the scope of inspection c) Approved drawings and reference standards (ISS/IEC/BS etc.) d) Previous inspection reports of transformers of similar rating (if available) e) Type test certificates (if already conducted). 4.2 The Inspector shall have access at all reasonable times to inspect and examine the materials and workmanship of the works during its manufacture or erection and if part of the works is being manufactured or assembled on other premises or works, the Manufacturer shall obtain for the Inspector permission to inspect as if the works were manufactured or assembled on the Manufacturer’s own premises or works. 4.3 The Manufacturer shall give the Inspector ten (10) days written notice of any material being ready for testing. Such tests shall be to the Manufacturer’s account. The Inspector, unless the witnessing of the tests is virtually waived and confirmed in writing, | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 116 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0274 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | will attend such tests within ten (10) days of the date on which the equipment is noticed as being ready for test/inspection. 4.4 Virtual Stage inspection & Factory Acceptance Test (FAT) | will attend such tests within ten (10) days of the date on which the equipment is noticed as being ready for test/inspection. 4.4 Virtual Stage inspection & Factory Acceptance Test (FAT) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 117 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0275 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | The conventional practice of witnessing Stage inspection and Factory Acceptance Test (FAT) of transformers and reactors as per technical specification of the utility/purchaser requires physical presence of utility’s/purchaser’s representative/inspector at manufacturer’s works and involves considerable co-ordination efforts and planning by both utility/purchaser and manufacturers, especially in special situations like Covid-19 pandemic. The self- certification/waiver of FAT is not desirable. Under the situation like Covid-19 or if there is mutual agreement between the manufacturer & the utility/purchaser, manufacturer can offer virtual stage inspection or FAT or both, with similar experience/confidence as on-site witness, as an alternative to conventional method. 4.4.1 The resources required for virtual inspection/testing: | The conventional practice of witnessing Stage inspection and Factory Acceptance Test (FAT) of transformers and reactors as per technical specification of the utility/purchaser requires physical presence of utility’s/purchaser’s representative/inspector at manufacturer’s works and involves considerable co-ordination efforts and planning by both utility/purchaser and manufacturers, especially in special situations like Covid-19 pandemic. The self- certification/waiver of FAT is not desirable. Under the situation like Covid-19 or if there is mutual agreement between the manufacturer & the utility/purchaser, manufacturer can offer virtual stage inspection or FAT or both, with similar experience/confidence as on-site witness, as an alternative to conventional method. 4.4.1 The resources required for virtual inspection/testing: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 117 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0276 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | (a) High speed Wi-Fi Internet (b) Necessary electronic devices like Mobiles, Tabs or iPads, portable cameras, computers for test equipment or instruments, Conference call setup with laptop, cameras in test lab and test bay for clear view of the test bay as well as transformer/reactor under test, connection leads and measuring equipment etc. For better clarity and transparency, wherever possible, screens of computers for test equipment or instruments should be paralleled for direct view of the customer. Example – Loss Measurement system, PD test System, HV Test System etc. | (a) High speed Wi-Fi Internet (b) Necessary electronic devices like Mobiles, Tabs or iPads, portable cameras, computers for test equipment or instruments, Conference call setup with laptop, cameras in test lab and test bay for clear view of the test bay as well as transformer/reactor under test, connection leads and measuring equipment etc. For better clarity and transparency, wherever possible, screens of computers for test equipment or instruments should be paralleled for direct view of the customer. Example – Loss Measurement system, PD test System, HV Test System etc. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 117 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0277 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Earthing | SAFETY | (Note: Issues of screen blinking may be observed during chopped wave lightning impulse due to earthing issues and should be ignored) (c) Qualified engineers well-conversant with technology shall be deployed to effectively handle online stage inspection/FAT. (d) Online applications like Microsoft Teams, Skype, Google meet, Google hangout, WhatsApp, etc. (e) Measuring Instruments with valid calibration certificates | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (Note: Issues of screen blinking may be observed during chopped wave lightning impulse due to earthing issues and should be ignored) (c) Qualified engineers well-conversant with technology shall be deployed to effectively handle online stage inspection/FAT. (d) Online applications like Microsoft Teams, Skype, Google meet, Google hangout, WhatsApp, etc. (e) Measuring Instruments with valid calibration certificates | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 117 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0278 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | (f) Recording facility of all the activities performed during stage inspection/FAT as well as photography of recording of important readings should form part of the Stage/Final inspection reports of the product. (g) The manufacturer shall nominate a nodal officer, who shall be responsible for coordinating with the utility/purchaser and camera operators for visual arrangement/facilities spread across different locations within the manufacturer’s works. (h) Different sections like Core - coil assembly area, winding area, | (f) Recording facility of all the activities performed during stage inspection/FAT as well as photography of recording of important readings should form part of the Stage/Final inspection reports of the product. (g) The manufacturer shall nominate a nodal officer, who shall be responsible for coordinating with the utility/purchaser and camera operators for visual arrangement/facilities spread across different locations within the manufacturer’s works. (h) Different sections like Core - coil assembly area, winding area, | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 118 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0279 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | tank inspection area etc. shall be provided with adequate no. of cameras or portable cameras can be used for clear and proper visualisation of the test object. (i) During stage inspection/FAT, the position of cameras (with zoom in/out facility) shall be done in such a way that the test object, measuring instruments and test equipment are clearly visible. 4.4.2 Procedure for virtual inspection / testing: | tank inspection area etc. shall be provided with adequate no. of cameras or portable cameras can be used for clear and proper visualisation of the test object. (i) During stage inspection/FAT, the position of cameras (with zoom in/out facility) shall be done in such a way that the test object, measuring instruments and test equipment are clearly visible. 4.4.2 Procedure for virtual inspection / testing: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 118 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0280 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | (a) Manufacturer’s QA/QC in-charge will plan, verify the process checklist and ensure that the Stage inspection/Routine/FAT are conducted as per approved quality plan in line with the Technical Specification. (b) Manufacturer will submit soft copies of Photographs and Calibration Certificates with proper index sheet duly certified from their end in order to demonstrate readiness of Transformer/Reactor for inspection/testing. (c) The Date and time and arrangement for online stage inspection/FAT shall be finalised in consultation with the utility/purchaser. (d) Online inspection/FAT shall be done through online application platform like – Microsoft Teams, Skype, Google meet, Google hangout, WhatsApp, etc., considering the system compatibility and security in consultation with the utility/purchaser. | (a) Manufacturer’s QA/QC in-charge will plan, verify the process checklist and ensure that the Stage inspection/Routine/FAT are conducted as per approved quality plan in line with the Technical Specification. (b) Manufacturer will submit soft copies of Photographs and Calibration Certificates with proper index sheet duly certified from their end in order to demonstrate readiness of Transformer/Reactor for inspection/testing. (c) The Date and time and arrangement for online stage inspection/FAT shall be finalised in consultation with the utility/purchaser. (d) Online inspection/FAT shall be done through online application platform like – Microsoft Teams, Skype, Google meet, Google hangout, WhatsApp, etc., considering the system compatibility and security in consultation with the utility/purchaser. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 118 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0281 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | Online recording facility of the activities performed or witnessed must be available at manufacturer’s end at all time for customer’s reference/review/record. (e) Utility’s/purchaser’s approval shall be taken in advance for the virtual stage inspection/FAT including the specific online application platform that will be used. | Online recording facility of the activities performed or witnessed must be available at manufacturer’s end at all time for customer’s reference/review/record. (e) Utility’s/purchaser’s approval shall be taken in advance for the virtual stage inspection/FAT including the specific online application platform that will be used. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 118 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0282 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | (f) Whenever required the Mock trial may be carried out at manufacturer’s work to get hands on experience before offering to customer. (g) All issues must be discussed and resolved before commencement of inspection/tests. (h) The Test circuits and Test procedure shall be shared with utility’s/purchaser’s inspector for clarity & better understanding. | (f) Whenever required the Mock trial may be carried out at manufacturer’s work to get hands on experience before offering to customer. (g) All issues must be discussed and resolved before commencement of inspection/tests. (h) The Test circuits and Test procedure shall be shared with utility’s/purchaser’s inspector for clarity & better understanding. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 119 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0283 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Inspection | SAFETY | (i) Application link and security password shall be shared with the utility’s/purchaser’s inspecting officer on the same day of inspection and password must be secured to maintain the confidentiality. (j) While conducting remote FAT, due care must be taken to keep the data safe while transmitting from factory to utility’s/ purchaser’s inspector through a web-based application. There are various Cybersecurity requirements and InfoSec protocols, which should be adhered to for safety like Database Security, Strong Password Policy, Access Control, Restricted Access via 2-Factor Authentication for utility/purchaser, Single Session or Timed Sessions, Resetting Passwords, Password Expiry Policy, Validations for 3rd Party participants, Authentication for users/test engineers etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (i) Application link and security password shall be shared with the utility’s/purchaser’s inspecting officer on the same day of inspection and password must be secured to maintain the confidentiality. (j) While conducting remote FAT, due care must be taken to keep the data safe while transmitting from factory to utility’s/ purchaser’s inspector through a web-based application. There are various Cybersecurity requirements and InfoSec protocols, which should be adhered to for safety like Database Security, Strong Password Policy, Access Control, Restricted Access via 2-Factor Authentication for utility/purchaser, Single Session or Timed Sessions, Resetting Passwords, Password Expiry Policy, Validations for 3rd Party participants, Authentication for users/test engineers etc. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 119 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0284 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Inspection | General | INSPECTION | (k) All tests shall be conducted as per relevant latest standards/procedures mentioned in the Technical Specification. The readings recorded in each test will be shown to remote-end inspector live for witness/acceptance. At the end of each test, either side shall discuss the summary of test results to avoid ambiguity at later stage. During Temperature Rise test, the HOT resistance has to be measured at the time of shutdown of power supply to Transformer. The camera position shall be suitably placed, so that the readings are visible without any obstruction by the working personnel. As | (k) All tests shall be conducted as per relevant latest standards/procedures mentioned in the Technical Specification. The readings recorded in each test will be shown to remote-end inspector live for witness/acceptance. At the end of each test, either side shall discuss the summary of test results to avoid ambiguity at later stage. During Temperature Rise test, the HOT resistance has to be measured at the time of shutdown of power supply to Transformer. The camera position shall be suitably placed, so that the readings are visible without any obstruction by the working personnel. As | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 119 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0285 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Inspection | FAILURE_ANALYSIS | far as possible, resistance measurement should be done inside the Control Room to avoid any obstructions or interfere of personnel. (l) During testing, one camera shall always be focused towards test bay area where the transformer / reactor is under test for online overview of connections. If one camera is not enough to see both transformer and test leads, more no. of cameras shall be deployed. This will enable complete testing connection overview to inspecting officer all the time. (m) The camera must be operated by the authorised person of the manufacturer as per the direction of the inspection team [representatives of utility/purchaser]. The inspection team should have the facility to communicate directly with the manufacturer’s representative for a thorough & effective inspection including the physical verification of the dimension, surface defect etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | far as possible, resistance measurement should be done inside the Control Room to avoid any obstructions or interfere of personnel. (l) During testing, one camera shall always be focused towards test bay area where the transformer / reactor is under test for online overview of connections. If one camera is not enough to see both transformer and test leads, more no. of cameras shall be deployed. This will enable complete testing connection overview to inspecting officer all the time. (m) The camera must be operated by the authorised person of the manufacturer as per the direction of the inspection team [representatives of utility/purchaser]. The inspection team should have the facility to communicate directly with the manufacturer’s representative for a thorough & effective inspection including the physical verification of the dimension, surface defect etc. | Transformers and reactors, 66 kV and above voltage class | PDF p. 120 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0286 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Inspection | Inspection | INSPECTION | (n) The image quality shall be good enough for assessment of the condition of the transformer which may affect the quality & performance of transformer. The factors affecting image quality include:  Poor image resolution.  Image out of focus.  Inadequate lighting /Glare from strong light source/shadows  Frequent loss of connectivity between the Inspection team | (n) The image quality shall be good enough for assessment of the condition of the transformer which may affect the quality & performance of transformer. The factors affecting image quality include:  Poor image resolution.  Image out of focus.  Inadequate lighting /Glare from strong light source/shadows  Frequent loss of connectivity between the Inspection team | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 120 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0287 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | and the onsite Video monitors. (o) The Two-way Audio-Video communication Scheme for stage inspection/FAT of transformer/reactor through web shall be as follows: | and the onsite Video monitors. (o) The Two-way Audio-Video communication Scheme for stage inspection/FAT of transformer/reactor through web shall be as follows: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 120 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0288 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | (p) The camera should be focused for continuous visibility of the test values in the meters so that the utility’s/purchaser’s inspector can see the test values throughout the Inspection. | (p) The camera should be focused for continuous visibility of the test values in the meters so that the utility’s/purchaser’s inspector can see the test values throughout the Inspection. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 121 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0289 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | (q) During the stage Inspection/FAT, test results/readings & test connections shall be recorded and mailed to the utility’s/ purchaser’s inspector. (r) The manufacturer has to prepare test report on daily basis during testing period by the end of each day. Test Reports must be issued by the testing in charge of manufacturer indicating list of Tests carried out and the test results. (s) For long duration tests (Temperature rise and partial discharge and impulse), manufacturer shall ensure that Cameras shall be provided near transformer/reactor under test and the Power analyser or equipment’s computer so that the readings can be seen simultaneously. (t) After completion of inspection, OEMs representative should sign off from the application. (u) After getting stage inspection Clearance from utility/purchaser, the transformer/reactor may be moved to next stage of manufacturing process and after getting FAT Clearance from utility/purchaser, the transformer/reactor may be moved for processing of dispatch to site. | (q) During the stage Inspection/FAT, test results/readings & test connections shall be recorded and mailed to the utility’s/ purchaser’s inspector. (r) The manufacturer has to prepare test report on daily basis during testing period by the end of each day. Test Reports must be issued by the testing in charge of manufacturer indicating list of Tests carried out and the test results. (s) For long duration tests (Temperature rise and partial discharge and impulse), manufacturer shall ensure that Cameras shall be provided near transformer/reactor under test and the Power analyser or equipment’s computer so that the readings can be seen simultaneously. (t) After completion of inspection, OEMs representative should sign off from the application. (u) After getting stage inspection Clearance from utility/purchaser, the transformer/reactor may be moved to next stage of manufacturing process and after getting FAT Clearance from utility/purchaser, the transformer/reactor may be moved for processing of dispatch to site. | (r) The manufacturer has to prepare test report on daily basis during testing period by the end of each day | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 121 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0290 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Troubleshooting | Inspection | TROUBLESHOOTING | (v) All video recording of the inspection shall be done and it shall be shared with the utility / purchaser and also to be maintained by manufacturer/OEM for future reference. (w) The MoM of the stage inspection/FAT shall be prepared by the manufacturer/OEM and all points discussed & agreed including rectification/punch points, completion date etc. shall be communicated to the utility/purchaser. (x) Final Stage inspection report/FAT reports, supporting documents and photographs should be submitted to utility / purchaser for their future reference and record. | (v) All video recording of the inspection shall be done and it shall be shared with the utility / purchaser and also to be maintained by manufacturer/OEM for future reference. (w) The MoM of the stage inspection/FAT shall be prepared by the manufacturer/OEM and all points discussed & agreed including rectification/punch points, completion date etc. shall be communicated to the utility/purchaser. (x) Final Stage inspection report/FAT reports, supporting documents and photographs should be submitted to utility / purchaser for their future reference and record. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (v) All video recording of the inspection shall be done and it shall be shared with the utility / purchaser and also to be maintained by manufacturer/OEM for future reference. (w) The MoM of the stage inspection/FAT shall be prepared by the manufacturer/OEM and all points discussed & agreed including rectification/punch points, completion date etc. shall be communicated to the utility/purchaser. (x) Final Stage inspection report/FAT reports, supporting documents and photographs should be submitted to utility / purchaser for their future reference and record. | Transformers and reactors, 66 kV and above voltage class | PDF p. 122 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0291 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | The online virtual inspection & testing process at manufacturer’s/OEM’s premises will benefit both manufacturer and the utility/purchaser in terms of time, money & manpower/human resources and would be easier and faster. 4.5 The Inspector shall within ten (10) days from the date of inspection as defined herein give notice in writing to the Manufacturer, or any objection to any drawings and all or any equipment and workmanship which is in his opinion not in accordance with the contract. The manufacturer shall give due consideration to such objections and shall either make modifications that may be necessary to meet the said objections or shall inform in writing to the Inspector giving reasons therein, that no modifications are necessary to comply with the contract. | The online virtual inspection & testing process at manufacturer’s/OEM’s premises will benefit both manufacturer and the utility/purchaser in terms of time, money & manpower/human resources and would be easier and faster. 4.5 The Inspector shall within ten (10) days from the date of inspection as defined herein give notice in writing to the Manufacturer, or any objection to any drawings and all or any equipment and workmanship which is in his opinion not in accordance with the contract. The manufacturer shall give due consideration to such objections and shall either make modifications that may be necessary to meet the said objections or shall inform in writing to the Inspector giving reasons therein, that no modifications are necessary to comply with the contract. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 122 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0292 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | General | INSPECTION | 4.6 When the factory tests have been completed successfully at the manufacturer’s or sub-supplier’s works, the Inspector shall issue a certificate to this effect within ten (10) days after completion of tests but if the tests are not witnessed by the Inspector, the certificate shall be issued within ten (10) days of the receipt of the Manufacturer’s test certificate by the Inspector. 4.7 In all cases where the contract provides for tests whether at the premises or works of the Manufacturer or any sub-suppliers, the Manufacturer, except where otherwise specified shall provide free of charge such items as labour, material, electricity, fuel, water, stores, apparatus and instruments as may be reasonably demanded by the Inspector to carry out effectively such tests on the equipment in accordance with the Manufacturer and shall give facilities to the Inspector to accomplish testing. | 4.6 When the factory tests have been completed successfully at the manufacturer’s or sub-supplier’s works, the Inspector shall issue a certificate to this effect within ten (10) days after completion of tests but if the tests are not witnessed by the Inspector, the certificate shall be issued within ten (10) days of the receipt of the Manufacturer’s test certificate by the Inspector. 4.7 In all cases where the contract provides for tests whether at the premises or works of the Manufacturer or any sub-suppliers, the Manufacturer, except where otherwise specified shall provide free of charge such items as labour, material, electricity, fuel, water, stores, apparatus and instruments as may be reasonably demanded by the Inspector to carry out effectively such tests on the equipment in accordance with the Manufacturer and shall give facilities to the Inspector to accomplish testing. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 122 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0293 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | 4.8 The inspection by the Inspector and issue of Inspection Certificate thereon shall in no way limit the liabilities and responsibilities of the manufacturer in respect of the agreed Quality Assurance Programme forming a part of the contract. | 4.8 The inspection by the Inspector and issue of Inspection Certificate thereon shall in no way limit the liabilities and responsibilities of the manufacturer in respect of the agreed Quality Assurance Programme forming a part of the contract. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 122 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0294 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Inspection | SCHEDULE | 4.9 All inspection, measuring and test equipment used by manufacturer shall be calibrated periodically depending on its use and criticality of the test/measurement to be done. The manufacturer shall maintain all the relevant records of periodic calibration and instrument identification, and shall produce the same for inspection by purchaser. In case repair is carried out in the measuring and test equipment it should be compulsorily re- calibrated. All calibrated measuring and test equipment must be properly sealed after calibration to stop any kind of manipulation with the equipment. Wherever mutually agreed between manufacturer & Purchaser, the manufacturer shall re-calibrate the measuring/test equipment in the presence of the Inspector. 4.10 Preparation of inspection report is the concluding part of inspection. Every inspection agency has its own style of preparation of inspection report. However, since it is a quality document, we must ensure that all relevant information and enclosures are made available along with the report. The inspection report has mainly three parts: | NOT COVERED | The manufacturer shall maintain all the relevant records of periodic calibration and instrument identification, and shall produce the same for inspection by purchaser | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 123 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0295 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | quantity offered, sampling, observation noted during inspection, remark on test results etc. b) The second part contains reports on physical verification. c) The third part of the report contains the routine test results of | quantity offered, sampling, observation noted during inspection, remark on test results etc. b) The second part contains reports on physical verification. c) The third part of the report contains the routine test results of | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 123 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0296 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Inspection | Inspection | INSPECTION | the inspected transformers, temperature rise test results, if carried-out, and few demonstrative sample calculations e.g. Load Loss calculation at normal and extreme taps, Temperature rise calculation, Noise level calculation etc. 5.0 INSPECTION AND TESTING | the inspected transformers, temperature rise test results, if carried-out, and few demonstrative sample calculations e.g. Load Loss calculation at normal and extreme taps, Temperature rise calculation, Noise level calculation etc. 5.0 INSPECTION AND TESTING | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 123 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0297 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Inspection | Inspection | INSPECTION | The inspection envisaged by the purchaser is given below. However, the manufacturer shall draw up and carry out a comprehensive inspection and testing programme in the form of detailed quality plan duly approved by Purchaser for necessary implementation during manufacture of the equipment. All accessories and components of transformer shall be purchased from source, approved by the purchaser. All process tests, critical raw material tests and witness/ inspection of these testing shall be carried out as per approved Manufacturing Quality Plan (MQP) by the purchaser. 5.1 Factory Tests | The inspection envisaged by the purchaser is given below. However, the manufacturer shall draw up and carry out a comprehensive inspection and testing programme in the form of detailed quality plan duly approved by Purchaser for necessary implementation during manufacture of the equipment. All accessories and components of transformer shall be purchased from source, approved by the purchaser. All process tests, critical raw material tests and witness/ inspection of these testing shall be carried out as per approved Manufacturing Quality Plan (MQP) by the purchaser. 5.1 Factory Tests | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 123 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0298 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | this document. Complete test report shall be submitted to purchaser after proper scrutiny and signing on each page by the test engineer of the manufacturer. 5.1.2 The manufacturer shall be fully equipped to perform all the required tests as specified. He shall confirm the capabilities of the proposed manufacturing plant in this regard. Any limitations shall be clearly stated. 5.1.3 The manufacturer shall bear all additional costs related to tests which are not possible to carry out at his own works. 5.1.4 In case, any failure observed during factory testing involving winding/ winding shield/ static shield ring, then affected winding of all phases shall be replaced by new one mutually agreed between manufacturer & Purchaser. 5.1.5 Tank Tests (A) Oil Leakage Test | NOT COVERED | NOT VERIFIED | NOT VERIFIED | this document. Complete test report shall be submitted to purchaser after proper scrutiny and signing on each page by the test engineer of the manufacturer. 5.1.2 The manufacturer shall be fully equipped to perform all the required tests as specified. He shall confirm the capabilities of the proposed manufacturing plant in this regard. Any limitations shall be clearly stated. 5.1.3 The manufacturer shall bear all additional costs related to tests which are not possible to carry out at his own works. 5.1.4 In case, any failure observed during factory testing involving winding/ winding shield/ static shield ring, then affected winding of all phases shall be replaced by new one mutually agreed between manufacturer & Purchaser. 5.1.5 Tank Tests (A) Oil Leakage Test | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 124 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0299 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | All tanks and oil filled compartments shall be completely filled with air or oil of a viscosity not greater than that of insulating oil conforming to IEC 60296 at the ambient temperature and subjected to a pressure equal to normal head of oil plus 35 kN/sq.m (5 psi) measured at the base of the tank. This pressure shall be maintained for a period of not less than 12 hours for oil and 1 hour for air during which no leakage shall occur. | All tanks and oil filled compartments shall be completely filled with air or oil of a viscosity not greater than that of insulating oil conforming to IEC 60296 at the ambient temperature and subjected to a pressure equal to normal head of oil plus 35 kN/sq.m (5 psi) measured at the base of the tank. This pressure shall be maintained for a period of not less than 12 hours for oil and 1 hour for air during which no leakage shall occur. | NOT VERIFIED | 12 hours; 1 hour | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 124 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0300 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | All transformer/reactor tanks shall be subjected to the specified vacuum. The tank designed for full vacuum (760 mm of mercury at sea level) shall be tested at an internal pressure of 3.33 KN/Sq.m absolute (25 torr) for one hour. The permanent deflection of flat plate after the vacuum has been released shall not exceed the values specified below: | All transformer/reactor tanks shall be subjected to the specified vacuum. The tank designed for full vacuum (760 mm of mercury at sea level) shall be tested at an internal pressure of 3.33 KN/Sq.m absolute (25 torr) for one hour. The permanent deflection of flat plate after the vacuum has been released shall not exceed the values specified below: | NOT VERIFIED | 760 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 124 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0301 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | All transformer/reactor tanks, its radiator, conservator and other fittings together or separately shall be subjected to a pressure corresponding to twice the normal head of oil or normal oil head pressure plus 35 KN/ sq.m whichever is lower, measured at the base of the tank and maintained for eight hours. The permanent deflection of flat plates after the excess pressure has been released shall not exceed the figure specified above for vacuum test. | All transformer/reactor tanks, its radiator, conservator and other fittings together or separately shall be subjected to a pressure corresponding to twice the normal head of oil or normal oil head pressure plus 35 KN/ sq.m whichever is lower, measured at the base of the tank and maintained for eight hours. The permanent deflection of flat plates after the excess pressure has been released shall not exceed the figure specified above for vacuum test. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 125 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0302 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | 5.2.1 Stage inspection will be carried out by the Inspector on Core, Winding, core-coil assembly & Tank during the manufacturing stages of the transformer/reactor. The manufacturer will have to call for the stage inspection and shall arrange the inspection at manufacturer’s premises or manufacturer’s sub-supplier’s premises, as applicable, free of cost. 5.2.2 Stage inspection will be carried out on at least one Transformer/reactor against an offer of minimum 50% of the ordered quantity as mentioned in delivery schedule. On the basis of satisfactory stage inspection, manufacturer will proceed further. 5.2.3 The manufacturer will offer the core for stage inspection and get approval from purchaser during manufacturing stage. The BIS certified prime core materials are only to be used. The manufacturer has to produce following documents at the time of stage inspection for confirmation of use of prime core materials. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 125 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0303 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | a) Invoice of supplier b) Mills’ approved test certificates c) Packing list d) Bill of lading e) Bill of entry certificate by custom. f) Description of material, electrical analysis, physical inspection, | a) Invoice of supplier b) Mills’ approved test certificates c) Packing list d) Bill of lading e) Bill of entry certificate by custom. f) Description of material, electrical analysis, physical inspection, | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 125 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0304 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | To avoid any possibility of mixing of ‘Prime material’ with any other second grade/ defective material, the imported packed slit coils of CRGO materials shall be opened in the presence of the Inspector. Only after the inspection and approval from | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | To avoid any possibility of mixing of ‘Prime material’ with any other second grade/ defective material, the imported packed slit coils of CRGO materials shall be opened in the presence of the Inspector. Only after the inspection and approval from | Transformers and reactors, 66 kV and above voltage class | PDF p. 125 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0305 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Inspection | SAFETY | purchaser, the core material will be cut in-house or sent to external agency for cutting individual laminations. In case the core is sent to external agency for cutting, the Inspector will have full access to visit such agency for the inspection of the cutting of core. Core material shall be directly procured either from the manufacturer or through their accredited marketing organisation of repute and not through any agent. 5.2.4 Typical example for calculation of flux density, core quantity, no- load loss and weight of copper during stage inspection is given in the Annexure-F. 5.3 Type Tests on fittings | NOT COVERED | NOT VERIFIED | NOT VERIFIED | purchaser, the core material will be cut in-house or sent to external agency for cutting individual laminations. In case the core is sent to external agency for cutting, the Inspector will have full access to visit such agency for the inspection of the cutting of core. Core material shall be directly procured either from the manufacturer or through their accredited marketing organisation of repute and not through any agent. 5.2.4 Typical example for calculation of flux density, core quantity, no- load loss and weight of copper during stage inspection is given in the Annexure-F. 5.3 Type Tests on fittings | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0306 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Following fittings shall conform to type tests and the type test reports shall be furnished along with drawing of the equipment/fittings. | Following fittings shall conform to type tests and the type test reports shall be furnished along with drawing of the equipment/fittings. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0307 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Testing | OLTC | TESTING | test for 400 kV and above voltage class) b) OLTC (Test as per IS 8468/IEC:60214 and degree of protection | test for 400 kV and above voltage class) b) OLTC (Test as per IS 8468/IEC:60214 and degree of protection | NOT VERIFIED | 400 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0308 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | test for IP-55 on Driving mechanism box) c) Buchholz relay d) OTI and WTI e) Pressure Relief Device (including degree of protection test for IP | test for IP-55 on Driving mechanism box) c) Buchholz relay d) OTI and WTI e) Pressure Relief Device (including degree of protection test for IP | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0309 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 55 in terminal box) f) Sudden Pressure Relay (including degree of protection test for | 55 in terminal box) f) Sudden Pressure Relay (including degree of protection test for | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0310 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | IP 55 in terminal box) g) Magnetic Oil Level gauge & Terminal Box degree of protection | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0311 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | test for IP-55. h) Air Cell (Flexible air separator) - Oil side coating, Air side under | test for IP-55. h) Air Cell (Flexible air separator) - Oil side coating, Air side under | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0312 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | cubicle (IP-55 test) j) Bus post Insulators k) Oil pump l) Cooling fan & motor assembly m) RTCC Panel (IP-43 test) 6.0 Pre-Shipment Checks at Manufacturer's Works The following pre-shipment checks shall be done at manufacturer’s works: 6.1 Check for inter-changeability of components of similar transformers/reactors for mounting dimensions. | cubicle (IP-55 test) j) Bus post Insulators k) Oil pump l) Cooling fan & motor assembly m) RTCC Panel (IP-43 test) 6.0 Pre-Shipment Checks at Manufacturer's Works The following pre-shipment checks shall be done at manufacturer’s works: 6.1 Check for inter-changeability of components of similar transformers/reactors for mounting dimensions. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 126 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0313 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | General | INSPECTION | 1g: Start recording 2g: Warning 3g: Alarm Further, drop-out setting shall be 1g and threshold setting shall be in the range of 5g to 10g. 6.4 Check for proper provision for bracing to arrest the movement of core and winding assembly inside the tank. 6.5 Gas tightness test to confirm tightness and record of dew point of dry air inside the tank. Derivation of leakage rate and ensure the adequate reserve dry air capacity. 6.6 Due security arrangements to be ensured during transportation to avoid pilferage and tempering with the valves and other accessories used while dry air filling. | 1g: Start recording 2g: Warning 3g: Alarm Further, drop-out setting shall be 1g and threshold setting shall be in the range of 5g to 10g. 6.4 Check for proper provision for bracing to arrest the movement of core and winding assembly inside the tank. 6.5 Gas tightness test to confirm tightness and record of dew point of dry air inside the tank. Derivation of leakage rate and ensure the adequate reserve dry air capacity. 6.6 Due security arrangements to be ensured during transportation to avoid pilferage and tempering with the valves and other accessories used while dry air filling. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 127 | Chapter-4: Quality Assurance Programme | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0314 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | 1.1. The supplier shall be responsible to select and verify the route, mode of transportation and make all necessary arrangement with the appropriate authorities for the transportation of the equipment. The dimension of the equipment shall be such that when packed for transportation, it shall comply with the requirements of loading and clearance restrictions for the selected route. It shall be the responsibility of the supplier to coordinate the arrangement for transportation of the transformer/reactor for all the stages from the manufacturer’s work to site. 1.2. The supplier shall carry out the route survey along with the transporter and finalise the detail methodology for transportation of transformer/reactor and based on route survey; any modification/extension/improvement to existing road, bridges, culverts etc. if required, shall be in the scope. 1.3. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 129 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0315 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | General | SAFETY | The inland transportation of the transformer/reactor shall be on multi-axel low platform trailers of adequate capacity and equipped with GPS system for tracking the location of transformer at all times during transportation from manufacturer works to designated site. The supplier shall intimate to purchaser about the details of transporter engaged for transportation of the transformer/reactor for tracking the units during transit. Requirement of Hydraulic trailer is envisaged for a load of more than 40 T. The transportation during monsoon period should be avoided as far as possible. 1.4. All metal blanking plates and covers which are specifically required for transportation and storage of the transformer/ reactor shall be considered as part of the transformer/reactor and shall be handed over to the Purchaser after completion of the erection. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The inland transportation of the transformer/reactor shall be on multi-axel low platform trailers of adequate capacity and equipped with GPS system for tracking the location of transformer at all times during transportation from manufacturer works to designated site. The supplier shall intimate to purchaser about the details of transporter engaged for transportation of the transformer/reactor for tracking the units during transit. Requirement of Hydraulic trailer is envisaged for a load of more than 40 T. The transportation during monsoon period should be avoided as far as possible. 1.4. All metal blanking plates and covers which are specifically required for transportation and storage of the transformer/ reactor shall be considered as part of the transformer/reactor and shall be handed over to the Purchaser after completion of the erection. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 129 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0316 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | Bill of quantity of these items shall be included in the relevant drawing/document. 1.5. The supplier shall despatch the transformer/reactor filled | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 129 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0317 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | with dry air conforming to EN 12021 at positive pressure. The necessary arrangement shall be ensured by the supplier to take care of pressure drop of dry air during transit and storage till completion of oil filling during erection. A dry air pressure testing valve with necessary pressure gauge and adaptor valve shall be provided. The duration of the storage of | with dry air conforming to EN 12021 at positive pressure. The necessary arrangement shall be ensured by the supplier to take care of pressure drop of dry air during transit and storage till completion of oil filling during erection. A dry air pressure testing valve with necessary pressure gauge and adaptor valve shall be provided. The duration of the storage of | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 129 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0318 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | transformer/reactor at site with dry air, shall preferably be limited to three months (including the duration of transportation), after which the recommendation of manufacturer is to be followed if it is not filled with oil. The dry air cylinder(s) (with regulating valves) provided to maintain positive pressure can be taken back by the supplier after oil filling. In case turret, having insulation assembly, is transported separately then positive dry air pressure shall be ensured. 1.6. The largest / heaviest package of transformer / reactor shall be sufficiently lashed and same shall be checked before dispatch from the manufacturing unit. 1.7. | transformer/reactor at site with dry air, shall preferably be limited to three months (including the duration of transportation), after which the recommendation of manufacturer is to be followed if it is not filled with oil. The dry air cylinder(s) (with regulating valves) provided to maintain positive pressure can be taken back by the supplier after oil filling. In case turret, having insulation assembly, is transported separately then positive dry air pressure shall be ensured. 1.6. The largest / heaviest package of transformer / reactor shall be sufficiently lashed and same shall be checked before dispatch from the manufacturing unit. 1.7. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 130 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0319 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Failure | SAFETY | Transformer/reactor shall also be fitted with at least 2 numbers Electronic impact recorders (on returnable basis) in diagonally opposite position (to eliminate chances of loss of data to failure of recorder) during transportation to measure the magnitude and duration of the impact in all three directions. The impact recorder shall be mounted on the upper side of the tank (width wise). The acceptance criteria and limits of impact, which can be withstood by the equipment during transportation and handling in all three directions, shall not exceed “3g” for 50 msec (20Hz) or as per OEM standard, whichever is lower. Following setting of impact recorder shall be ensured at the time of installation with transformer/reactor unit before despatch from factory: 1g: Start recording 2g: Warning 3g: Alarm | NOT COVERED | NOT VERIFIED | 20Hz | Transformer/reactor shall also be fitted with at least 2 numbers Electronic impact recorders (on returnable basis) in diagonally opposite position (to eliminate chances of loss of data to failure of recorder) during transportation to measure the magnitude and duration of the impact in all three directions. The impact recorder shall be mounted on the upper side of the tank (width wise). The acceptance criteria and limits of impact, which can be withstood by the equipment during transportation and handling in all three directions, shall not exceed “3g” for 50 msec (20Hz) or as per OEM standard, whichever is lower. Following setting of impact recorder shall be ensured at the time of installation with transformer/reactor unit before despatch from factory: 1g: Start recording 2g: Warning 3g: Alarm | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 130 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0320 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | 2.0 Points to be checked after receipt of transformer/reactor at site in presence of manufacturer’s and purchaser’s representative: 2.1. The transformer/reactor unloading and handling work at site should be carried out by skilled people, under the supervision of manufacturer’s representative. 2.2. A careful external inspection must be made when transformer/reactor arrives at site. Condition of each package | 2.0 Points to be checked after receipt of transformer/reactor at site in presence of manufacturer’s and purchaser’s representative: 2.1. The transformer/reactor unloading and handling work at site should be carried out by skilled people, under the supervision of manufacturer’s representative. 2.2. A careful external inspection must be made when transformer/reactor arrives at site. Condition of each package | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 130 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0321 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | and its contents and visible parts of transformer/reactor etc. shall be checked for any damage and recorded. 2.3. Pressure and Dew point of dry air shall be checked after receipt of transformer/reactor at site. It should be within permissible band as per the graph given in Fig.-1. 2.4. In case of transportation of transformer/reactor in oil filled condition, oil level & leakage (if any) shall be checked. 2.5. In case of any damage or dry air/ oil leakage beyond permissible limit, the manufacturer shall be informed immediately. 2.6. In case of dry air leakage is beyond permissible limit, the dry air pressurisation to be done on a continuous basis to safe guard the transformer Core Coil Assembly (CCA) condition till the problem is located and solved. 2.7. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 131 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0322 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | Transformer Oil | TESTING | Core Insulation Test shall be carried out to check healthiness of insulation between core to tank, core to yoke clamp (frame) and yoke clamp (frame) to tank. (Not applicable for Air Core Reactors) 2.8. In case of transformer transported with oil, a sample of oil should be taken from the bottom of the tank and tested for BDV and moisture content. | Core Insulation Test shall be carried out to check healthiness of insulation between core to tank, core to yoke clamp (frame) and yoke clamp (frame) to tank. (Not applicable for Air Core Reactors) 2.8. In case of transformer transported with oil, a sample of oil should be taken from the bottom of the tank and tested for BDV and moisture content. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 131 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0323 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION | 2.9. The data of impact recorder shall be analysed jointly by the purchaser in association with the manufacturer. In case the impact recorder indicates shocks of ≥ 3g during shipment, further course of action for internal inspection shall be taken jointly by the manufacturer & supplier. Impact Recorder should be detached from the Transformer/ Reactor, preferably after the main unit has been placed on its foundation. | 2.9. The data of impact recorder shall be analysed jointly by the purchaser in association with the manufacturer. In case the impact recorder indicates shocks of ≥ 3g during shipment, further course of action for internal inspection shall be taken jointly by the manufacturer & supplier. Impact Recorder should be detached from the Transformer/ Reactor, preferably after the main unit has been placed on its foundation. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 131 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0324 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | 2.10. Unpacking and inspection of all accessories shall be carried out taking all precautions so that the tools used for opening do not cause damage to the contents. Proper storage of all accessories shall be ensured after unpacking in line with the OEM’s recommendation. Fragile instruments like oil level gauge, temperature indicators, etc. are to be stored indoor. Any damaged or missing components shall be reported to equipment manufacturer and insurance agency so that the same can be investigated or shortage made up as per the terms/ conditions of the contract. All accessories for long storage shall be packed by OEM in special packing case. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 2.10. Unpacking and inspection of all accessories shall be carried out taking all precautions so that the tools used for opening do not cause damage to the contents. Proper storage of all accessories shall be ensured after unpacking in line with the OEM’s recommendation. Fragile instruments like oil level gauge, temperature indicators, etc. are to be stored indoor. Any damaged or missing components shall be reported to equipment manufacturer and insurance agency so that the same can be investigated or shortage made up as per the terms/ conditions of the contract. All accessories for long storage shall be packed by OEM in special packing case. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 131 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0325 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Inspection | INSTALLATION | 3.0 Storage of the main unit and the accessories at site: 3.1 If erection work cannot start immediately due to some reasons, then accessories shall be repacked into their own crates properly and packing list should be retained. 3.2 All packing cases shall be kept above ground by suitable supports so as to allow free air flow underneath. The storage space area shall be such that it is accessible for inspection, water does not collect on or around the area and handling/transport is easy. Proper drainage arrangement in storage areas to be ensured so that in no situation, any component gets submerged in water due to rain, flooding etc. 3.3 It is preferable to store the main unit on its own location/foundation. | 3.0 Storage of the main unit and the accessories at site: 3.1 If erection work cannot start immediately due to some reasons, then accessories shall be repacked into their own crates properly and packing list should be retained. 3.2 All packing cases shall be kept above ground by suitable supports so as to allow free air flow underneath. The storage space area shall be such that it is accessible for inspection, water does not collect on or around the area and handling/transport is easy. Proper drainage arrangement in storage areas to be ensured so that in no situation, any component gets submerged in water due to rain, flooding etc. 3.3 It is preferable to store the main unit on its own location/foundation. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 132 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0326 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Corrective Action | General | CORRECTIVE_ACTION | If the foundation is not likely to be ready for more than three (3) months, then suitable action has to be planned by the responsible agency for proper storage of the Unit as per the recommendation of OEM. 3.4 If the transformer/reactor is to be stored up to three (3) months (including the duration of transportation) after arrival at site, it can be stored with dry air filled condition. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | If the foundation is not likely to be ready for more than three (3) months, then suitable action has to be planned by the responsible agency for proper storage of the Unit as per the recommendation of OEM. 3.4 If the transformer/reactor is to be stored up to three (3) months (including the duration of transportation) after arrival at site, it can be stored with dry air filled condition. | Transformers and reactors, 66 kV and above voltage class | PDF p. 132 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0327 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | Transformer Oil | TESTING | Dry air pressure shall be monitored on daily basis so that chances of exposure of active part to atmosphere may be avoided. In case of drop in dry air pressure, dew point of dry air shall be measured to check the dryness of the transformer/reactor. If there is drop in dew point, fresh dry air need to be filled. Leaks shall be identified and rectified and dry air shall be filled to the required pressure. 3.5 In case the transformer/reactor is to be stored for more than 3 months, it shall be stored in oil filled condition. Processed oil shall be filled which complies with the required specification with moisture content ≤ 5ppm and BDV ≥ 70kV. In case of storage of transformer/reactor in oil-filled condition, the oil filled in the units shall be tested for BDV and moisture contents once in every three months. The oil sample shall be taken from bottom valve. If BDV is less and moisture content is more than as given for service condition, then oil shall be filtered. | Dry air pressure shall be monitored on daily basis so that chances of exposure of active part to atmosphere may be avoided. In case of drop in dry air pressure, dew point of dry air shall be measured to check the dryness of the transformer/reactor. If there is drop in dew point, fresh dry air need to be filled. Leaks shall be identified and rectified and dry air shall be filled to the required pressure. 3.5 In case the transformer/reactor is to be stored for more than 3 months, it shall be stored in oil filled condition. Processed oil shall be filled which complies with the required specification with moisture content ≤ 5ppm and BDV ≥ 70kV. In case of storage of transformer/reactor in oil-filled condition, the oil filled in the units shall be tested for BDV and moisture contents once in every three months. The oil sample shall be taken from bottom valve. If BDV is less and moisture content is more than as given for service condition, then oil shall be filtered. | Dry air pressure shall be monitored on daily basis so that chances of exposure of active part to atmosphere may be avoided | 3 months; 5ppm; 70kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 133 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0328 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | commissioning tests to keep the spare ready for use. The following steps to be followed: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 133 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0329 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Tan Delta | INSTALLATION | of the transformer/reactor. It is advised to carryout Capacitance & Tan delta measurement before erection | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 133 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0330 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | to be erected and driving shaft is to be aligned properly. Conservator of OLTC is also to be erected. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 134 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0331 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Transformer Oil | TESTING | Oil sample is to be drawn from oil drums for testing of various parameters. The oil is to be filled in the transformer tank as per standard procedure and is to be circulated to obtain the required parameter. | Oil sample is to be drawn from oil drums for testing of various parameters. The oil is to be filled in the transformer tank as per standard procedure and is to be circulated to obtain the required parameter. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 134 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0332 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | circulation is completed, oil sample need to be sent to any NABL accredited oil laboratory for testing. The pre- commissioning tests shall be carried out as per Clause No. 12 and the test results are to be forwarded to the OEMs and observations / comments are to be recorded. | circulation is completed, oil sample need to be sent to any NABL accredited oil laboratory for testing. The pre- commissioning tests shall be carried out as per Clause No. 12 and the test results are to be forwarded to the OEMs and observations / comments are to be recorded. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 134 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0333 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | (c) Once the pre-commissioning test results have been reviewed and are acceptable, the bushings are to be removed by lowering the oil and the bushing-openings to be blanked off | (c) Once the pre-commissioning test results have been reviewed and are acceptable, the bushings are to be removed by lowering the oil and the bushing-openings to be blanked off | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 134 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0334 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | with blanking plates. Oil is to be filled up to requisite mark on MOG of temporary conservator provided on main tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 135 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0335 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Alternatively, the transformer/reactor can also be kept in a completely assembled oil-filled condition with all the bushings & conservator erected. In this case all the bushings as well as the main tank of the equipment should be shorted and earthed. In case the spare transformer/reactor is stored in an area not shielded/protected against lightening, arrangement may be made for a temporary lightening mast in its vicinity. (d) Following actions are required during storage of the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 135 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0336 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE |  Oil parameters are to be checked every six (6) month and record is to be maintained.  Circulation of oil is to be carried out every six months to keep the oil in healthy condition. BDV and moisture values are to be checked and maintained after filtration.  The condition of the dehydrating material silica gel is to be checked every three (3) month. The colour of silica gel shall be blue. In case the colour of 50 % of volume of silica gel is found to be pink, the same should be replaced/re-generated.  Manual operation of OLTC is to be exercised every six months for all Taps (applicable for transformers).  Long duration storage insurance may be taken as per utility’s policy. |  Oil parameters are to be checked every six (6) month and record is to be maintained.  Circulation of oil is to be carried out every six months to keep the oil in healthy condition. BDV and moisture values are to be checked and maintained after filtration.  The condition of the dehydrating material silica gel is to be checked every three (3) month. The colour of silica gel shall be blue. In case the colour of 50 % of volume of silica gel is found to be pink, the same should be replaced/re-generated.  Manual operation of OLTC is to be exercised every six months for all Taps (applicable for transformers).  Long duration storage insurance may be taken as per utility’s policy. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 135 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0337 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing, Substation | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (e) All the spares of the transformer/reactor are to be properly identified and packing list kept ready for transportation of the equipment to any location on emergency basis. Oil tankers are also to be kept available in the substation where spares are stored and when request is received, the oil in the equipment needs to be drained and transported in dry air filled condition. 3.7 Storage of Resin Impregnated Paper (RIP) bushings | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 135 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0338 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (a) Resin Impregnated Paper (RIP) bushing technology offers number of advantages over Oil Impregnated Paper (OIP) bushing. Oil leakage is completely eliminated. Self- extinguishing property of RIP does not allow spread of fire. High thermal strength (because of Class E insulation- 120ºC) provides a large margin to ageing in service. However, these bushings by design are susceptible to absorption of moisture which will affect the dielectric | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 135 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0339 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | strength of the paper used in the manufacturing of bushing. Proper storage of RIP bushings in dry & clean environment and protection against any mechanical damage is essential to keep it healthy. It is advisable to cover the RIP bushing package box with a plastic or tarpaulin sheet to avoid ingress of moisture. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 136 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0340 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (b) The standard package box with cover shall be designed for long term storage of the RIP bushings. The package should always be kept in the covered area to prevent the possibility of ingress of moisture during long term storage. Oil end portion of RIP type bushings shall be fitted with metal housing with positive dry air pressure and a suitable pressure monitoring device shall be fitted on the metal housing during storage to avoid direct contact with moisture with epoxy. The pressure of dry air needs to be maintained in case of leakage of dry air. If any drying agents have been provided along with the RIP bushing, the same must be retained and checked from time to time. | (b) The standard package box with cover shall be designed for long term storage of the RIP bushings. The package should always be kept in the covered area to prevent the possibility of ingress of moisture during long term storage. Oil end portion of RIP type bushings shall be fitted with metal housing with positive dry air pressure and a suitable pressure monitoring device shall be fitted on the metal housing during storage to avoid direct contact with moisture with epoxy. The pressure of dry air needs to be maintained in case of leakage of dry air. If any drying agents have been provided along with the RIP bushing, the same must be retained and checked from time to time. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 136 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0341 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Safety | Bushing | SAFETY | (c) Adequate precautions must also be taken to ensure that the storage of RIP bushing with polymer housing, which is susceptible to attacks by rodents or birds, is done in a rodent/pest-free environment by using PVC coated mesh or any other material for wrapping. Bushings which are kept in storage container can be used even after long term storage without any further testing of the bushing. A photograph of a suitably stored RIP bushing is shown below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (c) Adequate precautions must also be taken to ensure that the storage of RIP bushing with polymer housing, which is susceptible to attacks by rodents or birds, is done in a rodent/pest-free environment by using PVC coated mesh or any other material for wrapping. Bushings which are kept in storage container can be used even after long term storage without any further testing of the bushing. A photograph of a suitably stored RIP bushing is shown below: | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 136 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0342 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | 4.0 Insulating Oil 4.1. When insulating oil is dispatched to site separately, it is usually in sealed steel drums. Oil received in drums must be stored on an elevated platform. Drums are to be placed horizontally with its opening cap in middle. In some of the cases, oil is supplied in tankers also. The oil to be used for filling and topping up must comply with oil specifications given in Technical Specification for acceptance criteria. Oil Samples shall be taken from oil drums/ tanker received at site and sent to NABL accredited oil Lab for oil parameter testing. As high dielectric losses cannot be removed by filter treatment, such lots have to be rejected. If the oil is supplied in railroad or trailer tanks, one or two samples are sufficient. If the oil is delivered in 200 litres drums, the following scheme for checking is recommended. | 4.0 Insulating Oil 4.1. When insulating oil is dispatched to site separately, it is usually in sealed steel drums. Oil received in drums must be stored on an elevated platform. Drums are to be placed horizontally with its opening cap in middle. In some of the cases, oil is supplied in tankers also. The oil to be used for filling and topping up must comply with oil specifications given in Technical Specification for acceptance criteria. Oil Samples shall be taken from oil drums/ tanker received at site and sent to NABL accredited oil Lab for oil parameter testing. As high dielectric losses cannot be removed by filter treatment, such lots have to be rejected. If the oil is supplied in railroad or trailer tanks, one or two samples are sufficient. If the oil is delivered in 200 litres drums, the following scheme for checking is recommended. | NOT VERIFIED | 200 litres | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 137 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0343 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Transformer Oil | SAFETY | In case any doubt arises, number of drums to be checked needs to be increased. However, before filling oil, each drum has to be physically checked for free moisture and appearance. A data sheet shall be maintained indicating the number of drums supplied in each lot and number of drums of each lot used in filling a particular Transformer/ Reactor. The oil test results carried out as above shall also be recorded. The copy of test certificate of routine testing at oil refinery should be available at site for comparison of test results. 4.2. Samples from Oil Drum Check the seals on the drums. The drum shall first be allowed to stand with bung (lid) vertically upwards for at least 24 hours. The area around the bung shall be cleaned and clean glass or brass tube long enough to reach within 10mm of the lower most part of the drum shall be inserted, keeping the uppermost end of the tube sealed with the thumb while doing so. Remove the thumb thereby allowing oil to enter the bottom of the tube. Reseal the | NOT COVERED | NOT VERIFIED | 24 hours; 10mm | In case any doubt arises, number of drums to be checked needs to be increased. However, before filling oil, each drum has to be physically checked for free moisture and appearance. A data sheet shall be maintained indicating the number of drums supplied in each lot and number of drums of each lot used in filling a particular Transformer/ Reactor. The oil test results carried out as above shall also be recorded. The copy of test certificate of routine testing at oil refinery should be available at site for comparison of test results. 4.2. Samples from Oil Drum Check the seals on the drums. The drum shall first be allowed to stand with bung (lid) vertically upwards for at least 24 hours. The area around the bung shall be cleaned and clean glass or brass tube long enough to reach within 10mm of the lower most part of the drum shall be inserted, keeping the uppermost end of the tube sealed with the thumb while doing so. Remove the thumb thereby allowing oil to enter the bottom of the tube. Reseal the | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 137 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0344 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | tube and extract an oil sample. The first two samples should be discarded. Thereafter, the sample should be released into a suitable receptacle. Samples shall be collected in clean steel bottles. The bottles shall be rinsed with the same oil and shall be without any air bubble. 5.0 Internal Inspection 5.1 Before starting erection, thorough internal inspection of transformer/reactor shall be carried out by engineer along with manufacturer’s representative. 5.2 Internal inspection shall preferably be carried out in dry and sunny weather along with circulation of dry air (With working person inside the tank, a minimum of 20 cfm/0.56 cubic- meter/minute of breathable air and additional 5 cfm/0.14 cubic-meter/minute for each additional person should be purged in the tank. | tube and extract an oil sample. The first two samples should be discarded. Thereafter, the sample should be released into a suitable receptacle. Samples shall be collected in clean steel bottles. The bottles shall be rinsed with the same oil and shall be without any air bubble. 5.0 Internal Inspection 5.1 Before starting erection, thorough internal inspection of transformer/reactor shall be carried out by engineer along with manufacturer’s representative. 5.2 Internal inspection shall preferably be carried out in dry and sunny weather along with circulation of dry air (With working person inside the tank, a minimum of 20 cfm/0.56 cubic- meter/minute of breathable air and additional 5 cfm/0.14 cubic-meter/minute for each additional person should be purged in the tank. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 138 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0345 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Inspection | SAFETY | Entry of person inside the tank should be avoided if adequate space is not available as in case of smaller rating of transformer.) using dry air generator of dew point -400 C or better and shall be completed as quickly as possible to avoid ingress of moisture. If the Ambient humidity exceeds 65 % the internal inspection is to be avoided. 5.3 Prior to making any entry into the transformer/reactor tank, a foreign material exclusion programme shall be established to avoid the danger of any foreign objects falling into the transformer/reactor: | NOT COVERED | NOT VERIFIED | 400 C | Entry of person inside the tank should be avoided if adequate space is not available as in case of smaller rating of transformer.) using dry air generator of dew point -400 C or better and shall be completed as quickly as possible to avoid ingress of moisture. If the Ambient humidity exceeds 65 % the internal inspection is to be avoided. 5.3 Prior to making any entry into the transformer/reactor tank, a foreign material exclusion programme shall be established to avoid the danger of any foreign objects falling into the transformer/reactor: | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 138 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0346 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Inspection | INSPECTION |  Loose articles should be removed from the pockets of anyone working on the transformer/reactor cover.  All jewelry, watches, pens, coins and knives should be removed from pockets.  Protective clothing and clean shoe covers are recommended.  Tools should be tied with clean cotton tape or cord securely fastened.  Plated tools or tools with parts that may become detached should be avoided.  An inventory of all parts taken into transformer/reactor should be recorded and checked before closing inspection cover to assure all items were removed. |  Loose articles should be removed from the pockets of anyone working on the transformer/reactor cover.  All jewelry, watches, pens, coins and knives should be removed from pockets.  Protective clothing and clean shoe covers are recommended.  Tools should be tied with clean cotton tape or cord securely fastened.  Plated tools or tools with parts that may become detached should be avoided.  An inventory of all parts taken into transformer/reactor should be recorded and checked before closing inspection cover to assure all items were removed. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 138 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0347 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | 5.4 The inspection should include:  Removal of any shipping, blocking or temporary support.  Examination for indication of core shifting. | 5.4 The inspection should include:  Removal of any shipping, blocking or temporary support.  Examination for indication of core shifting. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 138 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0348 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT | Current Transformer | Commissioning | Transformer Oil | COMMISSIONING |  Tests for unintentional core or core clamp grounds.  Visual inspection of windings, leads, and connections including clamping, bracing, blocking, spacer alignment, phase barriers, oil boxes, and coil wraps.  Inspection of De-energized Tap Changer (DETC) and in-tank On-Load Tap Changers (LTCs) including contact alignment and pressure.  Inspection of current transformers including supports and wiring harness.  Checks for dirt, metal particles, moisture, or other foreign material.  Any other suspected damage based on impact recorder readings In case of any abnormality noticed during internal inspection, same shall be referred to manufacturer immediately before starting erection activities. Detailed photographs of all visible parts/ components as per above shall be taken during internal inspection and shall be attached with pre-commissioning report. |  Tests for unintentional core or core clamp grounds.  Visual inspection of windings, leads, and connections including clamping, bracing, blocking, spacer alignment, phase barriers, oil boxes, and coil wraps.  Inspection of De-energized Tap Changer (DETC) and in-tank On-Load Tap Changers (LTCs) including contact alignment and pressure.  Inspection of current transformers including supports and wiring harness.  Checks for dirt, metal particles, moisture, or other foreign material.  Any other suspected damage based on impact recorder readings In case of any abnormality noticed during internal inspection, same shall be referred to manufacturer immediately before starting erection activities. Detailed photographs of all visible parts/ components as per above shall be taken during internal inspection and shall be attached with pre-commissioning report. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 139 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0349 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Transformer Oil | SAFETY | 6.0 Precautions during erection 6.1 During all erection activities, a well-qualified and experienced representative of manufacturer shall be present at the site for supervision and other necessary activities. 6.2 During erection, efforts shall be made to minimize the exposure of active parts (core and coils) of transformer/ reactor. Moisture may condense on any surface cooler than the surrounding air. Excessive moisture in insulation or dielectric liquid lowers its dielectric strength and may cause a failure of transformer/ reactor. 6.3 Further, either dry air generator or dry air cylinders should be used all the time to minimize ingress of moisture. The transformer/reactor should be sealed/blanked and pressurised after working hours. Transformer/reactor shall never be allowed to be opened without application of dry air. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 6.0 Precautions during erection 6.1 During all erection activities, a well-qualified and experienced representative of manufacturer shall be present at the site for supervision and other necessary activities. 6.2 During erection, efforts shall be made to minimize the exposure of active parts (core and coils) of transformer/ reactor. Moisture may condense on any surface cooler than the surrounding air. Excessive moisture in insulation or dielectric liquid lowers its dielectric strength and may cause a failure of transformer/ reactor. 6.3 Further, either dry air generator or dry air cylinders should be used all the time to minimize ingress of moisture. The transformer/reactor should be sealed/blanked and pressurised after working hours. Transformer/reactor shall never be allowed to be opened without application of dry air. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 139 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0350 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | 6.4 It is advisable to apply a slight overpressure with dry air inside the main tank to the tune of 30 kPa (0.3 atmospheres) at the end of the day. Next day the pressure shall be checked and suspected leaks is to be detected with leak detection instruments or with soap water or with plastic bags tightened around valves (being inflated by leaking air) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 139 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0351 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | 6.5 For oil-filled units, whenever oil is drained out below the inspection covers, job shall be treated as exposed. Other exposure activities are as below: | 6.5 For oil-filled units, whenever oil is drained out below the inspection covers, job shall be treated as exposed. Other exposure activities are as below: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 140 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0352 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Installation | Bushing | INSTALLATION |  Bushing erection  Internal jumper connections of Bushings  Fixing bushing turrets  Core insulation checking (in case the checking point not accessible outside)  Buchholz relay pipe work fixing on cover  Gas release pipes/equaliser pipe fixing  Entering inside the tank for connections/inspection etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 140 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0353 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | For oil filled units depending upon the level up to which the oil is drained decides the exposure time. All such exposure time should be recorded in a log sheet to decide the oil processing (drying) and oil filling of transformer/reactor. | For oil filled units depending upon the level up to which the oil is drained decides the exposure time. All such exposure time should be recorded in a log sheet to decide the oil processing (drying) and oil filling of transformer/reactor. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 140 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0354 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | 6.6 "GET THE TRANSFORMER AND REACTOR UNDER OIL AS SOON AS POSSIBLE!" It is good practice to proceed with the erection in such a sequence that all fittings and auxiliaries with oil seals to the tank are assembled first. The oil filling will then be performed as easily as possible. The "active part" inside - core and coils - is then impregnated and protected. It has good time to soak properly, before the unit shall be energized, while remaining fittings are assembled on the unit, and commissioning checks carried out. 6.7 For transformer/reactor with a gas pressure of 2.5-3 PSI, the acceptable limits of dew point shall be as under: | 6.6 "GET THE TRANSFORMER AND REACTOR UNDER OIL AS SOON AS POSSIBLE!" It is good practice to proceed with the erection in such a sequence that all fittings and auxiliaries with oil seals to the tank are assembled first. The oil filling will then be performed as easily as possible. The "active part" inside - core and coils - is then impregnated and protected. It has good time to soak properly, before the unit shall be energized, while remaining fittings are assembled on the unit, and commissioning checks carried out. 6.7 For transformer/reactor with a gas pressure of 2.5-3 PSI, the acceptable limits of dew point shall be as under: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 140 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0355 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Before oil filling is started, a final check is made for the tightness of the transformer/reactor tank by applying vacuum. After vacuum is applied to a transformer/reactor main tank without oil, leakage test must be carried out to ensure that there are no leaks on the tank which would result in ambient air being drawn into the transformer/reactor. The following procedure is to be adopted: | Before oil filling is started, a final check is made for the tightness of the transformer/reactor tank by applying vacuum. After vacuum is applied to a transformer/reactor main tank without oil, leakage test must be carried out to ensure that there are no leaks on the tank which would result in ambient air being drawn into the transformer/reactor. The following procedure is to be adopted: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 141 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0356 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | (Vacuum application and measurement should be performed only on top of the main tank) - A vacuum gauge of McLeod type or electronic type, with a reading range covering the interval of 1 kPa (1-10 mm mercury) to be used.  Connect the vacuum pump to vacuum pulling valve  Evacuate the transformer/ reactor tank until the pressure is | (Vacuum application and measurement should be performed only on top of the main tank) - A vacuum gauge of McLeod type or electronic type, with a reading range covering the interval of 1 kPa (1-10 mm mercury) to be used.  Connect the vacuum pump to vacuum pulling valve  Evacuate the transformer/ reactor tank until the pressure is | NOT VERIFIED | 1-10 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 141 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0357 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | below 50 mbar (5 kPa or about 2 mm of Hg).  Shut the vacuum valve and stop the pump.  Wait for an hour and take a first vacuum reading – say P1.  Take a second reading 30 minutes later- say P2.  Note the volume of the tank (quantity of oil required according | NOT COVERED | NOT VERIFIED | 2 mm; 30 minutes | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 141 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0358 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | the oil quantity V. If the pressures are expressed in kPa, and the oil quantity in m3, then the product shall be less than 3.6. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0359 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | (P2 – P1) x V < 3.6 The transformer/reactor is then considered to be holding sufficient vacuum and is tight. Continue taking readings (for at least 2 to 3 hours) at successive 30 min intervals to confirm the result.  If the leak test is successful, the vacuum pump shall be | (P2 – P1) x V < 3.6 The transformer/reactor is then considered to be holding sufficient vacuum and is tight. Continue taking readings (for at least 2 to 3 hours) at successive 30 min intervals to confirm the result.  If the leak test is successful, the vacuum pump shall be | NOT VERIFIED | 3 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0360 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | continued to run, until the pressure has come down to 0.13 kPa (1 Torr) or less. The vacuum shall then be held/maintained at that level for the duration as given in Table-2 before the oil filling starts.  If the specified vacuum cannot be reached, or if it does not | continued to run, until the pressure has come down to 0.13 kPa (1 Torr) or less. The vacuum shall then be held/maintained at that level for the duration as given in Table-2 before the oil filling starts.  If the specified vacuum cannot be reached, or if it does not | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0361 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Installation | OLTC | INSTALLATION | In case the transformer is provided with an On Load Tap Changer (OLTC), while evacuating the main transformer tank, the pressure inside the diverter switch compartment is also be equalised with main tank so that both are evacuated simultaneously and no undue pressure is allowed on the tap changer chamber. While releasing vacuum, the tap changer chamber vacuum should also be released simultaneously. For this one pressure equalizer pipe should be connected between main tank and tap changer. Manufacturer’s instruction manual shall be referred to protect the air cell/diaphragm in the conservator during evacuation. | In case the transformer is provided with an On Load Tap Changer (OLTC), while evacuating the main transformer tank, the pressure inside the diverter switch compartment is also be equalised with main tank so that both are evacuated simultaneously and no undue pressure is allowed on the tap changer chamber. While releasing vacuum, the tap changer chamber vacuum should also be released simultaneously. For this one pressure equalizer pipe should be connected between main tank and tap changer. Manufacturer’s instruction manual shall be referred to protect the air cell/diaphragm in the conservator during evacuation. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0362 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | This vacuum must be maintained for the time specified as per the voltage class in Table-2 before and should also be maintained during the subsequent oil filling operations by continuous running of the vacuum pumps. | This vacuum must be maintained for the time specified as per the voltage class in Table-2 before and should also be maintained during the subsequent oil filling operations by continuous running of the vacuum pumps. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0363 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | 7.0 Drying of wet winding of transformer/reactor by application of vacuum, dry nitrogen gas filling and heating | 7.0 Drying of wet winding of transformer/reactor by application of vacuum, dry nitrogen gas filling and heating | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0364 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Commissioning | SAFETY | The drying of a new transformer/reactor is required on the first commissioning and when the moisture gets absorbed by the solid insulation used in transformer/reactor due to various reasons. The process of drying out a transformer/reactor requires care and good judgment. If the drying out process is carelessly or improperly performed, a great damage may result to the transformer/reactor insulation. In no case shall a transformer/reactor be left unattended during any part of the dry out period unless on-line dry-out process is adopted which incorporates all necessary safety features. The | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The drying of a new transformer/reactor is required on the first commissioning and when the moisture gets absorbed by the solid insulation used in transformer/reactor due to various reasons. The process of drying out a transformer/reactor requires care and good judgment. If the drying out process is carelessly or improperly performed, a great damage may result to the transformer/reactor insulation. In no case shall a transformer/reactor be left unattended during any part of the dry out period unless on-line dry-out process is adopted which incorporates all necessary safety features. The | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 142 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0365 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Safety | Transformer Oil | SAFETY | When the transformer/reactor is being dried out, it is necessary to ensure that firefighting equipment is available near the transformer/reactor as a precaution as there are chances of fire as we are dealing with heat and inflammable oil. 7.1 Isolation Required | NOT COVERED | NOT VERIFIED | NOT VERIFIED | When the transformer/reactor is being dried out, it is necessary to ensure that firefighting equipment is available near the transformer/reactor as a precaution as there are chances of fire as we are dealing with heat and inflammable oil. 7.1 Isolation Required | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 143 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0366 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | All the openings of transformer/reactor main tank like openings for coolers/radiators, conservator, OLTC etc. are to be properly isolated and totally blanked. 7.2 Procedure | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 143 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0367 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | are to be installed around the transformer/reactor tank. The heaters are to be kept ON till a temperature of about 75oC– 80oC of the core & winding of transformer/reactor is achieved as measured by top oil temperature in the transformer/reactor. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 143 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0368 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | (c) After ascertaining that there is no leakage, the vacuum pulling on the transformer/reactor tank is to be started until absolute vacuum (1-5 torr) is achieved and the same is to be maintained for about 48 hours (minimum)running the vacuum pump continuously. The duration of vacuum can vary between 48 to 96 hrs., depending upon the dew point being achieved. During the running of Vacuum pump, the condensate shall be collected for measurement. Observe the rate of condensate collection on hourly basis. Depending on the value of rate of condensate (less than 40 ml/hr for 24 hrs), continuation of further vacuum shall be decided. | (c) After ascertaining that there is no leakage, the vacuum pulling on the transformer/reactor tank is to be started until absolute vacuum (1-5 torr) is achieved and the same is to be maintained for about 48 hours (minimum)running the vacuum pump continuously. The duration of vacuum can vary between 48 to 96 hrs., depending upon the dew point being achieved. During the running of Vacuum pump, the condensate shall be collected for measurement. Observe the rate of condensate collection on hourly basis. Depending on the value of rate of condensate (less than 40 ml/hr for 24 hrs), continuation of further vacuum shall be decided. | NOT VERIFIED | 48 hours; 40 ml | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 143 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0369 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | General | INSTALLATION | point of Nitrogen at the inlet is to be measured and should be of the order of - 50 C or better. Develop the pressure of Nitrogen upto the positive pressure of 0.15 kg/cm2 and maintain it for 24 hours. Heating from outside is to be continued while Nitrogen circulation is in progress. Then the Nitrogen pressure is released and the dew point of air at the outlet is measured. If the dew point is within acceptable limits as per Table-I, then the dryness of transformer/reactor is achieved. In case the required dew point is not achieved, the transformer/reactor is subjected to vacuum treatment for 48 hours (minimum). The dry Nitrogen gas is pressurised, maintained for 24 hours and the dew point is measured. The cycle is to be repeated till desired dew point as per Table-1 is achieved. | point of Nitrogen at the inlet is to be measured and should be of the order of - 50 C or better. Develop the pressure of Nitrogen upto the positive pressure of 0.15 kg/cm2 and maintain it for 24 hours. Heating from outside is to be continued while Nitrogen circulation is in progress. Then the Nitrogen pressure is released and the dew point of air at the outlet is measured. If the dew point is within acceptable limits as per Table-I, then the dryness of transformer/reactor is achieved. In case the required dew point is not achieved, the transformer/reactor is subjected to vacuum treatment for 48 hours (minimum). The dry Nitrogen gas is pressurised, maintained for 24 hours and the dew point is measured. The cycle is to be repeated till desired dew point as per Table-1 is achieved. | NOT VERIFIED | 24 hours; 48 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 144 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0370 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | (e) Duration of vacuum cycle may vary between 48-96 hrs. Initially two dry Nitrogen gas cycles may be kept for 24 hrs. Afterwards it may be kept for 48 hrs., depending upon dew point being achieved. 7.3 After completion of drying process, oil filling and hot oil circulation is to be carried out before commissioning. Please ensure standing time as per Table-2 given below before charging. | (e) Duration of vacuum cycle may vary between 48-96 hrs. Initially two dry Nitrogen gas cycles may be kept for 24 hrs. Afterwards it may be kept for 48 hrs., depending upon dew point being achieved. 7.3 After completion of drying process, oil filling and hot oil circulation is to be carried out before commissioning. Please ensure standing time as per Table-2 given below before charging. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 144 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0371 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | After the completion of standing time, air release operation is to be carried out in Buchholz relays, turrets and other release points given by the manufacturers before charging. If the transformer has oil pumps, then the oil pumps are to be operated for a duration of 10 minutes before conducting the air release. | NOT COVERED | NOT VERIFIED | 10 minutes | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 145 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0372 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Transformer Oil | TESTING | Once the oil is tested from the drums and found meeting the requirements, the oil is transferred to oil storage tank for oil filtration before filling inside the transformer. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 145 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0373 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | Before being used, the tanks and hoses shall be visually inspected inside for cleanness. Any residual oil from earlier use shall be carefully removed, and the tank is flushed with a small quantity of new oil, which is then discarded. | Before being used, the tanks and hoses shall be visually inspected inside for cleanness. Any residual oil from earlier use shall be carefully removed, and the tank is flushed with a small quantity of new oil, which is then discarded. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 145 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0374 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | After filtration, particle count shall be done (Limiting value for the particle count are 1000 particle/100 ml with size ≥ 5 μm; 130 particle/100 ml with size ≥ 15 μm.) and oil sample is tested for meeting specification for new oil. | After filtration, particle count shall be done (Limiting value for the particle count are 1000 particle/100 ml with size ≥ 5 μm; 130 particle/100 ml with size ≥ 15 μm.) and oil sample is tested for meeting specification for new oil. | NOT VERIFIED | 100 ml | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 145 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0375 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | For transformer/reactor dispatched with dry air filled from the works, the filling of oil inside the tank shall be done under vacuum. Transformer/reactor of high voltage ratings and their tanks are designed to withstand full vacuum. Manufacturer’s instructions should be followed regarding application of full vacuum during filling the oil in the tank. | For transformer/reactor dispatched with dry air filled from the works, the filling of oil inside the tank shall be done under vacuum. Transformer/reactor of high voltage ratings and their tanks are designed to withstand full vacuum. Manufacturer’s instructions should be followed regarding application of full vacuum during filling the oil in the tank. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 145 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0376 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | When filling a transformer/reactor with oil it is preferable that the oil be pumped into the bottom of the tank through a filter press or other reliable oil drying and cleaning device should be interposed between the pump and the tank (please refer Fig.- 2). The oil flow at the entry valve must be controlled to maintain a positive pressure above atmospheric and to limit the flow rate if necessary to 5000 litres/hour, or a rise in oil level in the tank | When filling a transformer/reactor with oil it is preferable that the oil be pumped into the bottom of the tank through a filter press or other reliable oil drying and cleaning device should be interposed between the pump and the tank (please refer Fig.- 2). The oil flow at the entry valve must be controlled to maintain a positive pressure above atmospheric and to limit the flow rate if necessary to 5000 litres/hour, or a rise in oil level in the tank | NOT VERIFIED | 5000 litres | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 145 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0377 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Continue oil filling until the level reaches approximately 200 mm above the ambient oil level indicated on the magnetic oil level gauge in the expansion vessel. Then, release the vacuum, with dry air of dew point -40o C or better (for > 220 kV, -25o C for others). | Continue oil filling until the level reaches approximately 200 mm above the ambient oil level indicated on the magnetic oil level gauge in the expansion vessel. Then, release the vacuum, with dry air of dew point -40o C or better (for > 220 kV, -25o C for others). | NOT VERIFIED | 200 mm; 220 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 146 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0378 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | The diverter tank can now be topped up at atmospheric pressure. Reconnect oil outlet hose to valve on flange on tap changer diverter head. Reinstate breather and very slowly top up the diverter switch such that the correct level is reached in the diverter expansion vessel. In the event the expansion vessel is overfull drain oil from flange into a suitable container until the correct level is reached. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The diverter tank can now be topped up at atmospheric pressure. Reconnect oil outlet hose to valve on flange on tap changer diverter head. Reinstate breather and very slowly top up the diverter switch such that the correct level is reached in the diverter expansion vessel. In the event the expansion vessel is overfull drain oil from flange into a suitable container until the correct level is reached. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 146 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0379 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | When the oil filling, under vacuum of the transformer/reactor main tank and diverter tank, is complete, the cooling system/ radiator bank can be filled (without vacuum) at atmospheric | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 146 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0380 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | pressure, via an oil processing plant. Oil must be admitted, very slowly, through the bottom cooler filter valve and the top cooler filter valve with air release valve kept open to atmosphere. As the oil level reaches the top vent, then top valve and air release valve are to be closed and the processing plant can be shut down. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 147 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0381 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Corrective Action | Transformer Oil | CORRECTIVE_ACTION | Note: Care must be taken not to pressurize the coolers/radiators. Upon completion, open the top cooler isolating valve in order to equalize the pressure in the cooler with the transformer/reactor tank. This will also allow contraction or expansion of the oil as the ambient temperature changes. Before filling oil into the conservator, the air cell/bellow to be inflated to 0.5 PSIG i.e. 0.035 kg/cm2 max. or upto the value recommended by the manufacturer by applying pressure (N2/Compressed dry air) so that it can take shape. After releasing pressure, breather pipe is to be fitted however it is recommended not to fit breather in position, instead a wire mesh guard may be connected over the flange of the pipe to prevent entry of any insect inside the pipe. This will ensure free air movement from the air cell to the atmosphere. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Note: Care must be taken not to pressurize the coolers/radiators. Upon completion, open the top cooler isolating valve in order to equalize the pressure in the cooler with the transformer/reactor tank. This will also allow contraction or expansion of the oil as the ambient temperature changes. Before filling oil into the conservator, the air cell/bellow to be inflated to 0.5 PSIG i.e. 0.035 kg/cm2 max. or upto the value recommended by the manufacturer by applying pressure (N2/Compressed dry air) so that it can take shape. After releasing pressure, breather pipe is to be fitted however it is recommended not to fit breather in position, instead a wire mesh guard may be connected over the flange of the pipe to prevent entry of any insect inside the pipe. This will ensure free air movement from the air cell to the atmosphere. | Transformers and reactors, 66 kV and above voltage class | PDF p. 147 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0382 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Use flow meter/indicator on outlet of filter machine and regulate the flow using the valve to limit oil filling rate to 2000 litres per hour max. in case filter capacity is more. Oil to be pushed slowly into conservator through the transformer/reactor via valve No. 5 (valve 2, 3 & 4 to remain open) till the oil comes out first through valve Nos. 2 & 3 (close these valves) and then through valve No. 4. Allow some oil to come out through valve No.4. Oil should come out freely into the atmosphere. This will ensure that air inside the conservator is expelled out and the space surrounding the air cell is full of oil. Close valve No. 4. During all these operations valve No.1 shall be in closed position. | Use flow meter/indicator on outlet of filter machine and regulate the flow using the valve to limit oil filling rate to 2000 litres per hour max. in case filter capacity is more. Oil to be pushed slowly into conservator through the transformer/reactor via valve No. 5 (valve 2, 3 & 4 to remain open) till the oil comes out first through valve Nos. 2 & 3 (close these valves) and then through valve No. 4. Allow some oil to come out through valve No.4. Oil should come out freely into the atmosphere. This will ensure that air inside the conservator is expelled out and the space surrounding the air cell is full of oil. Close valve No. 4. During all these operations valve No.1 shall be in closed position. | NOT VERIFIED | 2000 litres | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 147 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0383 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Excess oil from the conservator is to be drained by gravity only through valve No. 1 or through drain valve of the transformer/reactor via valve No. 5. Do not use filter machine for draining oil from the conservator. Also do not remove Buchholz relay and its associated pipe work, fitted between the conservator and the transformer/reactor tank while draining oil. Stop draining oil till indicator of magnetic oil level gauge reaches position-2 on the dial, which is corresponding to 30C reading on the oil temperature indicator. Fill the conservator according to the oil temperature and not the atmospheric temperature. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 147 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0384 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | After Oil filling, Hot Oil Circulation has to be applied to the transformers/reactors except under the circumstances when active part of transformer/reactor gets wet. Following conditions can be considered to define the transformer/reactor wet: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 148 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0385 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | erection (Overexposure when exposure > 12 Hrs) Under above mentioned conditions, manufacturer shall take necessary action for effective dry out of the Transformer/ Reactor. The oil sample from the transformer/reactor tank, after filling in tank before commissioning should meet the parameters specified in the specification elsewhere. 9.0 Hot oil circulation using high vacuum oil filter machine | erection (Overexposure when exposure > 12 Hrs) Under above mentioned conditions, manufacturer shall take necessary action for effective dry out of the Transformer/ Reactor. The oil sample from the transformer/reactor tank, after filling in tank before commissioning should meet the parameters specified in the specification elsewhere. 9.0 Hot oil circulation using high vacuum oil filter machine | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 148 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0386 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | To ensure proper dryness and absorption of possible trapped gas bubbles, the oil in the tank is circulated through the vacuum filter as shown in Fig.-4. The circulation procedure for the main tank is as follows: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | To ensure proper dryness and absorption of possible trapped gas bubbles, the oil in the tank is circulated through the vacuum filter as shown in Fig.-4. The circulation procedure for the main tank is as follows: | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 148 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0387 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (a) The transformer/reactor is connected to the oil filter machine in a loop through the top and bottom filter valves. The direction of circulation shall be from the transformer/reactor to the filter at the bottom and from the filter to the transformer/reactor at the top. (Please note that at the initial oil filling time, the direction is reverse to avoid air bubble formation). | (a) The transformer/reactor is connected to the oil filter machine in a loop through the top and bottom filter valves. The direction of circulation shall be from the transformer/reactor to the filter at the bottom and from the filter to the transformer/reactor at the top. (Please note that at the initial oil filling time, the direction is reverse to avoid air bubble formation). | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 149 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0388 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (b) The temperature of the oil from the filter to the transformer/reactor should be around 60o C and in no case it should go beyond 70o C otherwise this may cause oxidation of oil. (c) The circulation shall proceed until a volume of oil corresponding to 2 times the total oil volume in the tank has passed through the loop. (At freezing ambient temperature the circulation time is increased: circulate 3 times the volume at temperature down to minus 20o C, increase to 4 times below that temperature). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 149 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0389 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Safety | Transformer Oil | SAFETY | (a) Keep recommended fire extinguishers at site. (b) During hot oil circulation, keep fire extinguisher ready near transformer. (c) Carry out all pre-commissioning test and final commissioning check as elaborated in this document before energizing transformer. (d) Take precaution while handling PRV devices having heavy springs in compression to safeguard person and system. (e) Provide adequately rated cables & fuses. (f) Never apply voltage when transformer is under vacuum (g) Oil spillage shall be inspected regularly and attended, if any. Oil shall not be allowed to fall on ground. (h) Keep all combustible items at safe distance to reduce risk of fire. (i) No welding work shall be taken up near transformer. (j) Welding on oil filled transformer shall be avoided as far as possible. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | (a) Keep recommended fire extinguishers at site. (b) During hot oil circulation, keep fire extinguisher ready near transformer. (c) Carry out all pre-commissioning test and final commissioning check as elaborated in this document before energizing transformer. (d) Take precaution while handling PRV devices having heavy springs in compression to safeguard person and system. (e) Provide adequately rated cables & fuses. (f) Never apply voltage when transformer is under vacuum (g) Oil spillage shall be inspected regularly and attended, if any. Oil shall not be allowed to fall on ground. (h) Keep all combustible items at safe distance to reduce risk of fire. (i) No welding work shall be taken up near transformer. (j) Welding on oil filled transformer shall be avoided as far as possible. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 150 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0390 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing, Switchyard | NOT VERIFIED | Safety | Transformer Oil | SAFETY | If, under special circumstances, welding is absolutely necessary, it shall be done as per instruction of manufacturer only. (k) All erection personnel must use Personal Protective Equipment like, helmet, safety shoe, boiler suit, etc. (l) Electrical equipment like filter machine, dry air generator etc., must be earthed. (m) First Aid box shall be kept ready at site. (n) Adequate lighting must be available for clear visibility (o) Cordon off the working area, particularly when transformer augmentation work in a switchyard is taken up. (p) All major erection activity like bushing, conservator and radiators must be carried out with crane of adequate capacity and boom size. (q) Never carry out work with unskilled workers. (r) Safety posters, like “No Smoking”, “Wear Helmet”, etc., must be displayed. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | If, under special circumstances, welding is absolutely necessary, it shall be done as per instruction of manufacturer only. (k) All erection personnel must use Personal Protective Equipment like, helmet, safety shoe, boiler suit, etc. (l) Electrical equipment like filter machine, dry air generator etc., must be earthed. (m) First Aid box shall be kept ready at site. (n) Adequate lighting must be available for clear visibility (o) Cordon off the working area, particularly when transformer augmentation work in a switchyard is taken up. (p) All major erection activity like bushing, conservator and radiators must be carried out with crane of adequate capacity and boom size. (q) Never carry out work with unskilled workers. (r) Safety posters, like “No Smoking”, “Wear Helmet”, etc., must be displayed. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 150 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0391 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | (s) Use approved and tested Earth rods (t) Safety Nodal Officer to make sure that site is cleared on daily basis to prevent fire hazards. | NOT COVERED | tested Earth rods (t) Safety Nodal Officer to make sure that site is cleared on daily basis to prevent fire hazards | NOT VERIFIED | (s) Use approved and tested Earth rods (t) Safety Nodal Officer to make sure that site is cleared on daily basis to prevent fire hazards. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 150 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0392 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Commissioning | SCHEDULE | The Contractor shall prepare a detailed inspection and testing schedule/programme in consultation with the OEM for field activities covering areas right from the receipt of material stage up to commissioning stage and shall got it approved by the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 150 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0393 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | Purchaser. An indicative pre-commissioning checks & test, commissioning check and final energization is given below.. Supplier shall follow purchaser approved Field Quality Plan (FQP). Testing of oil sample at site shall be carried out as per specification. | Purchaser. An indicative pre-commissioning checks & test, commissioning check and final energization is given below.. Supplier shall follow purchaser approved Field Quality Plan (FQP). Testing of oil sample at site shall be carried out as per specification. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 151 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0394 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | Once oil filling is completed, following pre-commissioning checks and tests are performed to ensure the healthiness of the Transformer/ Reactor prior to its energization. The following checks should be carried out before commencement of the pre-commissioning tests: | Once oil filling is completed, following pre-commissioning checks and tests are performed to ensure the healthiness of the Transformer/ Reactor prior to its energization. The following checks should be carried out before commencement of the pre-commissioning tests: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 151 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0395 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC, Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | (a) Ensure that transformer/reactor and its auxiliaries are free from visible defects on physical inspection (b) Ensure cleanliness of transformer/reactor and the surrounding areas (c) Ensure that all fittings are as per out line General Arrangement Drawing (d) Ensure that bushings are clean and free from physical damages (e) Ensure that oil level is correct in all bushings (f) Ensure that oil level in Main/OLTC Conservator tank in MOG is as desired. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (a) Ensure that transformer/reactor and its auxiliaries are free from visible defects on physical inspection (b) Ensure cleanliness of transformer/reactor and the surrounding areas (c) Ensure that all fittings are as per out line General Arrangement Drawing (d) Ensure that bushings are clean and free from physical damages (e) Ensure that oil level is correct in all bushings (f) Ensure that oil level in Main/OLTC Conservator tank in MOG is as desired. | Transformers and reactors, 66 kV and above voltage class | PDF p. 151 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0396 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Bushing | NOT VERIFIED | Maintenance Schedule | Tan Delta | SCHEDULE | (g) Ensure gear box oil level in OLTC (h) Ensure that OTI and WTI pockets are filled with transformer oil (i) Ensure that cap in the tan delta measurement point in the bushing is tight and grounded (j) Ensure unused secondary cores of Bushing CT’s, if any, has been shorted (k) Ensure CT secondary star point has been formed properly and grounded at one end only as per scheme (l) Ensure that Buchholz Relay is correctly mounted with arrow pointing towards conservator (m) Ensure all power and control cable terminals are tightened (n) Ensure all cables and ferrules are provided with number as per cable schedule (o) Ensure that external cabling from junction box to relay/control panel is completed (p) Ensure operation of cooling fans, oil pumps etc. (q) Ensure correct operation of all protection devices and alarms/trip: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 151 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0397 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | iv) Excessive winding temperature v) Excessive oil temperature vi) Low oil flow vii) Low oil level indication viii) Fan and pump failure protection (as applicable) (r) Check for the adequate protection on the electric circuit supplying the accessories. (s) Ensure operation of OLTC manually & electrically at local and remotely by RTCC/BCU/SAS (t) Ensure that indication of tap position on Diverter switch, Drive mechanism & RTCC are same. (u) Ensure working of numerical AVR (v) Ensure that the cable glands have been packed properly. The unused holes if any have also been blanked. The following pre-commissioning tests shall be carried out before energization: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | iv) Excessive winding temperature v) Excessive oil temperature vi) Low oil flow vii) Low oil level indication viii) Fan and pump failure protection (as applicable) (r) Check for the adequate protection on the electric circuit supplying the accessories. (s) Ensure operation of OLTC manually & electrically at local and remotely by RTCC/BCU/SAS (t) Ensure that indication of tap position on Diverter switch, Drive mechanism & RTCC are same. (u) Ensure working of numerical AVR (v) Ensure that the cable glands have been packed properly. The unused holes if any have also been blanked. The following pre-commissioning tests shall be carried out before energization: | Transformers and reactors, 66 kV and above voltage class | PDF p. 152 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0398 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Safety | Tan Delta | SAFETY | i) Control wiring ii) Cooling system motor and control circuit iii) Main windings (PI & DAI) iv) Tap changer motor and control (as applicable) (b) Test on Bushing CTs (c) 2 kV for 1 minute test between bushing CT terminal and earth (d) Polarity and vector group test (for transformer) (e) Ratio test on all taps (for transformer) (f) Magnetising current test (g) Magnetic balance test (for 3 phase transformer/reactor) (h) Capacitance and Tan delta measurement of winding and bushing (i) Tan delta of bushing at variable frequency (Dielectric frequency response) (j) Frequency response analysis (FRA). (k) Measurement of vibration and noise level (for reactor) (l) Short circuit impedance test (m) Contact resistance measurement (n) Measurement of resistance of all windings on all steps of the tap changer (o) Protection relay settings (p) Measurement of safety clearances (q) Measurement of earth pit resistance | NOT COVERED | NOT VERIFIED | 2 kV; 1 minute | i) Control wiring ii) Cooling system motor and control circuit iii) Main windings (PI & DAI) iv) Tap changer motor and control (as applicable) (b) Test on Bushing CTs (c) 2 kV for 1 minute test between bushing CT terminal and earth (d) Polarity and vector group test (for transformer) (e) Ratio test on all taps (for transformer) (f) Magnetising current test (g) Magnetic balance test (for 3 phase transformer/reactor) (h) Capacitance and Tan delta measurement of winding and bushing (i) Tan delta of bushing at variable frequency (Dielectric frequency response) (j) Frequency response analysis (FRA). (k) Measurement of vibration and noise level (for reactor) (l) Short circuit impedance test (m) Contact resistance measurement (n) Measurement of resistance of all windings on all steps of the tap changer (o) Protection relay settings (p) Measurement of safety clearances (q) Measurement of earth pit resistance | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 152 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0399 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Switchyard, Fire Protection | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | 13.0 Final commissioning checks The following commissioning checks should be carried out before energization of the transformer/ reactor: (a) All the pre-commissioning test results of unit are verified and compared with factory results before commissioning. (b) No leakage of oil in any part of unit. (c) Ensure safe electrical clearance of conductor jumpers in the switchyard with transformer/ reactor body, gantry, column, jumpers, fire wall etc. (d) Ensure that tertiary winding terminals are insulated, when they are not used/ connected to any system. (e) Ensure earthing of Neutral, main tank body, radiator frame structure, fans and motor. (f) Neutral earthing conductor of suitable size must run through support insulator and connected to two separate earthing pits which are in turn connected to main earth mat of switchyard. | 13.0 Final commissioning checks The following commissioning checks should be carried out before energization of the transformer/ reactor: (a) All the pre-commissioning test results of unit are verified and compared with factory results before commissioning. (b) No leakage of oil in any part of unit. (c) Ensure safe electrical clearance of conductor jumpers in the switchyard with transformer/ reactor body, gantry, column, jumpers, fire wall etc. (d) Ensure that tertiary winding terminals are insulated, when they are not used/ connected to any system. (e) Ensure earthing of Neutral, main tank body, radiator frame structure, fans and motor. (f) Neutral earthing conductor of suitable size must run through support insulator and connected to two separate earthing pits which are in turn connected to main earth mat of switchyard. | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 153 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0400 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC, Bushing, Switchyard | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (g) Ensure that conductor jumpers connected to HV, LV and tertiary terminals are not tight and should have the allowance for contraction. Also ensure that connectors are properly tightened at bushing terminal. (h) Ensure that R.Y.B designated terminals of transformer/ reactor are matching with R,Y,B buses of switchyards on HV and LV side. (i) Ensure oil level in the Bushings. (j) Ensure continuity of OLTC operation at all taps. (k) In a transformer bank of three single phase units, ensure master-slave OLTC scheme. (l) In a transformer bank of three single phase units, ensure tertiary connection and protection scheme (if provided). (m) Ensure oil filling in conservator tank according to temperature scale in MOG and also ensure oil level in prismatic glass. (n) Ensure that all valves between main tank and radiator banks are opened. | (g) Ensure that conductor jumpers connected to HV, LV and tertiary terminals are not tight and should have the allowance for contraction. Also ensure that connectors are properly tightened at bushing terminal. (h) Ensure that R.Y.B designated terminals of transformer/ reactor are matching with R,Y,B buses of switchyards on HV and LV side. (i) Ensure oil level in the Bushings. (j) Ensure continuity of OLTC operation at all taps. (k) In a transformer bank of three single phase units, ensure master-slave OLTC scheme. (l) In a transformer bank of three single phase units, ensure tertiary connection and protection scheme (if provided). (m) Ensure oil filling in conservator tank according to temperature scale in MOG and also ensure oil level in prismatic glass. (n) Ensure that all valves between main tank and radiator banks are opened. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 153 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0401 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | Power Transformer | Design / Technical Reference | OLTC | DESIGN_REFERENCE | (o) Ensure those radiator valves connected to header are open. (p) Ensure that valve to conservator tank via Buchholz relay is open. (q) Ensure physical operation of local protections like Buchholz, PRV, Surge relay of OLTC etc. (r) Ensure OTI and WTI settings of fan & pumps operation, Alarm and Trip as per approved drawings. Fan and pump operation shall be ensured locally and remotely. (s) Review and ensure protection scheme of power transformer/ reactor with over all protection scheme at remote end in control room. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 153 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0402 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | For Transformer:  Differential Protection  Restricted Earth Fault (REF) Protection.  Over current and Earth fault protection / impedance | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | For Transformer:  Differential Protection  Restricted Earth Fault (REF) Protection.  Over current and Earth fault protection / impedance | Transformers and reactors, 66 kV and above voltage class | PDF p. 154 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0403 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Condition Monitoring | Transformer Oil | CONDITION_MONITORING | protection.  Over fluxing Protection  Tertiary Protection (if applicable)  Over load alarm  OTI & WTI- alarm and trip  RTCC panel/relay interface with protection system  Local protection like Buchholz, PRV etc.  MOG-low oil alarm  Integration of on-line condition monitoring equipment (if | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 154 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0404 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | For Reactor:  Differential Protection  Restricted Earth Fault (REF) Protection.  Reactor backup protection (impedance protection/ Over | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | For Reactor:  Differential Protection  Restricted Earth Fault (REF) Protection.  Reactor backup protection (impedance protection/ Over | Transformers and reactors, 66 kV and above voltage class | PDF p. 154 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0405 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | current and Earth fault protection)  OTI & WTI- alarm and trip  Local protection like Buchholz, PRV etc.  MOG-low oil alarm  Integration of on-line condition monitoring equipment (if | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | current and Earth fault protection)  OTI & WTI- alarm and trip  Local protection like Buchholz, PRV etc.  MOG-low oil alarm  Integration of on-line condition monitoring equipment (if | Transformers and reactors, 66 kV and above voltage class | PDF p. 154 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0406 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC, Bushing, Fire Protection | NOT VERIFIED | Safety | Tan Delta | SAFETY | applicable). (t) Ensure the common earthing of tank, frame and core provided in transformer. (u) Ensure the shorting of spare cores of bushing CT’s. (v) Ensure that cap in the tan delta measurement point in the bushing is put back. (w) Ensure Fire Protection System and oil drain valve operation before charging and commissioning. (x) Oil test results after filtration must be within specified limit. (y) Spares like bushings shall be tested and kept ready before charging and commissioning. (z) Allow minimum period of 24 hrs. after filtration for oil temperature to settle down. (aa) Ensure release of air from plugs provided on top of main tank, conservator and radiator headers. (bb) Take charging clearance certificate from all erection agencies for removal of man, material and T&P from site. (cc) Ensure healthiness of Air Cell. (dd) Ensure availability of oil in the breather cup in main tank/ OLTC tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | applicable). (t) Ensure the common earthing of tank, frame and core provided in transformer. (u) Ensure the shorting of spare cores of bushing CT’s. (v) Ensure that cap in the tan delta measurement point in the bushing is put back. (w) Ensure Fire Protection System and oil drain valve operation before charging and commissioning. (x) Oil test results after filtration must be within specified limit. (y) Spares like bushings shall be tested and kept ready before charging and commissioning. (z) Allow minimum period of 24 hrs. after filtration for oil temperature to settle down. (aa) Ensure release of air from plugs provided on top of main tank, conservator and radiator headers. (bb) Take charging clearance certificate from all erection agencies for removal of man, material and T&P from site. (cc) Ensure healthiness of Air Cell. (dd) Ensure availability of oil in the breather cup in main tank/ OLTC tank. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 154 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0407 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, CVT | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | (ee) Ensure all rollers are locked with rails if transformer is on rollers (ff) Ensure door seals of Marshalling Box are intact and all cable gland plate’s unused holes are sealed. (gg) Ensure change over operation of AC supply from source- I to source-II in local master control cubicle. (hh) Ensure that all associated equipment of the bay e.g. CB, Isolator/Earth switch, CT/PT/CVT etc. has been checked properly as per OEM’s recommendations and utility practice. 14.0 Energization of transformer/ reactor Commissioning of transformer / reactor is not complete unless it is put into regular service. Following activities to follow: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 155 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0408 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, GIS, OLTC | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | (a) Perform DGA just before commissioning (b) Initially charge the transformer under no load. (c) Continuously observe the transformer operation at no load for at least 24 hours. (d) Gradually put the transformer on load, check and measure increase in temperature in relation to the load and check the operation with respect to temperature rise (monitor OTI & WTI), vibration, oil leakage, oil level indicators & gas detector relay and noise level etc. (e) Check OLTC operation. (f) Carry out Thermo-vision scanning of HV/LV terminals and tank body.[This test should be carried out once the transformer/reactor is stabilised and operating at higher temperature (> 60 deg.C)] (g) Carry out DGA of oil after 24 hours, one week, 15 days, one month & 3 months of energisation at site, thereafter as per normal frequency of 6 months / as and when required based on the trend analysis. Contractor shall prepare a comprehensive commissioning report and hand over testing and commissioning records to operation staff for future reference and record. | NOT COVERED | NOT VERIFIED | 24 hours; 15 days; 3 months; 6 months | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 155 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0409 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | Analysis (FRA) of the transformer/reactor. Transformers while experiencing severity of short circuit current loses its mechanical property by way of deformation of the winding or core. During pre-commissioning this test is required to ascertain by comparison with the factory results that transformer/reactor active part has not suffered any severe impact/ jerk during transportation. | Analysis (FRA) of the transformer/reactor. Transformers while experiencing severity of short circuit current loses its mechanical property by way of deformation of the winding or core. During pre-commissioning this test is required to ascertain by comparison with the factory results that transformer/reactor active part has not suffered any severe impact/ jerk during transportation. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 158 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0410 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, GIS, Substation, Switchyard | NOT VERIFIED | Commissioning | GIS | COMMISSIONING | 16.0 Flow chart for erection activities All test records of FAT, tests at site & pre-commissioning tests before energisation of the transformer/reactor shall be kept in digital form for future reference & record and should also be available with operation staff of substation/switchyard for ready reference. | 16.0 Flow chart for erection activities All test records of FAT, tests at site & pre-commissioning tests before energisation of the transformer/reactor shall be kept in digital form for future reference & record and should also be available with operation staff of substation/switchyard for ready reference. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 159 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0411 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | Oil filling in main tank from oil storage tank under vacuum through filter machine (Previously filtered and stored in oil storage tank with desired value | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 160 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0412 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | 1) Oil Samples for DGA shall be taken at intervals of 24 hrs, 1 week, 15 days,1 month and then 3 month after commissioning and thereafter as per periodic maintenance schedule. 2) PT Values shall be between 1.5 to 2.2 3) All bolts to be tightened as per the torque value provided by OEM. 4) Never exceed oil temperature beyond 60degree C during oil processing. 5) Oil BDV and PPM shall be more than 70KV and less than 5 respectively. 6) Fill the oil in conservator tank as per the temperature scale in MOG. 7) Settling time: i) 66KV: 24hrs ii) 132KV: 36hrs iii) 220KV: 48hrs iv) 400KV: 48hrs 8) Refer OEM manual for details of equipment handling, erection and testing. 9) Set WTI/ OTI and fans/ pumps operation as per approved drawing. 10) Ensure that no bushing core CT’s are left open circuit and tan delta caps are in place. 11) Ensure tank, core and frame earthing. | NOT COVERED | eek, 15 days,1 month and then 3 month after commissioning and thereafter as per periodic maintenance schedule | 15 days; 1 month; 3 month; 70KV; 66KV; 132KV; 220KV; 400KV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 160 | Chapter-5: Transportation, Erection, Testing and Commissioning | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0413 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Electrical equipment deterioration phenomena are related to electric, thermal, mechanical, chemical, environmental and combined stresses. Hence, failure of transformers/reactors could be due to insulation failure, or thermal failure, or mechanical failure or combination of these. Due to frequent system faults, over loading, environmental effect, unexpected continuous operating voltage and over voltage stresses of the system during the operation, many equipment fails much before their expected life span. There is no escape from normal long term ageing process but premature failure can be avoided by proper maintenance. Preventive maintenance is the key to keeping equipment healthy and in service. The most cost-effective maintenance approach is the one, which gives a high level of reliability while keeping maintenance cost minimum. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Electrical equipment deterioration phenomena are related to electric, thermal, mechanical, chemical, environmental and combined stresses. Hence, failure of transformers/reactors could be due to insulation failure, or thermal failure, or mechanical failure or combination of these. Due to frequent system faults, over loading, environmental effect, unexpected continuous operating voltage and over voltage stresses of the system during the operation, many equipment fails much before their expected life span. There is no escape from normal long term ageing process but premature failure can be avoided by proper maintenance. Preventive maintenance is the key to keeping equipment healthy and in service. The most cost-effective maintenance approach is the one, which gives a high level of reliability while keeping maintenance cost minimum. | Transformers and reactors, 66 kV and above voltage class | PDF p. 162 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0414 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | The type of maintenance practices usually being followed by various utilities is conventional Time-Based Maintenance (TBM) or Corrective Maintenance (CM) or Condition-Based Maintenance (CBM) or Reliability Centred Maintenance (RCM). Different maintenance strategies (TBM/CM/CBM/RCM) have different impact on Life Cycle Cost (LCC) of equipment. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 162 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0415 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | TBM practice is based on concept of preventive maintenance in pre- defined intervals. Unfortunately, as maintenance interval is increased, the equipment reliability is compromised. Condition-Based Maintenance (CBM) program offers an attractive option to overcome the shortcoming of traditional TBM. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 162 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0416 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | planning a major maintenance/overhaul  Reduces maintenance cost  Defers capital and maintenance expenditure  Reduces forced outages of equipment  Improves safety of operating personnel, reliability and quality of | NOT COVERED | NOT VERIFIED | NOT VERIFIED | planning a major maintenance/overhaul  Reduces maintenance cost  Defers capital and maintenance expenditure  Reduces forced outages of equipment  Improves safety of operating personnel, reliability and quality of | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 162 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0417 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | For reliable operation of vital assets like transformers/reactors, it is necessary to identify problem at early stage before a catastrophic failure occurs. The Condition Based Maintenance (CBM), which has become accepted approach world over, has also gained acceptance by Indian utilities. Condition Monitoring for any device is defined as “A generic procedure/activities directed towards identifying and avoiding root cause failure modes.” Condition monitoring activities can be described as the process of monitoring a parameter in the equipment, in order to identify a significant change which is indicative of a developing fault. It is a major component of predictive maintenance. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | For reliable operation of vital assets like transformers/reactors, it is necessary to identify problem at early stage before a catastrophic failure occurs. The Condition Based Maintenance (CBM), which has become accepted approach world over, has also gained acceptance by Indian utilities. Condition Monitoring for any device is defined as “A generic procedure/activities directed towards identifying and avoiding root cause failure modes.” Condition monitoring activities can be described as the process of monitoring a parameter in the equipment, in order to identify a significant change which is indicative of a developing fault. It is a major component of predictive maintenance. | Transformers and reactors, 66 kV and above voltage class | PDF p. 163 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0418 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Switchyard | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | In the factory, the transformer/reactor can be tested using a plethora of means and at all voltage ranges. However, at site the testing options are severely limited. Since transformers/reactors play an important role in the electrical power system it is imperative to conduct testing on a regular basis. The goal of testing is to confirm the transformer’s/reactor’s ability to continue functioning properly and to reduce the chance of failure. The test should be carried out using reliable and calibrated testing instruments of proven credentials having accuracy of repeatability. The equipment should be properly shielded for immunity from electromagnetic induction effect encountered in the switchyard. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | In the factory, the transformer/reactor can be tested using a plethora of means and at all voltage ranges. However, at site the testing options are severely limited. Since transformers/reactors play an important role in the electrical power system it is imperative to conduct testing on a regular basis. The goal of testing is to confirm the transformer’s/reactor’s ability to continue functioning properly and to reduce the chance of failure. The test should be carried out using reliable and calibrated testing instruments of proven credentials having accuracy of repeatability. The equipment should be properly shielded for immunity from electromagnetic induction effect encountered in the switchyard. | Transformers and reactors, 66 kV and above voltage class | PDF p. 163 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0419 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Substation, Switchyard | NOT VERIFIED | Condition Monitoring | General | CONDITION_MONITORING | As per Central Electricity Authority (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations, diagnostic equipment shall be employed to assess the health of various equipment in substations and switchyards of 132 kV and higher voltages. Portable type on-line diagnostic equipment and off- line diagnostic equipment shall be provided for one or a cluster of substations or switchyards, depending upon the size of the substations or switchyards. On-line diagnostic equipment may be provided for the critical equipment, the health of which is to be monitored continuously. | NOT COVERED | NOT VERIFIED | 132 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 163 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0420 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Failure | SAFETY | Utilities can also follow Reliability Centred Maintenance (RCM) practice. RCM is a structured process that identifies the effects of failures and defines the appropriate maintenance path for managing their impacts. RCM identifies the most technically and economically effective approach to maintenance. It is an optimised strategy that takes into account not only the operation time and/or the technical condition of an asset, but also its position in the network, its operational importance, any potential safety or environmental risk arising from its failure and any likely consequence of its potential outage. An important transformer serving many power consumers may require a higher level of maintenance than when a backup unit is available in an emergency. The extent of maintenance to be performed on a transformer is proportional to the level of risk associated with the unit. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Utilities can also follow Reliability Centred Maintenance (RCM) practice. RCM is a structured process that identifies the effects of failures and defines the appropriate maintenance path for managing their impacts. RCM identifies the most technically and economically effective approach to maintenance. It is an optimised strategy that takes into account not only the operation time and/or the technical condition of an asset, but also its position in the network, its operational importance, any potential safety or environmental risk arising from its failure and any likely consequence of its potential outage. An important transformer serving many power consumers may require a higher level of maintenance than when a backup unit is available in an emergency. The extent of maintenance to be performed on a transformer is proportional to the level of risk associated with the unit. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 164 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0421 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Commissioning | SAFETY | In practice, the criticality index is usually combined with a health index to prioritise maintenance activity. RCM may be applied to components either together or in isolation. RCM can not only improve the reliability of the system but also can reduce the required maintenance significantly resulting in significant reduction in O&M cost. 2.0 Conventional Tests for Condition Monitoring The following conventional tests on transformers/reactors are carried out at site and the test results are compared to the factory test results/pre-commissioning results. Acceptable values and frequency of carrying out these tests has been specified in the table in Appendix given at the end of the chapter. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | In practice, the criticality index is usually combined with a health index to prioritise maintenance activity. RCM may be applied to components either together or in isolation. RCM can not only improve the reliability of the system but also can reduce the required maintenance significantly resulting in significant reduction in O&M cost. 2.0 Conventional Tests for Condition Monitoring The following conventional tests on transformers/reactors are carried out at site and the test results are compared to the factory test results/pre-commissioning results. Acceptable values and frequency of carrying out these tests has been specified in the table in Appendix given at the end of the chapter. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 164 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0422 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Winding Resistance | FAILURE_ANALYSIS | 2.1 Winding Resistance Measurement Winding resistance is measured in the field in order to check for any abnormalities due to loose connections, broken strands and high contact resistance in tap changers etc. as a pre-commissioning checks & after a failure event and the measured values are compared with the factory test values. As the resistance of transformer/reactor winding is low, the measurement has to be carried out with the help of Kelvin Double Bridge/Transformer ohmmeter. Normally winding resistance values 1 ohm or above is measured using Wheatstone Bridge and winding resistance values less than 1 ohm is measured using micro-ohm meter or Kelvin Bridge. | NOT COVERED | NOT VERIFIED | 1 ohm | NOT COVERED | 2.1 Winding Resistance Measurement Winding resistance is measured in the field in order to check for any abnormalities due to loose connections, broken strands and high contact resistance in tap changers etc. as a pre-commissioning checks & after a failure event and the measured values are compared with the factory test values. As the resistance of transformer/reactor winding is low, the measurement has to be carried out with the help of Kelvin Double Bridge/Transformer ohmmeter. Normally winding resistance values 1 ohm or above is measured using Wheatstone Bridge and winding resistance values less than 1 ohm is measured using micro-ohm meter or Kelvin Bridge. | Transformers and reactors, 66 kV and above voltage class | PDF p. 164 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0423 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Winding Resistance | TESTING | The winding resistance measurement shall preferably be done when the difference in the top and bottom temperature of the winding (temperature of oil in steady-state condition) is equal to or less than 5C. The winding resistance measurement should preferably be carried out after completion of all other LV tests, as after this test core gets saturated. The tests like magnetizing current, magnetic balance etc. carried out after winding resistance measurement test may be affected and indicate a misleading results, if the core is not de-magnetized before carrying out these tests. For star connected winding with neutral brought out, the resistance shall be measured between the line and neutral terminal and average of three sets of reading shall be considered the tested value. | The winding resistance measurement shall preferably be done when the difference in the top and bottom temperature of the winding (temperature of oil in steady-state condition) is equal to or less than 5C. The winding resistance measurement should preferably be carried out after completion of all other LV tests, as after this test core gets saturated. The tests like magnetizing current, magnetic balance etc. carried out after winding resistance measurement test may be affected and indicate a misleading results, if the core is not de-magnetized before carrying out these tests. For star connected winding with neutral brought out, the resistance shall be measured between the line and neutral terminal and average of three sets of reading shall be considered the tested value. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 165 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0424 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Bushing | TESTING | If neutral bushing is not available on Star connected windings, measurement shall be taken between each phase and ground (if the neutral is grounded), or between pairs of bushings as if it were a Delta connected winding. In future, test shall be repeated in same fashion so that proper comparison can be made. The connections shall be as shown: | If neutral bushing is not available on Star connected windings, measurement shall be taken between each phase and ground (if the neutral is grounded), or between pairs of bushings as if it were a Delta connected winding. In future, test shall be repeated in same fashion so that proper comparison can be made. The connections shall be as shown: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 165 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0425 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Testing | DGA | TESTING | Where Rt = Resistance measured at winding temperature t degree C Results are to be compared to other phases in Star-connected transformers/reactors or between pairs of terminals on a Delta– connected winding to determine if resistance value is too high. Because field measurements make it unlikely that precise temperature measurements of the winding can be made, the expected deviation for this test in the field is 5.0 % of the factory test value. Precision in field measurements using digital instruments is affected by the presence of stray fields of relatively low capacitances. Comparison of readings with identical units has much more significance. As a check, Key gases increasing in DGA in case of close connections or broken strands or OLTC contact problems, will be ethane and/or ethylene and possibly methane. | Where Rt = Resistance measured at winding temperature t degree C Results are to be compared to other phases in Star-connected transformers/reactors or between pairs of terminals on a Delta– connected winding to determine if resistance value is too high. Because field measurements make it unlikely that precise temperature measurements of the winding can be made, the expected deviation for this test in the field is 5.0 % of the factory test value. Precision in field measurements using digital instruments is affected by the presence of stray fields of relatively low capacitances. Comparison of readings with identical units has much more significance. As a check, Key gases increasing in DGA in case of close connections or broken strands or OLTC contact problems, will be ethane and/or ethylene and possibly methane. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 166 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0426 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | 2.2 Voltage Ratio Test (only for transformers) Voltage Ratio Test is carried out in case any fault has occurred which is suspected to have affected one of the windings (completely or partially). The turns ratio of a transformer is the ratio of the number of turns in a higher voltage winding to that in a lower voltage winding. To carry out the test, keep the tap position in the lowest position and IV and LV terminals open. Apply 3 phase, 415 V or single phase 230 V supply depending on transformer type on HV terminals. Measure the voltages applied on each phase (Phase-Phase) on HV and IV/LV (as applicable) terminals simultaneously. Repeat this for each of the tap position separately and after interchanging the voltmeters of HV and IV/LV (as applicable) windings and then average the readings for final calculation of ratio. | NOT COVERED | NOT VERIFIED | 415 V; 230 V | NOT COVERED | 2.2 Voltage Ratio Test (only for transformers) Voltage Ratio Test is carried out in case any fault has occurred which is suspected to have affected one of the windings (completely or partially). The turns ratio of a transformer is the ratio of the number of turns in a higher voltage winding to that in a lower voltage winding. To carry out the test, keep the tap position in the lowest position and IV and LV terminals open. Apply 3 phase, 415 V or single phase 230 V supply depending on transformer type on HV terminals. Measure the voltages applied on each phase (Phase-Phase) on HV and IV/LV (as applicable) terminals simultaneously. Repeat this for each of the tap position separately and after interchanging the voltmeters of HV and IV/LV (as applicable) windings and then average the readings for final calculation of ratio. | Transformers and reactors, 66 kV and above voltage class | PDF p. 166 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0427 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Transformer Oil | TESTING | The above tests can also be performed by using Transformer Turns Ratio (TTR) meter available in convenient portable/hand-held form. They operate at low voltages, such as 8-10 V and 50-60 Hz, so that the test can be performed on a transformer even when the oil is removed. Two windings on one phase of a transformer are connected to the instrument, and the internal bridge elements are varied to produce a null indication on the detector, the exciting current is also being measured in most cases. | The above tests can also be performed by using Transformer Turns Ratio (TTR) meter available in convenient portable/hand-held form. They operate at low voltages, such as 8-10 V and 50-60 Hz, so that the test can be performed on a transformer even when the oil is removed. Two windings on one phase of a transformer are connected to the instrument, and the internal bridge elements are varied to produce a null indication on the detector, the exciting current is also being measured in most cases. | NOT VERIFIED | 8-10 V; 50-60 Hz | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 166 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0428 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Results of the transformation turns or voltage ratio are absolute, and may be compared with the specified values measured during factory testing. The turns ratio tolerance should be within 0.5% of the nameplate specifications. For three phase Y connected winding this tolerance applies to phase to neutral voltage. If the phase-to-neutral voltage is not explicitly indicated in the nameplate, then the rated phase-to-neutral voltage should be calculated by dividing the phase- to-phase voltage by √3. If there are shorted winding turns, the measured ratio will be affected. Out-of-tolerance ratio measurements may be symptomatic of shorted turns, especially if there is an associated high excitation current. | Results of the transformation turns or voltage ratio are absolute, and may be compared with the specified values measured during factory testing. The turns ratio tolerance should be within 0.5% of the nameplate specifications. For three phase Y connected winding this tolerance applies to phase to neutral voltage. If the phase-to-neutral voltage is not explicitly indicated in the nameplate, then the rated phase-to-neutral voltage should be calculated by dividing the phase- to-phase voltage by √3. If there are shorted winding turns, the measured ratio will be affected. Out-of-tolerance ratio measurements may be symptomatic of shorted turns, especially if there is an associated high excitation current. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 167 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0429 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Out- of-tolerance readings should be compared with prior tests because in some instances, the design turns ratio may vary from the nameplate voltage ratio on some taps because of the need to utilize an incremental number of winding turns to make up the taps while nameplate voltage increments may not exactly correspond. This error may combine with measurement error to give a misleading out-of- tolerance reading. Ratio measurements must be made on all taps to confirm the proper alignment and operation of the tap changers. Open turns in the excited winding will be indicated by very low exciting current and no output voltage. Open turns in the output winding will be indicated by normal levels of exciting current, but no or very low levels of unstable output voltage. | Out- of-tolerance readings should be compared with prior tests because in some instances, the design turns ratio may vary from the nameplate voltage ratio on some taps because of the need to utilize an incremental number of winding turns to make up the taps while nameplate voltage increments may not exactly correspond. This error may combine with measurement error to give a misleading out-of- tolerance reading. Ratio measurements must be made on all taps to confirm the proper alignment and operation of the tap changers. Open turns in the excited winding will be indicated by very low exciting current and no output voltage. Open turns in the output winding will be indicated by normal levels of exciting current, but no or very low levels of unstable output voltage. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 167 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0430 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Winding Resistance | FAILURE_ANALYSIS | The turns ratio test also detects/indicates high-resistance connections in the lead circuitry or high contact resistance in tap changers by higher excitation current and a difficulty in balancing the bridge during measurement. 2.3 Excitation/Magnetization Current Measurement Exciting/magnetizing current is the current required to force a given flux through the core. Exciting/magnetizing current measurement is carried out to locate defect in magnetic core structure such as shorted laminations or break down of core bolt insulation, turn to turn insulation failure, shifting of winding, problem in tap changer etc. This test should be done before DC measurements of winding resistance to reduce the effect of residual magnetism. Therefore, | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The turns ratio test also detects/indicates high-resistance connections in the lead circuitry or high contact resistance in tap changers by higher excitation current and a difficulty in balancing the bridge during measurement. 2.3 Excitation/Magnetization Current Measurement Exciting/magnetizing current is the current required to force a given flux through the core. Exciting/magnetizing current measurement is carried out to locate defect in magnetic core structure such as shorted laminations or break down of core bolt insulation, turn to turn insulation failure, shifting of winding, problem in tap changer etc. This test should be done before DC measurements of winding resistance to reduce the effect of residual magnetism. Therefore, | Transformers and reactors, 66 kV and above voltage class | PDF p. 167 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0431 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | General | TESTING | transformer/reactor under test is to be demagnetized before commencement of magnetizing current test. The test comprises a simple measurement of single-phase current on one side of the transformer/reactor (usually the high-voltage side in case of a transformer) with the other side left floating (with the exception of a grounded neutral). Three-phase transformers are tested by applying single-phase 10 kV voltage to one phase (HV terminals) at a time. Tap position is kept alternatively in the lowest position, normal position and highest position with IV & LV terminals open. Voltages applied on each phase on HV terminals and current in each phase of HV terminal are measured. The test is repeated for IV winding keeping HV and LV open and measure phase to phase voltage between the IV terminals and current on each of the IV terminals. | transformer/reactor under test is to be demagnetized before commencement of magnetizing current test. The test comprises a simple measurement of single-phase current on one side of the transformer/reactor (usually the high-voltage side in case of a transformer) with the other side left floating (with the exception of a grounded neutral). Three-phase transformers are tested by applying single-phase 10 kV voltage to one phase (HV terminals) at a time. Tap position is kept alternatively in the lowest position, normal position and highest position with IV & LV terminals open. Voltages applied on each phase on HV terminals and current in each phase of HV terminal are measured. The test is repeated for IV winding keeping HV and LV open and measure phase to phase voltage between the IV terminals and current on each of the IV terminals. | NOT VERIFIED | 10 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 168 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0432 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Winding Resistance | FAILURE_ANALYSIS | The set of reading for current measurement in each of the tap position should be equal. Unequal currents shall indicate possible short circuits in winding. Results between similar single-phase units should not vary more than 10 %. The test values on the outside legs should be within 15 % of each other, and values for the centre leg should not be more than those for either of the outside legs for a three-phase transformer. Results compared to previous tests made under the same conditions should not vary more than 25%. The comparison of the test values of healthy condition with the faulty condition shall help in pinpointing the trouble spots. If an out-of-tolerance reading is experienced while turns ratio, winding resistance, and impedance tests are normal, residual magnetism should be suspected. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The set of reading for current measurement in each of the tap position should be equal. Unequal currents shall indicate possible short circuits in winding. Results between similar single-phase units should not vary more than 10 %. The test values on the outside legs should be within 15 % of each other, and values for the centre leg should not be more than those for either of the outside legs for a three-phase transformer. Results compared to previous tests made under the same conditions should not vary more than 25%. The comparison of the test values of healthy condition with the faulty condition shall help in pinpointing the trouble spots. If an out-of-tolerance reading is experienced while turns ratio, winding resistance, and impedance tests are normal, residual magnetism should be suspected. | Transformers and reactors, 66 kV and above voltage class | PDF p. 168 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0433 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, AIS | NOT VERIFIED | Testing | Insulation Resistance | TESTING | Residual magnetism may be eliminated or reduced by applying a DC voltage to the windings through a voltage divider. The voltage should be raised from zero to a maximum value that will yield a current of no more than 10 A through the winding and then returned to zero. Care must be taken not to break the circuit while DC current is flowing in the winding. The polarity should then be reversed and the procedure repeated. Repeat the process several times, each time reducing the magnitude of current and each time reversing the polarity. The excitation current test should then be repeated. 2.4 Insulation Resistance Insulation resistance (IR) of windings is the simplest and most widely used test to check the soundness of transformer/reactor insulation. | Residual magnetism may be eliminated or reduced by applying a DC voltage to the windings through a voltage divider. The voltage should be raised from zero to a maximum value that will yield a current of no more than 10 A through the winding and then returned to zero. Care must be taken not to break the circuit while DC current is flowing in the winding. The polarity should then be reversed and the procedure repeated. Repeat the process several times, each time reducing the magnitude of current and each time reversing the polarity. The excitation current test should then be repeated. 2.4 Insulation Resistance Insulation resistance (IR) of windings is the simplest and most widely used test to check the soundness of transformer/reactor insulation. | NOT VERIFIED | 10 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 168 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0434 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Insulation Resistance | FAILURE_ANALYSIS | This test reveals the condition of insulation (i.e. degree of dryness of paper insulation), presence of any foreign contaminants in oil and also any gross defect inside the transformer/reactor (like failure to remove the temporary transportation bracket on the live portion of tap- changer part). Insulation resistance is measured by means of Megger which is available in 500 V, 1000 V, 2500 V and 5000 V ratings. For transformer/reactor windings with voltage rating 11 kV and above, 2.5 kV megger shall be used. IR value measurements of EHV transformers/reactors shall preferably be done with 5 kV motorized/digital megger. IR measurements shall be taken between the windings collectively (i.e. with all the windings being connected together) and the earthed tank (earth) and between each winding and the tank, the rest of the windings being earthed. Before taking measurements the neutral should be disconnected from earth. Following table gives combinations of IR measurements for auto-transformer, three-winding transformer & Shunt Reactor. | NOT COVERED | NOT VERIFIED | 500 V; 1000 V; 2500 V; 5000 V; 11 kV; 2.5 kV; 5 kV | NOT COVERED | This test reveals the condition of insulation (i.e. degree of dryness of paper insulation), presence of any foreign contaminants in oil and also any gross defect inside the transformer/reactor (like failure to remove the temporary transportation bracket on the live portion of tap- changer part). Insulation resistance is measured by means of Megger which is available in 500 V, 1000 V, 2500 V and 5000 V ratings. For transformer/reactor windings with voltage rating 11 kV and above, 2.5 kV megger shall be used. IR value measurements of EHV transformers/reactors shall preferably be done with 5 kV motorized/digital megger. IR measurements shall be taken between the windings collectively (i.e. with all the windings being connected together) and the earthed tank (earth) and between each winding and the tank, the rest of the windings being earthed. Before taking measurements the neutral should be disconnected from earth. Following table gives combinations of IR measurements for auto-transformer, three-winding transformer & Shunt Reactor. | Transformers and reactors, 66 kV and above voltage class | PDF p. 169 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0435 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | HV + IV to LV HV + IV to LV HV to E HV + IV to E HV to IV+ LV LV to E HV + LV to IV HV + IV +LV to E Date and time of measurement, sl. no., make of megger, oil temperature and IR values at intervals of 15 seconds, 1 minute and 10 minutes should be recorded. IR values may be checked with the values in manufacturer's test certificate and these values may be used as bench marks for future IR monitoring in service. IR values vary with type of insulation (transformer oil or air), temperature, and duration of application of voltage and to some extent applied voltage. Unless otherwise recommended by the manufacturer the following IR values as a thumb rule may be considered as the minimum satisfactory values at 30°C (one minute measurements) at the time of commissioning. | HV + IV to LV HV + IV to LV HV to E HV + IV to E HV to IV+ LV LV to E HV + LV to IV HV + IV +LV to E Date and time of measurement, sl. no., make of megger, oil temperature and IR values at intervals of 15 seconds, 1 minute and 10 minutes should be recorded. IR values may be checked with the values in manufacturer's test certificate and these values may be used as bench marks for future IR monitoring in service. IR values vary with type of insulation (transformer oil or air), temperature, and duration of application of voltage and to some extent applied voltage. Unless otherwise recommended by the manufacturer the following IR values as a thumb rule may be considered as the minimum satisfactory values at 30°C (one minute measurements) at the time of commissioning. | NOT VERIFIED | 1 minute; 10 minutes; 30°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 169 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0436 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | Insulation Resistance | TESTING | 1 minute (Meg ohm) 11kV 500 MΩ 33kV 1000 MΩ 66kV & above 1500 MΩ Even if the insulation is dry, IR values will be low if the resistivity of oil is poor. With the increase in duration of application of voltage, IR value increases. The increase in insulation resistance is an indication of dryness of insulation. The ratio of 60 second insulation resistance to 15 second insulation resistance value is called Dielectric Absorption Coefficient or Index (DAI). For oil filled transformers/reactors with class A insulation, in reasonably dried condition, the absorption coefficient at 30°C will be more than 1.3. 2.5 Polarization Index Test It is a ratiometric test, insensitive to temperature variation and may be used to predict insulation system performance even if charging currents (i.e. capacitive, absorption or leakage currents) have not diminished to zero. | 1 minute (Meg ohm) 11kV 500 MΩ 33kV 1000 MΩ 66kV & above 1500 MΩ Even if the insulation is dry, IR values will be low if the resistivity of oil is poor. With the increase in duration of application of voltage, IR value increases. The increase in insulation resistance is an indication of dryness of insulation. The ratio of 60 second insulation resistance to 15 second insulation resistance value is called Dielectric Absorption Coefficient or Index (DAI). For oil filled transformers/reactors with class A insulation, in reasonably dried condition, the absorption coefficient at 30°C will be more than 1.3. 2.5 Polarization Index Test It is a ratiometric test, insensitive to temperature variation and may be used to predict insulation system performance even if charging currents (i.e. capacitive, absorption or leakage currents) have not diminished to zero. | NOT VERIFIED | 1 minute; 11kV; 500 MΩ; 33kV; 1000 MΩ; 66kV; 1500 MΩ; 30°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 170 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0437 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Polarization Index | TESTING | Since leakage current increases at a faster rate with moisture present than does absorption current, the megohm readings will not increase with time as fast with insulation in poor condition as with insulation in good condition. This results in a lower polarization index. An advantage of the index ratio is that all of the variables that can affect a single megohm reading, such as temperature and humidity, are essentially the same for both the 1 min and 10 min readings. The polarization index test is performed generally by taking megohm readings at the following intervals at a constant DC voltage: 1 min and then every minute up to 10 min. The Polarization Index (PI) is the ratio of the 10 min to the 1 min megohm readings. | Since leakage current increases at a faster rate with moisture present than does absorption current, the megohm readings will not increase with time as fast with insulation in poor condition as with insulation in good condition. This results in a lower polarization index. An advantage of the index ratio is that all of the variables that can affect a single megohm reading, such as temperature and humidity, are essentially the same for both the 1 min and 10 min readings. The polarization index test is performed generally by taking megohm readings at the following intervals at a constant DC voltage: 1 min and then every minute up to 10 min. The Polarization Index (PI) is the ratio of the 10 min to the 1 min megohm readings. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 170 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0438 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Polarization Index | DESIGN_REFERENCE | PI= R10 / R1 Where PI is Polarization Index and R is resistance The following are guidelines for evaluating transformer/reactor insulation using polarization index values: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 170 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0439 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | Polarization Index | SAFETY | Condition Less than 1 Dangerous 1.0-1.1 Poor 1.1-1.25 Questionable 1.25-2.0 Fair 2.0 – 4.0 Good Above 4.0 Excellent A Polarization Index (PI) of more than 1.25 and Dielectric Absorption Index of more than 1.3 are generally considered satisfactory for a transformer/reactor when the results of other low voltage tests are found in order. PI less than 1 calls for immediate corrective action. 2.6 Capacitance and Tan Delta of Windings Dissipation Factor (DF)/Loss factor (Tan δ) and capacitance measurement of winding is carried out to ascertain the general condition of the insulation of the winding of transformer/reactor. For tan delta & capacitance measurement of transformer/reactor winding, the voltage rating of each winding under test must be considered and the test voltage selected accordingly. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Condition Less than 1 Dangerous 1.0-1.1 Poor 1.1-1.25 Questionable 1.25-2.0 Fair 2.0 – 4.0 Good Above 4.0 Excellent A Polarization Index (PI) of more than 1.25 and Dielectric Absorption Index of more than 1.3 are generally considered satisfactory for a transformer/reactor when the results of other low voltage tests are found in order. PI less than 1 calls for immediate corrective action. 2.6 Capacitance and Tan Delta of Windings Dissipation Factor (DF)/Loss factor (Tan δ) and capacitance measurement of winding is carried out to ascertain the general condition of the insulation of the winding of transformer/reactor. For tan delta & capacitance measurement of transformer/reactor winding, the voltage rating of each winding under test must be considered and the test voltage selected accordingly. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 171 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0440 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Capacitance | TESTING | If neutral bushings are involved, their voltage ratings must also be considered in selecting the test voltage. Removal of Jumpers from Bushings is pre-requisite for C & Tan δ measurement of windings. UST mode is used to measure insulation between two ungrounded terminals of the apparatus, isolate an individual section of insulation and test it without measuring other connected insulation. In the GST mode, both leakage paths are measured by the test set. The current, watts loss, and capacitance parameters of the UST and GSTg tests should equal the parameters in the GST test. This gives the overall condition or power factor of the test specimen. The GST Guard (GSTg) tests measures the total current leaking to ground only. In UST mode, ground is considered guard since grounded terminals are not measured and the only current measured is the current flowing on the other two leads. | If neutral bushings are involved, their voltage ratings must also be considered in selecting the test voltage. Removal of Jumpers from Bushings is pre-requisite for C & Tan δ measurement of windings. UST mode is used to measure insulation between two ungrounded terminals of the apparatus, isolate an individual section of insulation and test it without measuring other connected insulation. In the GST mode, both leakage paths are measured by the test set. The current, watts loss, and capacitance parameters of the UST and GSTg tests should equal the parameters in the GST test. This gives the overall condition or power factor of the test specimen. The GST Guard (GSTg) tests measures the total current leaking to ground only. In UST mode, ground is considered guard since grounded terminals are not measured and the only current measured is the current flowing on the other two leads. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 171 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0441 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | Any current flowing to a grounded terminal is bypassed directly to the AC source return. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 171 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0442 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | If the sum of the UST and GSTg parameters do not equal the GST parameters, then either the test set is malfunctioning or the test leads are configured incorrectly. | If the sum of the UST and GSTg parameters do not equal the GST parameters, then either the test set is malfunctioning or the test leads are configured incorrectly. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 172 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0443 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING | The summary of possible combination for measurement of tan delta & capacitance is given below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 172 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0444 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Capacitance | TESTING | Changes in the normal capacitance indicate abnormal conditions such as the presence of moisture, layer short circuits or open circuits in the capacitance network. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 172 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0445 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING |  Chemical deterioration due to time and temperature.  Contamination by water, carbon deposits, bad oil, dirt, etc.  Severe leakage through cracks and over surfaces.  Ionisation Environmental factors like variation in temperature, relative humidity, surrounding charged objects etc. may influence measurement of dielectric dissipation factor. Care shall be taken to control the above factors during measurements. An increase of DF accompanied by a marked increase in capacitance usually indicates excessive moisture in the insulation. Increase of DF alone may be caused by thermal deterioration or by contamination other than water. Maximum values of Dissipation Factor (Tan Delta) of class A insulation e.g. oil impregnated paper insulation is 0.005. Rate of change of tan Delta and capacitance is very important. The rate of change of tan δ more than 0.001 per year needs further investigation. |  Chemical deterioration due to time and temperature.  Contamination by water, carbon deposits, bad oil, dirt, etc.  Severe leakage through cracks and over surfaces.  Ionisation Environmental factors like variation in temperature, relative humidity, surrounding charged objects etc. may influence measurement of dielectric dissipation factor. Care shall be taken to control the above factors during measurements. An increase of DF accompanied by a marked increase in capacitance usually indicates excessive moisture in the insulation. Increase of DF alone may be caused by thermal deterioration or by contamination other than water. Maximum values of Dissipation Factor (Tan Delta) of class A insulation e.g. oil impregnated paper insulation is 0.005. Rate of change of tan Delta and capacitance is very important. The rate of change of tan δ more than 0.001 per year needs further investigation. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 173 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0446 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Maintenance Schedule | Tan Delta | SCHEDULE | Capacitance value can vary between +10% and -5%. Comparison of test results can be done with similar piece of equipment, which was tested under the same conditions. 2.7 Capacitance and Tan Delta of Bushings Insulation power factor or dissipation factor (Tan δ) and Capacitance measurement of bushing provide an indication of the quality and health of the insulation in the bushing. For getting accurate results of Tan delta and Capacitance without removing the bushing from the transformer, a suitable test set capable of taking measurement by ungrounded specimen test (UST) method shall be used. It utilises the test tap of the bushing and a Tan delta/Capacitance test set. Both Tan delta and Capacitance can be measured using the same set up. Test voltage to be applied shall not exceed half of the power frequency test voltage or 10 kV, whichever is lower. | NOT COVERED | NOT VERIFIED | 10 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 173 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0447 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | It is desirable to have the frequency of the test set or measuring bridge different from but close to operating power frequency; so that stray power frequency currents do not interfere with the operation of the instrument. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 173 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0448 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Safety | Tan Delta | SAFETY | Measurements shall be made at similar conditions as that of a previous measurement. The oil-paper insulation combination of bushings exhibit fairly constant tan delta over a wide range of operating temperature. Hence, effort is to be made for testing at temperature near to previous test so that temperature correction factor need not be applied. The following precautions/ steps are to be taken:  Porcelain of the bushings shall be clean and dry before test. Remove any dirt or oil with clean dry cloth.  Test shall not be carried out when there is condensation on the porcelain. Preferably, tests shall not be carried out when the relative humidity is in excess of 75%.  Terminals of the bushings of each winding shall be shorted together using bare braided copper jumper. These jumpers shall not be allowed to sag. Transformer windings of the bushing not being tested shall be grounded. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Measurements shall be made at similar conditions as that of a previous measurement. The oil-paper insulation combination of bushings exhibit fairly constant tan delta over a wide range of operating temperature. Hence, effort is to be made for testing at temperature near to previous test so that temperature correction factor need not be applied. The following precautions/ steps are to be taken:  Porcelain of the bushings shall be clean and dry before test. Remove any dirt or oil with clean dry cloth.  Test shall not be carried out when there is condensation on the porcelain. Preferably, tests shall not be carried out when the relative humidity is in excess of 75%.  Terminals of the bushings of each winding shall be shorted together using bare braided copper jumper. These jumpers shall not be allowed to sag. Transformer windings of the bushing not being tested shall be grounded. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 174 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0449 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Bushing | TESTING |  Measure and record the ambient temperature and relative humidity for reference. Record OTI and WTI during the measurement.  Do not test a bushing (new or spare) while it is in its wood shipping crate, or while it is lying on wood. Wood is not as good an insulator as porcelain and will cause the readings to be inaccurate. Keep the test results as a baseline record to compare with future tests. Environmental factors like variation in temperature, relative humidity, surrounding charged objects etc. have great influence on measurement of dielectric dissipation factor. Care shall be taken to control the above factors during measurements. Testing during periods of high humidity or precipitation should be avoided; otherwise proper evaluation of test results becomes very difficult. |  Measure and record the ambient temperature and relative humidity for reference. Record OTI and WTI during the measurement.  Do not test a bushing (new or spare) while it is in its wood shipping crate, or while it is lying on wood. Wood is not as good an insulator as porcelain and will cause the readings to be inaccurate. Keep the test results as a baseline record to compare with future tests. Environmental factors like variation in temperature, relative humidity, surrounding charged objects etc. have great influence on measurement of dielectric dissipation factor. Care shall be taken to control the above factors during measurements. Testing during periods of high humidity or precipitation should be avoided; otherwise proper evaluation of test results becomes very difficult. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 174 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0450 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Safety | Tan Delta | SAFETY | A very small amount of water vapour on the surface of external insulation could increase the amount of leakage current and will appear as increased loss in the test result. There should not be wide variation in the measured values of tan delta (dissipation factor) of the bushings of transformer/reactor (measured at periodic intervals) when compared with previous references. For bushings, the tan delta value shall not exceed 0.005 (during first | NOT COVERED | delta (dissipation factor) of the bushings of transformer/reactor (measured at periodic intervals) when compared with previous references | NOT VERIFIED | A very small amount of water vapour on the surface of external insulation could increase the amount of leakage current and will appear as increased loss in the test result. There should not be wide variation in the measured values of tan delta (dissipation factor) of the bushings of transformer/reactor (measured at periodic intervals) when compared with previous references. For bushings, the tan delta value shall not exceed 0.005 (during first | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 174 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0451 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Failure / Failure Analysis | Tan Delta | FAILURE_ANALYSIS | charging). However, there should not be any deviation of more than 0.001 from initial tan delta value of the bushing. The main capacitance (C1) of the bushing i.e., the capacitance between high voltage terminal and test tap is not affected by the surrounding conditions and the accepted deviation from the values measured at factory tests should not be more than 5%. The capacitance between bushing test tap and ground is largely influenced by the stray capacitances to grounded parts in the transformer and hence larger deviation in the measured value shall be accepted when compared with the factory test value. 2.8 Short Circuit Impedance (only for transformers) This test is used to detect winding movement that usually occurs due to heavy fault current or mechanical damage during transportation or installation since dispatch from the factory. The measurement is performed in single phase mode. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | charging). However, there should not be any deviation of more than 0.001 from initial tan delta value of the bushing. The main capacitance (C1) of the bushing i.e., the capacitance between high voltage terminal and test tap is not affected by the surrounding conditions and the accepted deviation from the values measured at factory tests should not be more than 5%. The capacitance between bushing test tap and ground is largely influenced by the stray capacitances to grounded parts in the transformer and hence larger deviation in the measured value shall be accepted when compared with the factory test value. 2.8 Short Circuit Impedance (only for transformers) This test is used to detect winding movement that usually occurs due to heavy fault current or mechanical damage during transportation or installation since dispatch from the factory. The measurement is performed in single phase mode. | Transformers and reactors, 66 kV and above voltage class | PDF p. 175 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0452 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Inspection | OLTC | INSPECTION | This test is performed for the combination of two winding. One of the winding is short circuited and voltage is applied to other winding. The voltage and current reading are noted. The test shall be conducted with variac of 0-280 V, 10 A, precision RMS voltmeter and ammeter. The conductors used for short-circuiting one of the transformer windings should have low impedance (less than 1m-ohm) and short length. The contacts should be clean and tight. The measured impedance voltage should be within 3 percent of impedance specified in rating and diagram nameplate of the transformer. Variation in impedance voltage of more than 3% should be considered significant and needs to be further investigated. 2.9 Operational checks and Inspection of OLTC (only for transformers) On-Load Tap Changers (OLTCs) are designed to be operated while the transformer is energized. | This test is performed for the combination of two winding. One of the winding is short circuited and voltage is applied to other winding. The voltage and current reading are noted. The test shall be conducted with variac of 0-280 V, 10 A, precision RMS voltmeter and ammeter. The conductors used for short-circuiting one of the transformer windings should have low impedance (less than 1m-ohm) and short length. The contacts should be clean and tight. The measured impedance voltage should be within 3 percent of impedance specified in rating and diagram nameplate of the transformer. Variation in impedance voltage of more than 3% should be considered significant and needs to be further investigated. 2.9 Operational checks and Inspection of OLTC (only for transformers) On-Load Tap Changers (OLTCs) are designed to be operated while the transformer is energized. | NOT VERIFIED | 0-280 V; 10 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 175 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0453 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Maintenance Schedule | OLTC | SCHEDULE | OLTCs may be located either on the high voltage winding or on the low voltage winding, depending on the requirements of the user, the cost effectiveness of the application and tap changer availability. OLTC being a current interrupting device requires periodic inspection and maintenance. The frequency of | NOT COVERED | OLTC being a current interrupting device requires periodic inspection and maintenance | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 175 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0454 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | inspections is based on time in service, range of use and number of operations. Normally the temperature of the OLTC compartment may be few degrees Celsius less than the main tank. Any temperature approaching or above that of the main tank indicates an internal problem in OLTC. Prior to opening the OLTC compartment, it should be inspected for external symptoms of potential problems. The integrity of Paint (blister or damage to the coat may be due to exposure to contamination with salts and the leftover residue on the surface may absorb moisture weakening the strength of underlying steel tank), weld leaks, oil seal integrity, pressure relief device and liquid level gauge etc. should be inspected prior to opening of the OLTC compartment. | inspections is based on time in service, range of use and number of operations. Normally the temperature of the OLTC compartment may be few degrees Celsius less than the main tank. Any temperature approaching or above that of the main tank indicates an internal problem in OLTC. Prior to opening the OLTC compartment, it should be inspected for external symptoms of potential problems. The integrity of Paint (blister or damage to the coat may be due to exposure to contamination with salts and the leftover residue on the surface may absorb moisture weakening the strength of underlying steel tank), weld leaks, oil seal integrity, pressure relief device and liquid level gauge etc. should be inspected prior to opening of the OLTC compartment. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 176 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0455 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, OLTC | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | After de-energization, for internal inspection, close all valves between oil conservator, transformer tank and tap-changer head, then lower the oil level in the diverter switch oil compartment by draining of oil. After opening the OLTC compartment, the door gasket should be inspected for any sign of deterioration. The compartment floor should be inspected for debris that might indicate abnormal wear and sliding surfaces should be inspected for signs of excessive wear. The following checks should be carried out during inspection and maintenance and the manufacturer’s service engineer should be consulted for any assistance required in maintenance/overhauling activity to ensure trouble free operation in the future:  Functioning of control switches  OLTC stopping on position  Fastener tightness  Any signs of moisture ingress indicated by rusting, oxidation or free | After de-energization, for internal inspection, close all valves between oil conservator, transformer tank and tap-changer head, then lower the oil level in the diverter switch oil compartment by draining of oil. After opening the OLTC compartment, the door gasket should be inspected for any sign of deterioration. The compartment floor should be inspected for debris that might indicate abnormal wear and sliding surfaces should be inspected for signs of excessive wear. The following checks should be carried out during inspection and maintenance and the manufacturer’s service engineer should be consulted for any assistance required in maintenance/overhauling activity to ensure trouble free operation in the future:  Functioning of control switches  OLTC stopping on position  Fastener tightness  Any signs of moisture ingress indicated by rusting, oxidation or free | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 176 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0456 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION |  Mechanical block integrity  Proper operation of hand-crank and its interlock switch  Physical condition of tap selector  Freedom of movement of external shaft assembly  Extent of arc erosion on stationary and movable arcing contacts  Inspect barrier board for tracking and cracking  After filling with oil, manually crank throughout entire range  Oil BDV and Moisture content (PPM) to be measured and recorded |  Mechanical block integrity  Proper operation of hand-crank and its interlock switch  Physical condition of tap selector  Freedom of movement of external shaft assembly  Extent of arc erosion on stationary and movable arcing contacts  Inspect barrier board for tracking and cracking  After filling with oil, manually crank throughout entire range  Oil BDV and Moisture content (PPM) to be measured and recorded | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 177 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0457 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Finally, the tap selector compartment should be flushed with clean transformer oil and all carbonization which may have been deposited should be removed. Minimum BDV should be 50 kV and Moisture content should be less than 20 PPM. | NOT COVERED | NOT VERIFIED | 50 kV; 20 PPM | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 177 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0458 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Tan Delta | INSPECTION | a. Visual Inspection/Color b. Dielectric Strength (BDV) c. Moisture Content (PPM) d. Dielectric Loss/Power factor/Dissipation factor (Tan Delta) e. Inter facial Tension (IFT) f. Acidity (Neutralization No.) g. Oxidation Stability/Ageing test h. Particle Count (For 400 kV and above transformer & reactor) | a. Visual Inspection/Color b. Dielectric Strength (BDV) c. Moisture Content (PPM) d. Dielectric Loss/Power factor/Dissipation factor (Tan Delta) e. Inter facial Tension (IFT) f. Acidity (Neutralization No.) g. Oxidation Stability/Ageing test h. Particle Count (For 400 kV and above transformer & reactor) | NOT VERIFIED | 400 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 177 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0459 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | Values of these parameters shall be as per specification (Chapter-2 and Annexure-L). Inhibitor concentration for inhibited oil in service needs to be monitored and eventually maintained. For this purpose IEC 60422 may be referred. 2.11 Dissolved Gas Analysis (DGA) and Interpretation | Values of these parameters shall be as per specification (Chapter-2 and Annexure-L). Inhibitor concentration for inhibited oil in service needs to be monitored and eventually maintained. For this purpose IEC 60422 may be referred. 2.11 Dissolved Gas Analysis (DGA) and Interpretation | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 177 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0460 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | DGA is one of the most widely used diagnostic tools for detecting and evaluating faults in transformer / reactors. The fundamental purpose of DGA is to discriminate between normal and abnormal condition. Oil and oil-immersed electrical insulating materials decompose under the influence of thermal and electrical stresses and generate gaseous decomposition products of varying composition which dissolve in the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | DGA is one of the most widely used diagnostic tools for detecting and evaluating faults in transformer / reactors. The fundamental purpose of DGA is to discriminate between normal and abnormal condition. Oil and oil-immersed electrical insulating materials decompose under the influence of thermal and electrical stresses and generate gaseous decomposition products of varying composition which dissolve in the | Transformers and reactors, 66 kV and above voltage class | PDF p. 177 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0461 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | oil. The nature, amount and rate of generation of the individual component gases that are detected are indicative of the type and degree of the abnormality responsible for the gas generation. The purpose of DGA is to detect the internal faults within the oil-filled electrical equipment at an early stage and also to find incipient faults such as partial discharge, over-heating, arcing etc. The data obtained from this test is applied to various DGA techniques available in IEEE, IEC standards etc. such as IEEE.C57.104, IEC-60599 etc. for the interpretation of the test results that may give the type, severity and sometimes location of the fault. The transformer/reactor undergoes electrical, mechanical, chemical and thermal stresses during its service life which may result in slow evolving incipient faults inside the transformer. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | oil. The nature, amount and rate of generation of the individual component gases that are detected are indicative of the type and degree of the abnormality responsible for the gas generation. The purpose of DGA is to detect the internal faults within the oil-filled electrical equipment at an early stage and also to find incipient faults such as partial discharge, over-heating, arcing etc. The data obtained from this test is applied to various DGA techniques available in IEEE, IEC standards etc. such as IEEE.C57.104, IEC-60599 etc. for the interpretation of the test results that may give the type, severity and sometimes location of the fault. The transformer/reactor undergoes electrical, mechanical, chemical and thermal stresses during its service life which may result in slow evolving incipient faults inside the transformer. | Transformers and reactors, 66 kV and above voltage class | PDF p. 178 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0462 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | The gases generated under abnormal electrical or thermal stresses are hydrogen(H2), methane(CH4), ethane(C2H6), ethylene(C2H4), acetylene(C2H2), carbon monoxide(CO), carbon dioxide(CO2), nitrogen(N2) and oxygen(O2) which get dissolved in oil. Collectively these gases are known as FAULT GASES, which are routinely detected and quantified at extremely low level, typically in parts per million (ppm) in Dissolved Gas Analysis (DGA). CO & CO2 formation increases not only with temperature but also with oxygen content of oil and the moisture content of paper. Large quantity of CO & CO2 are evolved from overheating of cellulose. Most commonly used method to determine the content of these gases in oil is by Headspace extraction and Gas Chromatograph. Interpretation of DGA Results: The interpretation of DGA results is often complex. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The gases generated under abnormal electrical or thermal stresses are hydrogen(H2), methane(CH4), ethane(C2H6), ethylene(C2H4), acetylene(C2H2), carbon monoxide(CO), carbon dioxide(CO2), nitrogen(N2) and oxygen(O2) which get dissolved in oil. Collectively these gases are known as FAULT GASES, which are routinely detected and quantified at extremely low level, typically in parts per million (ppm) in Dissolved Gas Analysis (DGA). CO & CO2 formation increases not only with temperature but also with oxygen content of oil and the moisture content of paper. Large quantity of CO & CO2 are evolved from overheating of cellulose. Most commonly used method to determine the content of these gases in oil is by Headspace extraction and Gas Chromatograph. Interpretation of DGA Results: The interpretation of DGA results is often complex. | Transformers and reactors, 66 kV and above voltage class | PDF p. 178 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0463 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | The interpretation of DGA data begins with the detection of an abnormal condition. There is no direct/definite interpretation method to indicate exact location & type of fault and to evaluate the condition of a transformer. There are several possibilities wherein DGA status can be very different from the actual condition of the transformer. Some cause of gas generation are related to fault conditions (e.g. arcing, overheating, PD). At times, gases generation may be related to more benign conditions like stray gassing (a non-damage fault), contamination, previous fault now inactive, and mild core overheating, rusting or other chemical reactions involving steel, uncoated surfaces or protective paints etc. Additionally, some pre-failure conditions especially mechanical or insulating system weakness will not generate | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The interpretation of DGA data begins with the detection of an abnormal condition. There is no direct/definite interpretation method to indicate exact location & type of fault and to evaluate the condition of a transformer. There are several possibilities wherein DGA status can be very different from the actual condition of the transformer. Some cause of gas generation are related to fault conditions (e.g. arcing, overheating, PD). At times, gases generation may be related to more benign conditions like stray gassing (a non-damage fault), contamination, previous fault now inactive, and mild core overheating, rusting or other chemical reactions involving steel, uncoated surfaces or protective paints etc. Additionally, some pre-failure conditions especially mechanical or insulating system weakness will not generate | Transformers and reactors, 66 kV and above voltage class | PDF p. 178 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0464 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | gas. Some normal conditions also generate gases, for example, normal ageing, and insulating liquid oxidation. Detection of gas does not give any conclusive status of health by itself. Prior DGA results should be used for characterization of increments and rates. If abnormal DGA results are found, any available supplementary information, such as test and maintenance records, loading pattern, environmental conditions, etc., should be consulted for possible clues as to the origin and nature of the abnormalities. Comparison of DGA data from sister units is also useful in absence of such information. The different interpretation methods only provide guidelines to take an engineering judgment about the equipment. Some important extract of IEEE.C57.104-2019 and IEC-60599-2015 method of evaluation Dissolved Gas is given below for guidance only. | gas. Some normal conditions also generate gases, for example, normal ageing, and insulating liquid oxidation. Detection of gas does not give any conclusive status of health by itself. Prior DGA results should be used for characterization of increments and rates. If abnormal DGA results are found, any available supplementary information, such as test and maintenance records, loading pattern, environmental conditions, etc., should be consulted for possible clues as to the origin and nature of the abnormalities. Comparison of DGA data from sister units is also useful in absence of such information. The different interpretation methods only provide guidelines to take an engineering judgment about the equipment. Some important extract of IEEE.C57.104-2019 and IEC-60599-2015 method of evaluation Dissolved Gas is given below for guidance only. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 179 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0465 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | IEC 60599 method for Gas Analysis: This method is applicable only when the fault gas results are ten times the sensitivity limit of the Gas Chromatograph (GC). As per IEC 60567 the sensitivity limit for the GC should be 1 ppm for all the hydrocarbons and 5 ppm for Hydrogen. In this method three ratios viz. C2H2/C2H4, CH4/H2 & C2H4/C2H6 are used for interpretation. Each ratio is assigned a code depending upon the range of values of ratios. These codes in different combinations are then used for diagnosis of type of fault such as Partial Discharge (PD), low energy discharge (D1), High energy discharge (D2), thermal faults of various temperatures (T1<300°C, 300°C<T2<700°C & T3>700°C). Fault often start as incipient faults of low energy, which may develop into more serious ones of higher energies, leading to possible gas alarms, breakdowns & failures. | NOT COVERED | NOT VERIFIED | 1 ppm; 5 ppm; 300°C; 700°C | NOT COVERED | IEC 60599 method for Gas Analysis: This method is applicable only when the fault gas results are ten times the sensitivity limit of the Gas Chromatograph (GC). As per IEC 60567 the sensitivity limit for the GC should be 1 ppm for all the hydrocarbons and 5 ppm for Hydrogen. In this method three ratios viz. C2H2/C2H4, CH4/H2 & C2H4/C2H6 are used for interpretation. Each ratio is assigned a code depending upon the range of values of ratios. These codes in different combinations are then used for diagnosis of type of fault such as Partial Discharge (PD), low energy discharge (D1), High energy discharge (D2), thermal faults of various temperatures (T1<300°C, 300°C<T2<700°C & T3>700°C). Fault often start as incipient faults of low energy, which may develop into more serious ones of higher energies, leading to possible gas alarms, breakdowns & failures. | Transformers and reactors, 66 kV and above voltage class | PDF p. 179 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0466 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Type Fault Examples low energy connections of different or floating potential, from shielding rings, toroids, adjacent disks or conductors of winding, broken brazing or closed loops in the core.  Discharges between clamping parts, bushing and tank, high voltage and ground within windings, on tank walls.  Tracking in wooden blocks, glue of insulating beam, winding spacers, Breakdown of oil, selector breaking current. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Type Fault Examples low energy connections of different or floating potential, from shielding rings, toroids, adjacent disks or conductors of winding, broken brazing or closed loops in the core.  Discharges between clamping parts, bushing and tank, high voltage and ground within windings, on tank walls.  Tracking in wooden blocks, glue of insulating beam, winding spacers, Breakdown of oil, selector breaking current. | Transformers and reactors, 66 kV and above voltage class | PDF p. 180 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0467 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Safety | Transformer Oil | SAFETY | ground, connectors, windings, bushings and tank, copper bus and tank, windings and core, in oil duct, turret. Closed loops between two adjacent conductors around the main magnetic flux, insulated bolts of core, metal rings holding core legs. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | ground, connectors, windings, bushings and tank, copper bus and tank, windings and core, in oil duct, turret. Closed loops between two adjacent conductors around the main magnetic flux, insulated bolts of core, metal rings holding core legs. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 180 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0468 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | NOTE 4 – Gas decomposition patters similar to partial discharges have been reported as a result of stray gassing of oil. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 181 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0469 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | IEEE C57.104 Method of Evaluation: DGA status: The classification process and recommendations given below are based on gas levels and level variation norms obtained from a statistical analysis of a large population of DGA results (90th and 95th percentiles). This procedure is a guideline only. | IEEE C57.104 Method of Evaluation: DGA status: The classification process and recommendations given below are based on gas levels and level variation norms obtained from a statistical analysis of a large population of DGA results (90th and 95th percentiles). This procedure is a guideline only. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 181 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0470 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | DGA | SAFETY | The transformer with DGA Status 2 or Status 3 (i.e., being above statistical norms) is not necessarily faulty. It can only be concluded that its behavior is somewhat unusual and warrants additional investigation and/or precautions to be implemented, either simple or extensive, as evaluated by the DGA expert. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The transformer with DGA Status 2 or Status 3 (i.e., being above statistical norms) is not necessarily faulty. It can only be concluded that its behavior is somewhat unusual and warrants additional investigation and/or precautions to be implemented, either simple or extensive, as evaluated by the DGA expert. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 183 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0471 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Note:- During the data analysis, it was determined that voltage class, MVA, and volume of mineral oil in the unit did not contribute in significant way to the determination of values provided in Table 1. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 183 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0472 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Note:- During the data analysis, it was determined that voltage class, MVA, and volume of mineral oil in the unit did not contribute in significant way to the determination of values provided in Table 2 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 184 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0473 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | successive laboratory DGA samples in µL/L (ppm) Maximum µL/L (ppm) variation between consecutive | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 184 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0474 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Note:- Contribution of voltage class, MVA, and volume of mineral oil in the unit was not studied for Table 3 as they have not been retained for Table 1 and Table 2. Data was insufficient to study age influence. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 184 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0475 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | analysis of laboratory DGA samples with all gas levels below Table 1 values, in µL/L/year (ppm/year) Maximum µL/L/year (ppm/year) rate in function of the period | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 185 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0476 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Note:- Contribution of voltage class, MVA, and volume of mineral oil in the unit was not studied for Table 4 as they have not been retained for Table 1 and Table 2. Data was insufficient to study age influence. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 185 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0477 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | The associated faults for the different evolved gases can be correlated as follows:  Hydrogen (H2) is created primarily from corona partial discharge and stray gassing of oil, also from sparking discharges and arcs.  Methane (CH4), Ethane (C2H6), and Ethylene (C2H4) are created from heating of oil or paper.  Acetylene (C2H2) is created from arcing in oil or paper at very high temperatures above 1000 °C.  Carbon Monoxide (CO) and Carbon Dioxide (CO2) are created from heating of cellulose or insulating liquid. | NOT COVERED | NOT VERIFIED | 1000 °C | NOT COVERED | The associated faults for the different evolved gases can be correlated as follows:  Hydrogen (H2) is created primarily from corona partial discharge and stray gassing of oil, also from sparking discharges and arcs.  Methane (CH4), Ethane (C2H6), and Ethylene (C2H4) are created from heating of oil or paper.  Acetylene (C2H2) is created from arcing in oil or paper at very high temperatures above 1000 °C.  Carbon Monoxide (CO) and Carbon Dioxide (CO2) are created from heating of cellulose or insulating liquid. | Transformers and reactors, 66 kV and above voltage class | PDF p. 185 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0478 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | The percentage of each individual gas is calculated from the accumulated total of these three fault gases. The same is then traced on the Duval triangle and the intersection indicates possible problems within the transformer/reactor. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The percentage of each individual gas is calculated from the accumulated total of these three fault gases. The same is then traced on the Duval triangle and the intersection indicates possible problems within the transformer/reactor. | Transformers and reactors, 66 kV and above voltage class | PDF p. 186 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0479 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | The Table below gives the numerical values for fault zone boundaries of Duval Triangle 1 Method expressed in (%CH4), (%C2H4), and (%C2H2). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The Table below gives the numerical values for fault zone boundaries of Duval Triangle 1 Method expressed in (%CH4), (%C2H4), and (%C2H2). | Transformers and reactors, 66 kV and above voltage class | PDF p. 186 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0480 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | research and some distinction of the severity of incipient electrical fault conditions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | research and some distinction of the severity of incipient electrical fault conditions. | Transformers and reactors, 66 kV and above voltage class | PDF p. 187 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0481 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | Note: There is tendency for the ratio C2H2/C2H4 and C2H4/C2H6 to increase to a ratio above 3 as the discharge develops in intensity. The limitation of the Rogers Ratios Method is that it cannot identify faults in a relatively large number of DGA results (typically 35%), because they do not correspond to any of the cases in column 1 of Table above even when μL/L (ppm) values are high and there is obviously a fault. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Note: There is tendency for the ratio C2H2/C2H4 and C2H4/C2H6 to increase to a ratio above 3 as the discharge develops in intensity. The limitation of the Rogers Ratios Method is that it cannot identify faults in a relatively large number of DGA results (typically 35%), because they do not correspond to any of the cases in column 1 of Table above even when μL/L (ppm) values are high and there is obviously a fault. | Transformers and reactors, 66 kV and above voltage class | PDF p. 187 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0482 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | DGA | SAFETY | The Rogers Ratio Method and Duval Triangle 1 Method should not be used on samples with very low gas levels, which can be unreliable and inaccurate. The DGA interpretation is still more of an art than a science. It is generally recognized by experts that increasing gas levels (i.e. gas generation rate) are more of concern than the levels themselves. It is emphasized that DGA shall give misleading results unless certain precautions are taken. These are proper sampling procedure, Type of sampling bottle, cleanliness of bottle, duration of storage, method of gas extraction, good testing equipment and skilled manpower. Sampling of transformer insulating liquid for DGA by trained & experiences person and the consultation of a transformer expert with DGA interpretation experience is strongly recommended. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | The Rogers Ratio Method and Duval Triangle 1 Method should not be used on samples with very low gas levels, which can be unreliable and inaccurate. The DGA interpretation is still more of an art than a science. It is generally recognized by experts that increasing gas levels (i.e. gas generation rate) are more of concern than the levels themselves. It is emphasized that DGA shall give misleading results unless certain precautions are taken. These are proper sampling procedure, Type of sampling bottle, cleanliness of bottle, duration of storage, method of gas extraction, good testing equipment and skilled manpower. Sampling of transformer insulating liquid for DGA by trained & experiences person and the consultation of a transformer expert with DGA interpretation experience is strongly recommended. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 187 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0483 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | Specific information to be added to the DGA reports Specific information to be added to the DGA reports is as follows: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 188 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0484 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE |  Date of commissioning  Voltage class/ Voltage ratio, Power rating  Oil Volume  Oil Temperature  Type of cooling system: ONAN, OFAF etc.  Oil & gas sampling date  Oil & gas sampling location  Type of OLTC and whether it is communicating with main tank or not  No. of OLTC operation,  Load since last DGA  Previous DGA done  Special operation or incidences just before the oil or gas sampling such as tripping, gas alarm, degassing, repair, outage etc. 2.12 Frequency Response Analysis (FRA) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 188 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0485 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Maintenance Schedule | Capacitance | SCHEDULE | The frequency response analysis (FRA) is a technique that is used to diagnose the condition, or more importantly the change of mechanical condition, of a transformer by analyzing the transformer winding’s frequency characteristics. FRA provides internal diagnostic information using nonintrusive procedures. The primary objective of FRA is to determine how the impedance of a test specimen behaves over a specified range of frequencies. The Short circuit forces can cause winding movement and changes in winding inductance or capacitance in Power Transformers. Recording the frequency response with these changes gives information regarding the internal condition of the equipment. Frequency Response Analysis (FRA) has proved to be an effective tool to detect such changes. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 188 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0486 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | The measured response is usually shown graphically by plotting the logarithmic amplitude ratio of the output voltage to input voltage in dB (y-axis) against the frequency (x-axis). (The logarithmic often shows the complete frequency range more clearly. The linear scale is useful for looking at discrete frequency bands and to compare small differences at particular frequencies). The Frequency Response of a transformer winding (often called the FRA response curve) is quite complex and consists of decreasing and increasing magnitude (in dB) with respect to frequency. The various resonances (maxima) and anti- | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 188 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0487 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | DGA | SAFETY | Frequency Response Analysis (FRA) is made to assess the mechanical integrity of the transformer/reactor. Transformer/Reactor, while experiencing severity of short circuit current, loses its mechanical property by way of deformation of the winding or core. These changes cannot be detected through conventional condition monitoring techniques such as Dissolved Gas Analysis, Winding Resistance Measurement, Capacitance and Tan delta measurement etc. Sometimes even transportation without proper precaution may cause some internal mechanical damages. FRA measurement, which is a signature analysis, provides vital information of the internal condition of the equipment so that early corrective action could be initiated. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Frequency Response Analysis (FRA) is made to assess the mechanical integrity of the transformer/reactor. Transformer/Reactor, while experiencing severity of short circuit current, loses its mechanical property by way of deformation of the winding or core. These changes cannot be detected through conventional condition monitoring techniques such as Dissolved Gas Analysis, Winding Resistance Measurement, Capacitance and Tan delta measurement etc. Sometimes even transportation without proper precaution may cause some internal mechanical damages. FRA measurement, which is a signature analysis, provides vital information of the internal condition of the equipment so that early corrective action could be initiated. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 189 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0488 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Testing | Transformer Oil | TESTING | The transformer/reactor under test should be completely de-energized and isolated from the power system. All bushings of windings shall be disconnected from the system. It is important to record all relevant information which includes date & time of measurement, details of test equipment, name plate data of transformer and test setup like tap position, oil status (whether immersed or not), oil level, oil temperature and terminal grounded or shorted. | The transformer/reactor under test should be completely de-energized and isolated from the power system. All bushings of windings shall be disconnected from the system. It is important to record all relevant information which includes date & time of measurement, details of test equipment, name plate data of transformer and test setup like tap position, oil status (whether immersed or not), oil level, oil temperature and terminal grounded or shorted. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 189 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0489 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Capacitance | FAILURE_ANALYSIS | Sinusoidal signal output of approximately 2 V to 24 V rms from the Frequency Response Analyzer is applied and one measuring input (R1) is connected to the end of a winding and the other measuring input (T1) is connected to the other end of the winding. The voltage is applied and measured with respect to the earthed transformer/reactor tank. The voltage transfer function T1/R1 is measured for each winding for five standard frequency scans from 5 Hz to 10 MHz and the amplitude & phase shift results are recorded. At low frequencies, the influence of capacitance is negligible and winding behaves as an inductor. As the frequency of input signal increases, the capacitance begins to dominate. The low frequency analysis reveals the winding movements/deformation or core defects and the high frequency analysis reveals the condition of winding tightness and lead connections etc. | NOT COVERED | NOT VERIFIED | 2 V; 24 V; 5 Hz | NOT COVERED | Sinusoidal signal output of approximately 2 V to 24 V rms from the Frequency Response Analyzer is applied and one measuring input (R1) is connected to the end of a winding and the other measuring input (T1) is connected to the other end of the winding. The voltage is applied and measured with respect to the earthed transformer/reactor tank. The voltage transfer function T1/R1 is measured for each winding for five standard frequency scans from 5 Hz to 10 MHz and the amplitude & phase shift results are recorded. At low frequencies, the influence of capacitance is negligible and winding behaves as an inductor. As the frequency of input signal increases, the capacitance begins to dominate. The low frequency analysis reveals the winding movements/deformation or core defects and the high frequency analysis reveals the condition of winding tightness and lead connections etc. | Transformers and reactors, 66 kV and above voltage class | PDF p. 189 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0490 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | It is ensured that winding which is not under test is terminated in open condition in order to avoid undue variations of the results among the three phases. The same procedure is followed on subsequent tests on the same or similar units, to ensure that measurements could be effectively compared. | It is ensured that winding which is not under test is terminated in open condition in order to avoid undue variations of the results among the three phases. The same procedure is followed on subsequent tests on the same or similar units, to ensure that measurements could be effectively compared. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 190 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0491 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | The voltage transfer function T1/R1 is measured for each winding for four standard frequency scans from 5 Hz to 2 MHZ and amplitude & phase shift results are recorded for subsequent analysis | NOT COVERED | NOT VERIFIED | 5 Hz | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 190 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0492 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | General | INSPECTION | Interpretation of the test results is based on subjective comparison of FRA responses taken at different intervals. If changes are observed in the later FRA spectrum with respect to the reference FRA spectrum, it is left to the experience of the analyst for qualitative condition assessment of the transformer/reactor. However, one should check for any significant shift in the resonance frequencies and emergence of new resonant frequencies in the later FRA response, which could be the result of any mechanical deformation in the transformer/reactor winding. As FRA is signature analysis, data of signature of the equipment when in healthy condition is required for proper analysis. Signatures could also be compared with unit of same internal design or with other phases of the same unit. Normally measured responses are analyzed for any of the following: | Interpretation of the test results is based on subjective comparison of FRA responses taken at different intervals. If changes are observed in the later FRA spectrum with respect to the reference FRA spectrum, it is left to the experience of the analyst for qualitative condition assessment of the transformer/reactor. However, one should check for any significant shift in the resonance frequencies and emergence of new resonant frequencies in the later FRA response, which could be the result of any mechanical deformation in the transformer/reactor winding. As FRA is signature analysis, data of signature of the equipment when in healthy condition is required for proper analysis. Signatures could also be compared with unit of same internal design or with other phases of the same unit. Normally measured responses are analyzed for any of the following: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 190 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0493 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Safety | General | SAFETY |  Changes in the response of the winding with reference to earlier signature.  Variation in the responses of the three phases of the same transformer/reactor.  Variation in the responses of transformers/reactors of the same design. In all the above cases the appearance of new features, i.e. production of new resonance peaks or valleys or major frequency shifts are causes for concern. The phase responses are also being recorded but normally it is sufficient to consider only amplitude responses. | NOT COVERED | NOT VERIFIED | NOT VERIFIED |  Changes in the response of the winding with reference to earlier signature.  Variation in the responses of the three phases of the same transformer/reactor.  Variation in the responses of transformers/reactors of the same design. In all the above cases the appearance of new features, i.e. production of new resonance peaks or valleys or major frequency shifts are causes for concern. The phase responses are also being recorded but normally it is sufficient to consider only amplitude responses. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 190 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0494 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | The traces in general will change shape and will be distorted in the low frequency range (below 5 KHz) if there is a core problem. The traces will be distorted and change shape in higher frequencies (above 10 KHz), if there is winding problem. Changes of less than 3 decibels (dB) compared to baseline traces are normal and within tolerances. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 190 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0495 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | The failure modes according to IEEE Std. C57.149-2012 is given below. In general, the FRA test is sensitive to defects that cause geometric change(s) within a transformer. Any defect of this kind is referred to as failure mode even though such defect does not necessarily lead to a catastrophic failure of equipment. In fact, the popularity of the FRA test has been driven by the desire to detect mechanical failures within a transformer. Failure modes are not exclusive to geometric variations within a transformer and can include variation in the core’s magnetic circuit and contact resistance. FRA test variations can be caused by a single type of failure or a combination of two or more. Failure due to faults creates high over- currents through the transformer. As a result, the transformer experiences strong and often violent electromagnetic forces. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The failure modes according to IEEE Std. C57.149-2012 is given below. In general, the FRA test is sensitive to defects that cause geometric change(s) within a transformer. Any defect of this kind is referred to as failure mode even though such defect does not necessarily lead to a catastrophic failure of equipment. In fact, the popularity of the FRA test has been driven by the desire to detect mechanical failures within a transformer. Failure modes are not exclusive to geometric variations within a transformer and can include variation in the core’s magnetic circuit and contact resistance. FRA test variations can be caused by a single type of failure or a combination of two or more. Failure due to faults creates high over- currents through the transformer. As a result, the transformer experiences strong and often violent electromagnetic forces. | Transformers and reactors, 66 kV and above voltage class | PDF p. 191 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0496 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | These violent events can often lead to compounded failure modes. These compounded events can complicate the FRA analysis but often helps to better understand the condition of the transformer. The failure modes and explanation of each is as follows: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | These violent events can often lead to compounded failure modes. These compounded events can complicate the FRA analysis but often helps to better understand the condition of the transformer. The failure modes and explanation of each is as follows: | Transformers and reactors, 66 kV and above voltage class | PDF p. 191 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0497 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | It should be noted that the effects of deformations on the FRA measurements vary with transformer type and design. The same deformation type may affect different transformers differently. Frequency ranges for failure modes given in tables below are approximate and might be some overlap between ranges. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | It should be noted that the effects of deformations on the FRA measurements vary with transformer type and design. The same deformation type may affect different transformers differently. Frequency ranges for failure modes given in tables below are approximate and might be some overlap between ranges. | Transformers and reactors, 66 kV and above voltage class | PDF p. 193 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0498 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | In general, changes of ± 3 dB (or more) in following frequency range may indicate following probable faults. Variation could either be a Shift or formation of new resonance peaks and valleys. The interpretation of FRA in different frequency range as derived from IEEE Std. C57.149-2012 is as follows: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | In general, changes of ± 3 dB (or more) in following frequency range may indicate following probable faults. Variation could either be a Shift or formation of new resonance peaks and valleys. The interpretation of FRA in different frequency range as derived from IEEE Std. C57.149-2012 is as follows: | Transformers and reactors, 66 kV and above voltage class | PDF p. 193 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0499 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | Frequency Range Probable Fault (assuming no other failure modes exist) 20 Hz – 10 kHz Winding turn-to-turn short circuit (affected winding show the greatest change), Core defects (OC test) 5 kHz – 100 kHz Axial winding deformation, Bulk winding movement, Contact resistance, Open circuit winding 50 kHz – 1 MHz Radial winding deformation 100 kHz-500 kHz Floating shield with local insulation carbonization (detectable response with changes in peaks and valleys) 1 MHz- 5 Mhz Winding looseness due to transportation, Floating shield with local insulation carbonization (largest differences in peaks and valleys) FRA relationship to other transformer diagnostics The FRA results (depending on the particular test connections) can be used to confirm the results of other diagnostic tests. The comparison of these tests with FRA is given below: | NOT COVERED | NOT VERIFIED | 20 Hz | NOT COVERED | Frequency Range Probable Fault (assuming no other failure modes exist) 20 Hz – 10 kHz Winding turn-to-turn short circuit (affected winding show the greatest change), Core defects (OC test) 5 kHz – 100 kHz Axial winding deformation, Bulk winding movement, Contact resistance, Open circuit winding 50 kHz – 1 MHz Radial winding deformation 100 kHz-500 kHz Floating shield with local insulation carbonization (detectable response with changes in peaks and valleys) 1 MHz- 5 Mhz Winding looseness due to transportation, Floating shield with local insulation carbonization (largest differences in peaks and valleys) FRA relationship to other transformer diagnostics The FRA results (depending on the particular test connections) can be used to confirm the results of other diagnostic tests. The comparison of these tests with FRA is given below: | Transformers and reactors, 66 kV and above voltage class | PDF p. 194 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0500 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Capacitance | FAILURE_ANALYSIS | Capacitance and dissipation factor (Tanδ) measurement at 50 Hz is a very common diagnostics techniques used for insulation condition assessment of the bushings since many decades. The moisture in paper, ageing of paper and other polar impurities in insulation can be detected by this measurement. However, relation between insulation condition (e.g. moisture and ageing) and C and Tan δ values at power frequency are sometimes uncertain. In many cases it has been observed that an initial developing fault in bushing may not always be reflected by Tan δ values at 50Hz. Similarly, a limitation of the capacitance method is that only partial breakdowns and contact problems in the main current path can be detected. Problems like partial discharge in bushings, partial breakdown between two capacitive layers are generally not reflected as any substantial change in capacitance value at 50Hz. | NOT COVERED | NOT VERIFIED | 50 Hz; 50Hz | NOT COVERED | Capacitance and dissipation factor (Tanδ) measurement at 50 Hz is a very common diagnostics techniques used for insulation condition assessment of the bushings since many decades. The moisture in paper, ageing of paper and other polar impurities in insulation can be detected by this measurement. However, relation between insulation condition (e.g. moisture and ageing) and C and Tan δ values at power frequency are sometimes uncertain. In many cases it has been observed that an initial developing fault in bushing may not always be reflected by Tan δ values at 50Hz. Similarly, a limitation of the capacitance method is that only partial breakdowns and contact problems in the main current path can be detected. Problems like partial discharge in bushings, partial breakdown between two capacitive layers are generally not reflected as any substantial change in capacitance value at 50Hz. | Transformers and reactors, 66 kV and above voltage class | PDF p. 195 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0501 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | In all such cases, Capacitance and dissipation factor (Tanδ) measurement at variable frequency, known as Frequency Domain Spectroscopy(FDS), and supplemented by DGA is found to be a good method for condition assessment of OIP bushings. FDS includes measurement of C and dissipation factor over a frequency range of 1 mHz to 1 kHz and may be used to help arrive at conclusions about effect of polarisation, moisture content, ageing effect etc. in transformer/reactor insulation. FDS has very good correlation with DGA and can be verified by visual inspection after dismantling. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 195 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0502 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | The permittivity, which can be used to characterize the insulation, is a dimensionless complex quantity, real part representing the energy stored in the electric field within the sample and imaginary part representing the energy losses. FDS characteristic of an oil-paper composite insulation represents the frequency and temperature dependency of permittivity and dissipation factor. In addition, defects like voids in paper, partial discharge and deposition of X-Wax in the bushings leading to high dielectric loss can be detected by the above measurement. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | The permittivity, which can be used to characterize the insulation, is a dimensionless complex quantity, real part representing the energy stored in the electric field within the sample and imaginary part representing the energy losses. FDS characteristic of an oil-paper composite insulation represents the frequency and temperature dependency of permittivity and dissipation factor. In addition, defects like voids in paper, partial discharge and deposition of X-Wax in the bushings leading to high dielectric loss can be detected by the above measurement. | Transformers and reactors, 66 kV and above voltage class | PDF p. 195 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0503 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | The FDS characteristic of the bushing may be interpreted in the manner as suggested: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 195 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0504 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | From Dissolved Gas Analysis (DGA), it is possible to detect PD. However, a direct measurement of PD is much helpful to ascertain a rapidly increasing rate of PD. Partial discharges (PD) are localized dielectric discharges in a partial area of a solid or liquid electrical dielectric insulation system at rated voltage. It is in general a consequence of local electrical stress | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 196 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0505 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | concentration in the insulation or on the surface of the insulation. Partial discharges in a transformer/reactor deteriorate its insulation and can lead to failure of the unit. Diagnostic PD measurements are recommended after conspicuous measured values such as increased gas-in-oil values. Partial Discharges can be measured in the field using Acoustic or UHF measurement method. (a) Acoustic PD measurement During a partial discharge, there occurs impulse conversion of some part of electric energy to mechanical energy, which is an acoustic emission wave. The acoustic emission is a group of phenomena involving generation of transient elastic (acoustic or vibro-acoustic) waves, resulting from liberation of intermolecular bond energy (deformation, cracking, phase transitions). | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | concentration in the insulation or on the surface of the insulation. Partial discharges in a transformer/reactor deteriorate its insulation and can lead to failure of the unit. Diagnostic PD measurements are recommended after conspicuous measured values such as increased gas-in-oil values. Partial Discharges can be measured in the field using Acoustic or UHF measurement method. (a) Acoustic PD measurement During a partial discharge, there occurs impulse conversion of some part of electric energy to mechanical energy, which is an acoustic emission wave. The acoustic emission is a group of phenomena involving generation of transient elastic (acoustic or vibro-acoustic) waves, resulting from liberation of intermolecular bond energy (deformation, cracking, phase transitions). | Transformers and reactors, 66 kV and above voltage class | PDF p. 197 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0506 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | A typical measurement system for partial discharges detection based on acoustic emission method is composed of: (i) piezoelectric sensors, (ii) preamplifiers, (iii) signal conditioning unit, (iv) signal acquisition unit and (v) specialized software for digital signal processing. Proper acoustic coupling between the sensor and the surface of the tank shall be ensured in the detection of partial discharges in a power. For this purpose, silicone grease or gel dedicated for ultrasonic applications may be utilised. A lack of direct contact of acoustic sensor with the tank causes a strong attenuation of the AE amplitude signal, and thus a strong decrease in sensitivity of partial discharges detection may occur. | A typical measurement system for partial discharges detection based on acoustic emission method is composed of: (i) piezoelectric sensors, (ii) preamplifiers, (iii) signal conditioning unit, (iv) signal acquisition unit and (v) specialized software for digital signal processing. Proper acoustic coupling between the sensor and the surface of the tank shall be ensured in the detection of partial discharges in a power. For this purpose, silicone grease or gel dedicated for ultrasonic applications may be utilised. A lack of direct contact of acoustic sensor with the tank causes a strong attenuation of the AE amplitude signal, and thus a strong decrease in sensitivity of partial discharges detection may occur. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 197 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0507 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Corrective Action | Transformer Oil | CORRECTIVE_ACTION | Moisture in the transformer/reactor oil can be measured and controlled using the Online Dryout System. This system has been recommended for 400 kV and above class transformers and reactors. The system is permanently installed which continuously keeps on removing the moisture while transformer/reactor is in charged stage. During the filtration process moisture PPM level is continuously monitored. This process removes moisture from transformer/reactor oil as well as the cellulose insulation. | NOT COVERED | NOT VERIFIED | 400 kV | NOT COVERED | Moisture in the transformer/reactor oil can be measured and controlled using the Online Dryout System. This system has been recommended for 400 kV and above class transformers and reactors. The system is permanently installed which continuously keeps on removing the moisture while transformer/reactor is in charged stage. During the filtration process moisture PPM level is continuously monitored. This process removes moisture from transformer/reactor oil as well as the cellulose insulation. | Transformers and reactors, 66 kV and above voltage class | PDF p. 198 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0508 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The transformer/reactor oil is circulated through a series of cylinders filled with specially designed cartridges that absorbs moisture as well as removes solid contaminants from the oil. However, this may not be suitable for Wet transformers/Reactors which may require Off Line Dryout. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 198 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0509 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Inspection | Bushing | INSPECTION | A thermovision camera determines the temperature distribution on the surface of the tank as well as in the vicinity of the jumper connection to the bushing. The information obtained by thermographs (as given below) is useful in predicting the temperature profile within the inner surface of tank and is likely to provide approximate details of heating mechanism. The following temperature rises above ambient have been found to be practical during infrared inspections: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 198 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0510 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Maintenance Schedule | SCHEDULE | 0-10 Minor Repair in regular maintenance schedule: Little probability of physical damage 11-39 Intermediate Repair in near future (2-4 weeks); Inspect for | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 198 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0511 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Condition Monitoring | General | CONDITION_MONITORING | Paper is the major solid dielectric material within a transformer, used either as conductor wraps and impregnated with insulating liquid, or as barrier boards, wraps, spacers, and clamps in compressed or resin bonded forms. The major constituents of the paper are cellulose (about 90%), lignin (about 6%), and the remainder (about 4%). The three most common degradation factors of cellulose have been identified as thermal, oxidative, and hydrolytic. When excessive paper degradation is suspected it is recommended to go for further analysis. Degradation of insulating paper can be ascertained by direct or indirect methods. Direct method employs Degree of Polymerization (DP), which requires a physical paper sample from the winding. However, this method being destructive to transformer, cannot be employed as a routine condition monitoring exercise. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 199 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0512 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Furfural Analysis is an indirect method assessment of degradation of insulating paper. For the oil-filled transformers, particularly which are in service for more than 15 years, it is advisable that the residual life should be estimated by assessing the extent of degradation of solid cellulosic paper insulation through Furan content analysis of oil and degree of polymerization of paper insulation. This would help utilities in making optimum use of transformers/reactors and also taking timely decision regarding Run-Refurbish-Replacement of transformers/reactors. | NOT COVERED | NOT VERIFIED | 15 years | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 199 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0513 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | One of the most dependable means of determining paper deterioration and remaining life is the DP test of the cellulose. The cellulose molecule is made up of a long chain of glucose rings which form the mechanical strength of the molecule and the paper. DP is the average number of these rings in the molecule. For DP measurement remove a sample of the paper insulation about 1 centimeter square from a convenient location near the top of center phase with a pair of tweezers. In general, in a three-phase transformer, the hottest most thermally aged paper will be at the top of the center phase. If it is not | One of the most dependable means of determining paper deterioration and remaining life is the DP test of the cellulose. The cellulose molecule is made up of a long chain of glucose rings which form the mechanical strength of the molecule and the paper. DP is the average number of these rings in the molecule. For DP measurement remove a sample of the paper insulation about 1 centimeter square from a convenient location near the top of center phase with a pair of tweezers. In general, in a three-phase transformer, the hottest most thermally aged paper will be at the top of the center phase. If it is not | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 199 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0514 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | General | INSPECTION | physical damages 40-75 Serious Repair in the immediate future (1-2 days). Disassemble and check for probable damage >76 Critical Critical problems; Repair immediately | physical damages 40-75 Serious Repair in the immediate future (1-2 days). Disassemble and check for probable damage >76 Critical Critical problems; Repair immediately | NOT VERIFIED | 1-2 days | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 199 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0515 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | The immediate byproducts related to paper degradation are CO, CO2, moisture, organic acids, and free glucose molecules. The free glucose degrades further into aromatic components known as furans. The presence of moisture and organic acids in the insulating liquid can further degrade the free glucose molecule into 5-hydroxymethyl-2- furfuryl or 5H2F. 5H2F is an unstable compound and can decompose further into 2-furaldehyde (2FAL) and other furans. The major furanic compound in oil which is stable is 2-furfuraldehyde (2FAL) and the others are present in very low or undetected level. The 2FAL is apparently stable for several years under the same conditions. The concentration of the furanic compounds gives an indication of the condition of the paper in terms of the degree of polymerization, while the rate of change of furan concentration can indicate the rate of aging of paper. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 200 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0516 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance | General | MAINTENANCE | Generally, the total concentrations are less than 0.5 ppm and, in some cases, these levels may be maintained throughout transformer life. The types and concentrations of furans in the insulating liquid sample can also indicate the occurrence of abnormal stresses in a transformer, whether short duration overheating of the insulation or prolonged general overheating. | NOT COVERED | NOT VERIFIED | 0.5 ppm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 200 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0517 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Inspection | DGA | INSPECTION | Generally, furanic compounds are extracted from the oil either by solvent extraction or solid phase extraction and measured by High Performance Liquid Chromatography (HPLC) with an UV detector. Furfuraldehyde/Furanic concentration can be measured colorimetrically using spectrophotometer. This method is rapid and accurate and measures only 2-Furfuraldehyde or 2-furfural (FAL) in oil. This technique is useful for quick screening of Furfuraldehyde in transformer oil. When DGAs are required, always request that furans testing be completed by the laboratory to check for paper deterioration. In | Generally, furanic compounds are extracted from the oil either by solvent extraction or solid phase extraction and measured by High Performance Liquid Chromatography (HPLC) with an UV detector. Furfuraldehyde/Furanic concentration can be measured colorimetrically using spectrophotometer. This method is rapid and accurate and measures only 2-Furfuraldehyde or 2-furfural (FAL) in oil. This technique is useful for quick screening of Furfuraldehyde in transformer oil. When DGAs are required, always request that furans testing be completed by the laboratory to check for paper deterioration. In | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 200 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0518 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | healthy transformers, there are no detectable furans in the oil, or they are less than 100 part per billion (ppb). Normal deterioration of paper is characterized by rate of furan evolution as 50-90 ppb per year. Large amount of furans can be generated when temperature is above 120-130 deg. C. In cases where significant damage to paper insulation from heat has occurred, furan levels have been found to be at least 100 ppb and up to 70,000 ppb. The monitoring of furanic compounds by annual sampling of the oil and its analysis using High Performance Liquid Chromatography (HPLC) has been under used for condition monitoring on a routine basis for some in recent years by some utilities. 4.0 Monitoring of leakage of oil from Transformer / reactor and other maintenance checks | NOT COVERED | The monitoring of furanic compounds by annual sampling of the oil and its analysis using High Performance Liquid Chromatography (HPLC) has been u | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 201 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0519 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Inspection | Transformer Oil | INSPECTION | Leakage of Oil from transformer/reactor is considered as a serious quality lapse on the part of the Original Equipment Manufacturer (OEM) as no leakage of oil is expected during the operating life of the transformer/reactor. The utility should monitor and conduct visual inspection of the transformer/reactor tank and other body parts like pipes, flange joints in pipes, valves & its stems, oil pump, radiators, headers, screw joints, gasket joints, weld joints, and air bleed plugs, etc. regularly (on quarterly basis) to check any rusting and any leakage of oil. The records of inspection should be maintained properly. If leakage is noticed, the cause of such leakage shall be investigated and following action may be taken in consultation with OEM. | Leakage of Oil from transformer/reactor is considered as a serious quality lapse on the part of the Original Equipment Manufacturer (OEM) as no leakage of oil is expected during the operating life of the transformer/reactor. The utility should monitor and conduct visual inspection of the transformer/reactor tank and other body parts like pipes, flange joints in pipes, valves & its stems, oil pump, radiators, headers, screw joints, gasket joints, weld joints, and air bleed plugs, etc. regularly (on quarterly basis) to check any rusting and any leakage of oil. The records of inspection should be maintained properly. If leakage is noticed, the cause of such leakage shall be investigated and following action may be taken in consultation with OEM. | regularly (on quarterly basis) to check any rusting and any leakage of oil | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 201 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0520 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | (a) Leakage at Screw joints: The presence of foreign material in threads, oval nipples, poor threads, improper fillers, and improper assembly can cause leakage through screw joints. It can be rectified with the proper tightening of screw joints & gasket joints. (b) Leakage at Pipe joints: The pipework leakage at pipe joints may be due to slack unions or badly seated joints. The pipes should be aligned properly and the union joints should be tightened. (c) Leakage at Gasket joint: Poor scarfed joints, insufficient or uneven compression, improper preparation of gasket surfaces can cause leakage at gasket locations. Gaskets sometimes shrink during service. It is, therefore, necessary to check the tightness of all bolts fastening gasketted joints. The bolts should be tightened to the correct pressure, evenly around the joints to avoid uneven pressure. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 201 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0521 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | (d) Leakage at Weld joint: The imperfect welds, material impurities, stress during transportation etc., can cause leakage in weld locations. If it is due to a defective weld, the same should be rectified after consulting the OEM. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | (d) Leakage at Weld joint: The imperfect welds, material impurities, stress during transportation etc., can cause leakage in weld locations. If it is due to a defective weld, the same should be rectified after consulting the OEM. | Transformers and reactors, 66 kV and above voltage class | PDF p. 202 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0522 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, AIS, OLTC, Bushing | Power Transformer | Safety | Transformer Oil | SAFETY | Apart from Condition Monitoring tests and monitoring of leakage of oil, regular maintenance checks such as checking of oil level in bushing/conservator/OLTC conservator, manual actuation of cooler fans/pumps, checking condition of silica gel, cleaning of bushings etc. are equally important and should not be ignored. Such checks and their periodicity has been mentioned in the table given in the Appendix. 5.0 Transformer Assessment Indices (TAIs) A Transformer Assessment Indices (TAIs) is one method that may help identify the transformers which most urgently need attention or intervention. The CIGRE document on Condition assessment of Power transformers (Reference /Brochure -761- WG A2.49) gives details on TAI. 6.0 Recommended, as-needed, and optional maintenance tests as per IEEE Std C57.152-2013 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Apart from Condition Monitoring tests and monitoring of leakage of oil, regular maintenance checks such as checking of oil level in bushing/conservator/OLTC conservator, manual actuation of cooler fans/pumps, checking condition of silica gel, cleaning of bushings etc. are equally important and should not be ignored. Such checks and their periodicity has been mentioned in the table given in the Appendix. 5.0 Transformer Assessment Indices (TAIs) A Transformer Assessment Indices (TAIs) is one method that may help identify the transformers which most urgently need attention or intervention. The CIGRE document on Condition assessment of Power transformers (Reference /Brochure -761- WG A2.49) gives details on TAI. 6.0 Recommended, as-needed, and optional maintenance tests as per IEEE Std C57.152-2013 | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 202 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0523 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | Power Transformer | Failure / Failure Analysis | Commissioning | FAILURE_ANALYSIS | As per IEEE Std C57.152-2013, recommended, as-needed, and optional maintenance tests typically performed on liquid-filled power transformers during their commissioning, while they are in service, and after protection trips caused by either a system fault or an internal fault is given below. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | As per IEEE Std C57.152-2013, recommended, as-needed, and optional maintenance tests typically performed on liquid-filled power transformers during their commissioning, while they are in service, and after protection trips caused by either a system fault or an internal fault is given below. | Transformers and reactors, 66 kV and above voltage class | PDF p. 202 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0524 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Bushing | TESTING | Arresters REC REC REC Opt Bushing CTs REC AN AN AN REC = Recommended AN = As needed based on the REC Test results Opt = Optional based on the AN test results N/A = Not Applicable | Arresters REC REC REC Opt Bushing CTs REC AN AN AN REC = Recommended AN = As needed based on the REC Test results Opt = Optional based on the AN test results N/A = Not Applicable | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 204 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0525 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Distribution Transformer, Transformer | Distribution Transformer | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | aNewly installed or repaired units prior to energization bIn-service transformers may need to be de-energized and properly set up, depending on the test to be performed. Condition-based maintenance practice-oil quality, DGA, and Furan tests-may be carried out at a regular interval and the necessity of other tests depend upon the assesses condition for power and distribution transformers. For hermetically sealed distribution transformers, the first round of tests after commissioning may be time based, and thereafter, the frequency should depend on the assessed condition. cAfter tripping of transformer due to system faults such as overcurrent. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | aNewly installed or repaired units prior to energization bIn-service transformers may need to be de-energized and properly set up, depending on the test to be performed. Condition-based maintenance practice-oil quality, DGA, and Furan tests-may be carried out at a regular interval and the necessity of other tests depend upon the assesses condition for power and distribution transformers. For hermetically sealed distribution transformers, the first round of tests after commissioning may be time based, and thereafter, the frequency should depend on the assessed condition. cAfter tripping of transformer due to system faults such as overcurrent. | Transformers and reactors, 66 kV and above voltage class | PDF p. 204 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0526 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | General | FAILURE_ANALYSIS | dAfter tripping of transformer due to internal faults such as differential tripping (before repair). eFuran Testing recommended for generator step-up(GSU) transformers and units operated above nameplate. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | dAfter tripping of transformer due to internal faults such as differential tripping (before repair). eFuran Testing recommended for generator step-up(GSU) transformers and units operated above nameplate. | Transformers and reactors, 66 kV and above voltage class | PDF p. 204 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0527 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance | General | MAINTENANCE | 7.0 Life Cycle Management of Transformer/Reactor Life Cycle Management is an integrated, information driven approach to all aspects of a product’s life from its design inception, through its manufacture, deployment and maintenance, and culminating in its removal from service and final disposal. The entire process can be summarized as shown: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 204 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0528 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | General | MAINTENANCE | The problems encountered in Operation & Maintenance and the measures felt necessary to enhance life of Equipment can be made part of relevant specifications, standards and maintenance practices. The feedback may also be relevant to the equipment manufacturer as well. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 205 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0529 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | For assessing the remaining life of an Equipment – Paper condition, Oil Condition and Equipment loading needs to be assessed separately. In addition to the tests mentioned above the following tests shall be useful in predicting the Residual Life of the equipment: | For assessing the remaining life of an Equipment – Paper condition, Oil Condition and Equipment loading needs to be assessed separately. In addition to the tests mentioned above the following tests shall be useful in predicting the Residual Life of the equipment: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 205 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0530 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE |  Furan Content  Degree of Polymerisation  Frequency Domain Spectrometry Results for Transformer  Oil Parameters like Inhibitor content, Acidity, Sludge, etc  Temperature & Loading Profile Life Extension can then be achieved based on systematically analysing and addressing the problematic area on a techno economic basis. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 206 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0531 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Condition Monitoring Tests, its frequency and acceptable values for Transformers and Reactors | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 207 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0532 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | (d) Checking of oil leaks Monthly (e) Checking condition of silica gel in breather Monthly (f) Checking of oil level in oil seal of breather Monthly (g) Manual actuation of cooler fans and oil pumps Monthly (h) External cleaning of all bushings Yearly (i) External cleaning of radiators Yearly | NOT COVERED | (d) Checking of oil leaks Monthly (e) Checking condition of silica gel in breather Monthly (f) Checking of oil level in oil seal of b | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 210 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0533 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Testing | Transformer Oil | TESTING | (k) Maintenance of OLTC driving mechanism Yearly (l) Checking/testing of buchholz relay by oil draining Yearly | NOT COVERED | (k) Maintenance of OLTC driving mechanism Yearly (l) Checking/testing of buchholz relay by oil draining Yearly | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 210 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0534 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Note: The frequency of test needs to be increased based on the analysis of trend of the test results. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 210 | Chapter-6: Condition Monitoring and Life Cycle Management | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0535 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | ONAN / ONAF1 / ONAF2 8. Rating at different cooling % 60 / 80 / 100 9. Cooler Bank Arrangement 2 X 50% 10. Frequency Hz 50 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 215 | SPECIFIC TECHNICAL REQUIREMENT | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0536 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | 21. Bushing i) Rated voltage HV kV 800 IV kV 420 LV kV 52 Neutral kV 36 ii) Rated current HV A 2500 IV A 2500 LV A 1250 Neutral A 3150 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 216 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0537 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | HV kVrms 570 IV kVrms 395 LV kVrms 95 Neutral kVrms 38 v) Neutral Grounding Solidly grounded vi) Insulation HV Graded IV Graded LV Uniform vii) Tertiary Connection Ungrounded Delta viii) Tan delta of winding % ≤0.5 22. Bushing i) Rated voltage HV kV 420 IV kV 245 LV kV 52 Neutral kV 36 ii) Rated current HV A 1250 | NOT COVERED | NOT VERIFIED | 38 v | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 220 | O C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0538 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | HV kVrms 570 IV kVrms 395 LV kVrms 95 Neutral kVrms 38 v) Neutral Grounding Solidly grounded vi) Insulation HV Graded IV Graded LV Uniform vii) Tertiary Connection Ungrounded Delta viii) Tan delta of winding % ≤0.5 22. Bushing i) Rated voltage HV kV 420 IV kV 245 LV kV 52 Neutral kV 36 ii) Rated current HV A 1250 IV A 2000 LV A 1250 | NOT COVERED | NOT VERIFIED | 38 v | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 224 | O C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0539 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | HV kVrms 570 IV kVrms 395 LV kVrms 95 Neutral kVrms 38 v) Neutral Grounding Solidly grounded vi) Insulation HV Graded IV Graded LV Uniform vii) Tertiary Connection Ungrounded Delta viii) Tan delta of winding % ≤0.5 22. Bushing i) Rated voltage HV kV 420 IV kV 245 LV kV 52 Neutral kV 36 ii) Rated current HV A 1250 IV A 1250 LV A 1250 | NOT COVERED | NOT VERIFIED | 38 v | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 228 | O C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0540 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | ONAN / ONAF1 / ONAF2 8. Rating at different cooling % 60 / 80 / 100 9. Cooler Bank 2 X 50% 10. Frequency Hz 50 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 231 | S. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0541 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | ONAN/ONAF / ODAF or ONAN / ONAF1 /ONAF2 8. Rating at different cooling % 60 / 80 / 100 9. Frequency Hz 50 10. Cooler Bank Arrangement 2 X 50% 11. Tap Changer i) Type On-load tap changer | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 253 | 10.0 (a) 100 MVA, 220/33 kV 3-ph Power Transformer | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0542 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | HV kVrms 395 LV kVrms 70 HV Neutral kVrms 38 LV neutral 70 v) Neutral Grounding (HV & LV) Solidly grounded vi) Insulation HV Graded LV Uniform vii) Tan delta of winding % ≤ 0.5 21. Bushing i) Rated voltage HV kV 245 LV kV 36 HV Neutral kV 36 LV Neutral kV 36 ii) Rated current HV A 1250 LV A 3150 HV Neutral A 3150 LV neutral 3150 iii) Lightning Impulse withstand Voltage HV kVp 1050 LV kVp 170 HV Neutral kVp 170 LV neutral kVp 170 iv) Switching Impulse withstand | NOT COVERED | NOT VERIFIED | 70 v | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 254 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0543 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | HV kVrms 505 LV kVrms 77 HV Neutral kVrms 77 LV Neutral kVrms 77 vi) Tan delta of bushing at ambient | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 255 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0544 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | vii) Minimum total creepage distances (Specific creepage distance: 31mm/kV corresponding to the line to line highest system voltage) HV bushing mm 7595 | NOT COVERED | NOT VERIFIED | 31mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 255 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0545 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | 230 (110 kV) LV kVrms 70 HV Neutral kVp 38 LV Neutral kVp 70 v) Neutral Grounding (HV and LV) Solidly grounded vi) Insulation HV Graded LV Uniform vii) Tan delta of winding % ≤0.5% 22. Bushings | NOT COVERED | NOT VERIFIED | 110 kV; 70 v | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 257 | O C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0546 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | HV kVrms 140 LV & LV Neutral kVrms 28 iv) Insulation Solidly grounded HV Uniform LV Uniform v) Tan delta of winding % ≤0.5 20. Bushings i) Rated voltage HV kV 72.5 LV & LV Neutral kV 17.5 ii) Rated current HV A 800 LV & LV neutral A 2000 iii) Lightning Impulse withstand | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 261 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0547 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | OLTC connection and range, vector group and the winding configuration (if necessary) are to be matched. 2. No external or internal Transformers/ Reactors are to be used to achieve | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 262 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0548 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | other two units. 17. System earthing HV Solidly earthed LV Unearthed 18. Maximum temperature rise over | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 264 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0549 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | units. 17. System earthing HV Solidly earthed LV Unearthed 18. Maximum temperature rise over | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 268 | 12 to | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0550 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | system voltage) HV mm 13020 HV neutral and LV mm 1116 28. Terminal arrangement HV line end Condenser bushing (Oil to air or Oil to SF6 or Oil to Oil) as per specification LV line end Isolated phase bus duct flange | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 269 | LV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0551 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | HV neutral Outdoor oil communicating type bushing (36kV) 29. Minimum phase spacing of the LV | NOT COVERED | NOT VERIFIED | 36kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 270 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0552 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | application 8. Applicable standard IEC 60076 9. Type of cooling OFWF or ODWF 10. No. of coolers 2x 100% (oil to water heat | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 271 | S. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0553 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | exchangers) No of oil pumps: 2 x 100% 11. Connection on HV / LV Star/ Delta (after 3-phase | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 271 | S. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0554 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | formation) 13. Rated frequency Hz 50 14. % impedance at 75°C As per IEC 60076-5 15. Maximum temperature rise at rated power | NOT COVERED | NOT VERIFIED | 75°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 271 | S. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0555 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | connection arrangement LV terminal Oil to air bushing HV neutral terminal Oil to air bushing 25. Transportation restriction if any As specified by the utility | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 273 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0556 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 6. Frequency Hz 50 7. No of Phases 1 (Single) 8. Reference standard IEC 60076-6 9. Service Outdoor 10. Duty Continuous at 800/√3kV | NOT COVERED | NOT VERIFIED | 3kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 274 | REACTORS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0557 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | vii) Minimum creepage distance (Specific Creepage Distance: of 31mm/kV corresponding to highest line to line voltage) Line bushing mm 24800 | NOT COVERED | NOT VERIFIED | 31mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 276 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0558 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 2. Rated Voltage (Ur) (1.0 pu) kV 420 3. Number of phases 3 (three) 4. Connection Star 5. Cooling type ONAN 6. Frequency Hz 50 7. Reference standard IEC 60076-6 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 277 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0559 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | vii) Minimum creepage distance (Specific Creepage Distance: of 31mm/kV corresponding to highest line to line voltage) Line bushing mm 13020 | NOT COVERED | NOT VERIFIED | 31mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 278 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0560 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 1. Rated Voltage, Ur (1p.u) kV 245 2. Rated Capacity at 245 kV MVAr 25 50 3. Connection Star with neutral brought out 4. Cooling System ONAN 5. Frequency Hz 50 6. No of Phases 3 (Three) 7. Reference Standard IEC 60076-6 8. Service Outdoor 9. Permissible un-balance current | NOT COVERED | NOT VERIFIED | 245 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 280 | 25 MVAr & 50 MVAr, 245 kV 3-phase Shunt Reactor | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0561 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | Line end kVrms 395 Neutral kVrms 70 v) Tan delta of windings < 0.005 17. Bushing i) Rated voltage Line end kV 245 | NOT COVERED | NOT VERIFIED | 70 v | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 281 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0562 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 19.0 Technical Parameters of Oil filled Neutral Grounding Reactor (NGR) S. No. Description Unit Parameters 1. Rated voltage from insulation kV 145 2. Connection Between neutral of reactor | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 283 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0563 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | and ground 3. Cooling System ONAN 4. Cooling medium Insulating oil 5. Frequency Hz 50 6. No of Phases 1 (Single) 7. Service Outdoor 8. Insulation Graded 9. Max. continuous current (rms) 10 A 10. Rated short time current (rms) 60 A for 10 seconds | NOT COVERED | NOT VERIFIED | 10 A; 60 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 283 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0564 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | i) Top oil measured by thermometer °C 45 ii) Winding measured by resistance °C 50 13. Insulation level for winding i) Lightning Impulse withstand | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 283 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0565 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Design / Technical Reference | Grounding | DESIGN_REFERENCE | 15. Method of grounding Solidly connected between neutral of shunt reactor and earth 16. Whether neutral is to be brought | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 284 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0566 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Surge Arrester | NOT VERIFIED | Failure / Failure Analysis | Surge Arrester | FAILURE_ANALYSIS | NOTE: The rating of Surge Arrester for NGR of 765kV reactor need to be decided based on proper study in view of failure of NGR. | NOT COVERED | NOT VERIFIED | 765kV | NOT COVERED | NOTE: The rating of Surge Arrester for NGR of 765kV reactor need to be decided based on proper study in view of failure of NGR. | Transformers and reactors, 66 kV and above voltage class | PDF p. 285 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0567 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | ground 3. Cooling System AN 4. Cooling medium Insulating oil 5. Frequency Hz 50 6. No of Phases 1 (Single) 7. Service Outdoor 8. Insulation Uniform 9. Max. continuous current (rms) 20 A 10. Rated short time current (rms) for | NOT COVERED | NOT VERIFIED | 20 A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 285 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0568 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Annexure-B: Technical Parameters of Bushing Current Transformers & Neutral Current | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 286 | TECHNICAL PARAMETERS OF BUSHING CURRENT TRANSFORMERS & | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0569 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, CT | Current Transformer | Design / Technical Reference | Grounding | DESIGN_REFERENCE | 11.0 Technical Parameters of Current Transformers for 125 MVAR (3-ph), 80 MVAR (3-ph) & 63 MVAR (3-ph), 420 kV Shunt Reactor & Neutral Grounding Reactor (NGR) | NOT COVERED | NOT VERIFIED | 125 MVAR; 80 MVAR; 63 MVAR; 420 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 297 | 80 MVAR (3-ph) & 63 MVAR (3-ph), 420 kV Shunt Reactor & Neutral | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0570 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | 8. Rated Capcity / Full load rating (HV/IV/LV) MVA 9. 3-Phase/Bank of Three Single Phase (A,B,C) 10. Rated No Load Voltages (HV/IV/LV) kV 11. Currents at normal tap (HV/IV/LV) Amp 12. Rated Frequency Hz 13. Connections and phase displacement symbols (Vector Group) 14. Weight Schedules (Minimum with no negative tolerance) i) Active part (Core + coil ) kg ii) Insulating Oil (excluding mass of extra oil) kg iii) Tank and Fittings kg iii) Total weight kg iv) Transportaion Weight kg v) Overall dimensions L x B x H mm vi) Size of heaviest package L x B x H mm | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 302 | MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0571 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC | NOT VERIFIED | Design / Technical Reference | OLTC | DESIGN_REFERENCE | 17. Tappings i)Type (OLTC/OCTC) and make of tap changer ii)Position of Tapping on the winding iii)Variation on iv)Range of variation v)No. of Steps vi) Whether control suitable for: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 303 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0572 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | i) Guaranteed No load loss at rated voltage and frequency kW Tolerance (to be considered for loss evaluation) % ii) Guranteed I2R Loss at rated current & frequency (at 750C) at principal | NOT COVERED | NOT VERIFIED | 750C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 303 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0573 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Tolerance (to be considered for loss evaluation) % iii) Eddy current and stray loss at rated current & frequency (at 750C) at | NOT COVERED | NOT VERIFIED | 750C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 303 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0574 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | v) Guaranteed Auxiliary loss at rated voltage and frequency kW Tolerance (to be considered for loss evaluation) % vi) Calculated Fan Loss kW vii) Calculated Pump Loss kW viii) Air core reactance of HV winding % ix) Guaranteed Impedance (at Highest MVA base) % (a) HV-IV (at Pricipal tap) (b) HV-LV(at Pricipal tap) (c) IV-LV(at Pricipal tap) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 304 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0575 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Capacitance | TESTING | Tolerance % xi) Zero sequence impedance at principal tap (for 3-phase transformers) 19. Capacitance to earth for HV/IV/LV pF 20. Regulation at full load at 75 0C winding temperature at: a) upf b) 0.8 pf | NOT COVERED | NOT VERIFIED | 0C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 304 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0576 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 23. Load at Maximum efficiency % 24. Any limitations in carrying out the required test? If Yes, State limitations | 23. Load at Maximum efficiency % 24. Any limitations in carrying out the required test? If Yes, State limitations | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 305 | 0.8 lead | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0577 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 10. W/kg at working flux density 11. Building Factor Considered 12. Calculated No Load Loss at rated voltage and Frequency | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 307 | T | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0578 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 15. Core Isolation test kV 16. Core bolt in limb / yoke Yes/No 17. Core bolt insulation withstand voltage for one minute kV 18. Maximum temperature rise of any part of core or its support structure in | 15. Core Isolation test kV 16. Core bolt in limb / yoke Yes/No 17. Core bolt insulation withstand voltage for one minute kV 18. Maximum temperature rise of any part of core or its support structure in | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 307 | T | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0579 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 3. No. of Cooler banks (2x50% / 2x100% / 1x100% etc.) 4. Temperature gradient between windings and oil 5. Time in minutes for which the transformer can run at full load without | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 309 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0580 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | i) Top Oil by thermometer ii) Average Winding by resistance iii) Winding hot spot | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 310 | 0C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0581 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | i) Radiator Bank ii) Oil to Air Heat Exchanger (Unit Cooler) iii) Oil to Water Cooler (Single Tube) iv) Oil to Water Cooler (Double Tube) v) Tank Mounted vi) Header Mounted vii) Separately Mounted viii) Degree of Protection of terminal box | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 310 | 0C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0582 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Coolers (Oil to Water): i) Quantity (Running + Standby) ii) Type and Rating iii) Oil flow rate (lpm) iv) Water flow rate (lpm) v) Nominal Cooling rate (kW) vi) Material of tube | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 311 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0583 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | 13. Cooler loss at rated output, normal ratio, rated voltage, rated frequency at | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 311 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0584 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | iii) Temperature sensors by fiber optic (if provided) iv) Oil actuated/gas operated relay | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 315 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0585 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | i) IS 335 / IEC60296 / as per specification ii) Inhibited/ un-inhibited iii) Mineral / Natural Ester / Synthetic Ester iv) Spare oil as percentage of first filling | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 317 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0586 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | v) Manufacturer vi)Quantity of oil (before filling and before commissioning) vii)Moisture content (mg/L or ppm) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 317 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0587 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | x) Breakdown Voltage (before and after treatment) (kV) xi) Interfacial tension at 20 oC (N/m) xi) Pour point (oC) xii) Flash point(oC) xiii) Acidity (mg KOH/gm) xiv) Inhibitors (for inhibited oil) (%) xv) Oxidation Stability | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | x) Breakdown Voltage (before and after treatment) (kV) xi) Interfacial tension at 20 oC (N/m) xi) Pour point (oC) xii) Flash point(oC) xiii) Acidity (mg KOH/gm) xiv) Inhibitors (for inhibited oil) (%) xv) Oxidation Stability | Transformers and reactors, 66 kV and above voltage class | PDF p. 318 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0588 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | 20. Provision for fire protection system (as per spec), if yes, provide details Y/N | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 20. Provision for fire protection system (as per spec), if yes, provide details Y/N | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 318 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0589 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | a. Core b. Windings c. Tank d. Fittings e. Oil f. Total weights of complete transformers with oil and fittings | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 318 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0590 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | 17. Vibration and tank stress at rated voltage 18. Rated Frequency Hz 19. Winding Connection 20. Weight Schedules (Minimum with no negative tolerance) i) Active part (Core + coil) kg ii) Insulating Oil (excluding mass of extra oil) kg iii) Tank and Fittings kg iv) Total weight kg v) Transportaion Weight kg vi) Overall dimensions L x B x H mm vii) Size of heaviest package L x B x H mm | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 321 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0591 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | i) Guaranteed Max. Total loss at rated current and frequency (at 750C) kW Tolerance % ii) Guranteed I2R Loss at rated current & frequency (at 750C) kW | NOT COVERED | NOT VERIFIED | 750C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 321 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0592 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | iii) Tolerance % iv) Reactance at rated voltage & frequency ohms v) Range of constant impedance vi) Ratio of zero sequence reactance to positive reactance (X0/X1) 23. Any limitations in carrying out the required test? If Yes, State limitations | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 322 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0593 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 2. No. of Cooler banks (2x50% / 2x100% / 1x100% etc.) 3. Temperature gradient between windings and oil 4. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 325 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0594 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Tan Delta | SAFETY | ground end i) Lightning Impulse withstand voltage (1.2/50µs) kVp ii) Chopped wave Lightning Impulse withstand voltage kVp iii) Switching Impulse withstand voltage (250/2500µs) kVp iv) Power frequency withstand voltage (one minute / 5 minutes) kVrms 2 Tan delta of windings at ambient Temperature % F. ACCESSORIES | NOT COVERED | NOT VERIFIED | 5 minutes | ground end i) Lightning Impulse withstand voltage (1.2/50µs) kVp ii) Chopped wave Lightning Impulse withstand voltage kVp iii) Switching Impulse withstand voltage (250/2500µs) kVp iv) Power frequency withstand voltage (one minute / 5 minutes) kVrms 2 Tan delta of windings at ambient Temperature % F. ACCESSORIES | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 326 | E. DIELECTRIC SYSTEM | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0595 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 5. Conservator: i) Total volume ii) Volume between highest and lowest visible oil levels | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 329 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0596 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Transformer Oil | COMMISSIONING | i) IS 335 / IEC60296 / as per specification ii) Inhibited/ un-inhibited iii) Mineral / Natural Ester / Synthetic Ester iv) Spare oil as percentage of first filling v) Manufacturer vi) Quantity of oil (before filling and before commissioning) vii) Moisture content (mg/L or ppm) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 330 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0597 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Failure / Failure Analysis | Tan Delta | FAILURE_ANALYSIS | viii) Tan delta (Dielectric Dissipation Factor) at 90oC ix) Resistivity (Ω-cm)) x) Breakdown Voltage (before and after treatment) (kV) xi) Interfacial tension at 20 oC (N/m) xii) Pour point (oC) xiii) Flash point(oC) xiv) Acidity (mg KOH/gm) xv) Inhibitors (for inhibited oil) (%) xvi) Oxidation Stability | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | viii) Tan delta (Dielectric Dissipation Factor) at 90oC ix) Resistivity (Ω-cm)) x) Breakdown Voltage (before and after treatment) (kV) xi) Interfacial tension at 20 oC (N/m) xii) Pour point (oC) xiii) Flash point(oC) xiv) Acidity (mg KOH/gm) xv) Inhibitors (for inhibited oil) (%) xvi) Oxidation Stability | Transformers and reactors, 66 kV and above voltage class | PDF p. 331 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0598 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | 19. Provision for fire protection system (as per spec), if yes, provide details Y/N | NOT COVERED | NOT VERIFIED | NOT VERIFIED | 19. Provision for fire protection system (as per spec), if yes, provide details Y/N | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 331 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0599 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | *The requirements of the IVW test can be incorporated in the IVPD test so that only one test is required. | *The requirements of the IVW test can be incorporated in the IVPD test so that only one test is required. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 335 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0600 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Earthing | TESTING | General Tests shall be carried out as per following procedure. However, IS 2026/IEC 60076 (with latest amendments) shall be followed in general for other tests. Manufacturer shall offer the transformer unit for type testing with all major fittings including radiator bank, Marshalling Box, Common Marshalling Box, RTCC (as applicable) assembled. 1. Core assembly dielectric and earthing continuity test | General Tests shall be carried out as per following procedure. However, IS 2026/IEC 60076 (with latest amendments) shall be followed in general for other tests. Manufacturer shall offer the transformer unit for type testing with all major fittings including radiator bank, Marshalling Box, Common Marshalling Box, RTCC (as applicable) assembled. 1. Core assembly dielectric and earthing continuity test | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 340 | 60076 (with latest amendments) shall be followed in general for other tests. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0601 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Insulation Resistance | TESTING | After assembly each core shall be tested for 1 minute at 2000 Volts between all yoke clamps, side plates and structural steel work (core to frame, frame to tank & core to tank). The insulation of core to tank, core to yoke clamp (frame) and yoke clamp (frame) to tank shall be able to withstand a voltage of 2 kV (DC) for 1 minute. Insulation resistance shall be minimum 1 GΩ for all cases mentioned above. 2. Measurement of winding resistance | After assembly each core shall be tested for 1 minute at 2000 Volts between all yoke clamps, side plates and structural steel work (core to frame, frame to tank & core to tank). The insulation of core to tank, core to yoke clamp (frame) and yoke clamp (frame) to tank shall be able to withstand a voltage of 2 kV (DC) for 1 minute. Insulation resistance shall be minimum 1 GΩ for all cases mentioned above. 2. Measurement of winding resistance | NOT VERIFIED | 1 minute; 2 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 340 | 60076 (with latest amendments) shall be followed in general for other tests. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0602 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | The short-circuit impedance and load loss for a pair of windings shall be measured at rated current & frequency with voltage applied to the terminals of one winding, with the terminals of the other winding short-circuited, and with possible other windings open circuited. The difference in temperature between the top and bottom liquid shall not exceed 5 K. To obtain this result | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 340 | 60076 (with latest amendments) shall be followed in general for other tests. | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0603 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | more rapidly, the liquid may be circulated by a pump. Loss measurement for all combinations (HV-IV, HV-LV, IV-LV and at Normal and extreme taps). 5. Short term heat run test (Not Applicable for unit on which temperature | more rapidly, the liquid may be circulated by a pump. Loss measurement for all combinations (HV-IV, HV-LV, IV-LV and at Normal and extreme taps). 5. Short term heat run test (Not Applicable for unit on which temperature | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 341 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0604 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | DGA | FAILURE_ANALYSIS | In addition to the type test for temperature rise conducted on one unit, each cooling combination shall routinely be subjected to a short term heat run test to confirm the performance of the cooling system and the absence of manufacturing defect such as major oil flow leaks that may bypass the windings or core. DGA samples shall be taken at intervals to confirm the gas evolution. For ODAF or OFAF cooling, the short term heat run test shall be done with the minimum number of pumps for full load operation in order to shorten the temperature build up. Each short term heat run test is nevertheless expected to take about 3 hours. For ODAF or OFAF cooled transformers an appropriate cross check shall be performed to prove the effective oil flow through the windings. | NOT COVERED | NOT VERIFIED | 3 hours | NOT COVERED | In addition to the type test for temperature rise conducted on one unit, each cooling combination shall routinely be subjected to a short term heat run test to confirm the performance of the cooling system and the absence of manufacturing defect such as major oil flow leaks that may bypass the windings or core. DGA samples shall be taken at intervals to confirm the gas evolution. For ODAF or OFAF cooling, the short term heat run test shall be done with the minimum number of pumps for full load operation in order to shorten the temperature build up. Each short term heat run test is nevertheless expected to take about 3 hours. For ODAF or OFAF cooled transformers an appropriate cross check shall be performed to prove the effective oil flow through the windings. | Transformers and reactors, 66 kV and above voltage class | PDF p. 341 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0605 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, AIS | NOT VERIFIED | Testing | Transformer Oil | TESTING | For this purpose the effect on the temperature decay by switching the pumps off/ on at the end of the heat run should demonstrate the effectiveness of the additional oil flow. Refer to SC 12, 1984 cigre 1984 SC12-13 paper by Dam, Felber, Preiniger et al. Short term heat run test may be carried out with the following sequence:  Heat run test with pumps running but oil not through coolers.  Raise temperature to 5 deg less than the value measured during temperature rise test.  Stop power input and pumps for 6 minutes and observe cooling down trend  Restart pumps and observe increased cooling trend due to forced oil flow This test is applicable for the Transformer without Pump also (ONAN or ONAF rating). | For this purpose the effect on the temperature decay by switching the pumps off/ on at the end of the heat run should demonstrate the effectiveness of the additional oil flow. Refer to SC 12, 1984 cigre 1984 SC12-13 paper by Dam, Felber, Preiniger et al. Short term heat run test may be carried out with the following sequence:  Heat run test with pumps running but oil not through coolers.  Raise temperature to 5 deg less than the value measured during temperature rise test.  Stop power input and pumps for 6 minutes and observe cooling down trend  Restart pumps and observe increased cooling trend due to forced oil flow This test is applicable for the Transformer without Pump also (ONAN or ONAF rating). | NOT VERIFIED | 6 minutes | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 341 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0606 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, AIS | NOT VERIFIED | Testing | Transformer Oil | TESTING | For such type of transformer test may be carried out with the following sequence: Arrangement shall be required with pump of suitable capacity (considering the oil velocity) without cooler bank.  Raise the oil temperature 20-25 deg C above ambient.  Stop power input and pumps for 6 minutes and observe cooling down trend.  Restart pumps and observe increased cooling trend due to forced oil flow. | For such type of transformer test may be carried out with the following sequence: Arrangement shall be required with pump of suitable capacity (considering the oil velocity) without cooler bank.  Raise the oil temperature 20-25 deg C above ambient.  Stop power input and pumps for 6 minutes and observe cooling down trend.  Restart pumps and observe increased cooling trend due to forced oil flow. | NOT VERIFIED | 6 minutes | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 341 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0607 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | A routine over excitation test at 1.05 p.u voltage for 12 hours shall be done on the tap position giving the highest flux. This test shall be carried out immediately after the routine short-term heat run test on the transformer. The rate of gas development during the test shall be evaluated using IEEE/IEC/CIGRE guidelines. 7. Temp. Rise Test as per IEC: 60076 | A routine over excitation test at 1.05 p.u voltage for 12 hours shall be done on the tap position giving the highest flux. This test shall be carried out immediately after the routine short-term heat run test on the transformer. The rate of gas development during the test shall be evaluated using IEEE/IEC/CIGRE guidelines. 7. Temp. Rise Test as per IEC: 60076 | NOT VERIFIED | 12 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 342 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0608 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | Transformer Oil | TESTING | Headspace extraction and Gas chromatographic analysis on oil shall also be conducted before, during and after this test and the values shall be recorded in the test report. The sampling shall be in accordance with IEC 60567. The temperature rise test shall be conducted at a tap for the worst combination of loading (3-Winding Loss) for the Top oil of the transformer. | Headspace extraction and Gas chromatographic analysis on oil shall also be conducted before, during and after this test and the values shall be recorded in the test report. The sampling shall be in accordance with IEC 60567. The temperature rise test shall be conducted at a tap for the worst combination of loading (3-Winding Loss) for the Top oil of the transformer. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 342 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0609 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | DGA | TESTING | 3-Winding Loss = HV (Max MVA) + IV(Max MVA) + LV (Max MVA). The Contractor before carrying out such test shall submit detailed calculations showing losses on various taps and for the three types of ratings of the transformer and shall recommend the combination that results in highest temperature rise for the test. The Temperature rise type test results shall serve as a “finger print” for the units to be tested only with short term heat run test. Headspace extraction and Gas chromatographic analysis on oil shall also be conducted before, during and after this test and the values shall be recorded in the test report. The sampling shall be in accordance with IEC 60567. Oil sample shall be drawn before and after heat run test and shall be tested for dissolved gas analysis. Oil sampling to be done 2 hours prior to commencement of temperature rise test. | 3-Winding Loss = HV (Max MVA) + IV(Max MVA) + LV (Max MVA). The Contractor before carrying out such test shall submit detailed calculations showing losses on various taps and for the three types of ratings of the transformer and shall recommend the combination that results in highest temperature rise for the test. The Temperature rise type test results shall serve as a “finger print” for the units to be tested only with short term heat run test. Headspace extraction and Gas chromatographic analysis on oil shall also be conducted before, during and after this test and the values shall be recorded in the test report. The sampling shall be in accordance with IEC 60567. Oil sample shall be drawn before and after heat run test and shall be tested for dissolved gas analysis. Oil sampling to be done 2 hours prior to commencement of temperature rise test. | NOT VERIFIED | 2 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 342 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0610 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | DGA | TESTING | Keep the pumps running for 2 hours before and after the heat run test. Take oil samples during this period. For ONAN/ONAF cooled transformers, sample shall not be taken earlier than 2 hours after shut down. The acceptance norms with reference to various gas generation rates shall be as per IEC 61181. The DGA results shall generally conform to IEC/IEEE/CIGRE guidelines. | Keep the pumps running for 2 hours before and after the heat run test. Take oil samples during this period. For ONAN/ONAF cooled transformers, sample shall not be taken earlier than 2 hours after shut down. The acceptance norms with reference to various gas generation rates shall be as per IEC 61181. The DGA results shall generally conform to IEC/IEEE/CIGRE guidelines. | NOT VERIFIED | 2 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 342 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0611 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | the maximum current tap for a minimum of 12 hours for ONAN/ONAF or ONAF1 and 24 hours for ODAF or OFAF or ONAF2 with saturated temperature for at least 4 hours while the appropriate power and current for core and load losses are supplied.  The total testing time, including ONAN heating up period, steady period | NOT COVERED | NOT VERIFIED | 12 hours; 24 hours; 4 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 343 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0612 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | and winding resistance measurements is expected to be about 48 hours.  DGA tests shall be performed before and after heat run test and DGA | and winding resistance measurements is expected to be about 48 hours.  DGA tests shall be performed before and after heat run test and DGA | NOT VERIFIED | 48 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 343 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0613 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Full details of the test arrangements, procedures and conditions shall be furnished with the test certificates and shall include at least the following. iii. General: | Full details of the test arrangements, procedures and conditions shall be furnished with the test certificates and shall include at least the following. iii. General: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 343 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0614 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Transformer Oil | SAFETY |  Purchaser’s order number and transformer site designation.  Manufacturer’s name and transformer serial number.  Rating of transformer  MVA  Voltages and tapping range  Number of phases  Frequency  Rated currents for each winding  Vector Group  Cooling Type  Measured no-load losses and load losses at 75° C.  Altitude of test bay.  Designation of terminals supplied and terminals strapped. iv. Top oil temperature rise test: | NOT COVERED | NOT VERIFIED | NOT VERIFIED |  Purchaser’s order number and transformer site designation.  Manufacturer’s name and transformer serial number.  Rating of transformer  MVA  Voltages and tapping range  Number of phases  Frequency  Rated currents for each winding  Vector Group  Cooling Type  Measured no-load losses and load losses at 75° C.  Altitude of test bay.  Designation of terminals supplied and terminals strapped. iv. Top oil temperature rise test: | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 343 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0615 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE |  time  Voltage between phases  Current in each phase and total power  Power in each phase and total power  Ambient temperature  Top oil temperature  Cooler inlet and outlet oil temperatures  Hot spot temperatures (make use of probes) (if applicable) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 343 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0616 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | with the corresponding series of thermal images (colour) during starting of the test then after every four hours till the temperature stabilised and finally during temperature stabilised for each rating (ONAN/ONAF/OFAF or ONAN/ONAF1/ONAF2). Notes: The probes may be left in position provided the reliability and integrity of unit will not be jeopardized during its long life expectancy. v. Winding temperature rise test | with the corresponding series of thermal images (colour) during starting of the test then after every four hours till the temperature stabilised and finally during temperature stabilised for each rating (ONAN/ONAF/OFAF or ONAN/ONAF1/ONAF2). Notes: The probes may be left in position provided the reliability and integrity of unit will not be jeopardized during its long life expectancy. v. Winding temperature rise test | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 344 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0617 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | oil and ambient air temperatures, together with the time required for the effect to disappear.  Record the thermal time constant of the winding.  Log the half-hourly readings of the quantities as for the top oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | oil and ambient air temperatures, together with the time required for the effect to disappear.  Record the thermal time constant of the winding.  Log the half-hourly readings of the quantities as for the top oil | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 344 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0618 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | temperature rise test.  Provide a table of readings, after shut-down of power, giving the | temperature rise test.  Provide a table of readings, after shut-down of power, giving the | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 344 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0619 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Winding Resistance | TESTING | a) Time after shut- down: b) Time increment: c) Winding resistance: At least 20 minutes reading d) Resistance increment: e) X, where x is the time after shut-down divided by the thermal time constant of the winding: and f) Y, where Y = 100 ( 1-e –x ) (Any graphical/computer method used to determine the temperature of a winding by extrapolation to the instant of power shut-down shall produce a linear curve.) | a) Time after shut- down: b) Time increment: c) Winding resistance: At least 20 minutes reading d) Resistance increment: e) X, where x is the time after shut-down divided by the thermal time constant of the winding: and f) Y, where Y = 100 ( 1-e –x ) (Any graphical/computer method used to determine the temperature of a winding by extrapolation to the instant of power shut-down shall produce a linear curve.) | NOT VERIFIED | 20 minutes | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 344 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0620 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | the determination of the winding temperatures at the instant of shut- down of power.  Record any action taken to remedy instability of the oil surge device | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 344 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0621 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | during initiation of the oil circulating pumps. Temperature measurements as per special probes or sensors (fibre optic) placed at various locations shall also be recorded. | during initiation of the oil circulating pumps. Temperature measurements as per special probes or sensors (fibre optic) placed at various locations shall also be recorded. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 344 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0622 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | The test shall be carried out on the tapping position that will cause the highest current under normal conditions. Hot spot temperature measurement shall be done by using temperature probes or sensors in approved locations. The transformer shall be fully erected as for service with all cooling equipment. i. Testing option 1: | The test shall be carried out on the tapping position that will cause the highest current under normal conditions. Hot spot temperature measurement shall be done by using temperature probes or sensors in approved locations. The transformer shall be fully erected as for service with all cooling equipment. i. Testing option 1: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 345 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0623 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Pre-load the unit with 100% of full load current for a period long enough to stabilise the top oil temperature with cooling as for service conditions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 345 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0624 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | transformer at the interval of every one hour.  Hold the overload current for a period of 4 hours.  Measure and record the hotspot temperatures. ii. Testing option 2: | transformer at the interval of every one hour.  Hold the overload current for a period of 4 hours.  Measure and record the hotspot temperatures. ii. Testing option 2: | NOT VERIFIED | 4 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 345 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0625 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Pre-load the unit with 100% of full load current for a period long enough to stabilise the top oil temperature with 100% cooling as per service conditions. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 345 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0626 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | Winding hotspot temperatures shall not exceed 130°C for option 1 and 135 °C for option 2. The temperature rise recorded by infra-red shall be not more than 10°K above top oil temperature or 15°K above the local oil temperature. The rate of gas development as determined from oil samples shall be determined. Samples shall be taken before and after the test and acceptance criteria shall be in accordance with IEC/IEEE guidelines. | Winding hotspot temperatures shall not exceed 130°C for option 1 and 135 °C for option 2. The temperature rise recorded by infra-red shall be not more than 10°K above top oil temperature or 15°K above the local oil temperature. The rate of gas development as determined from oil samples shall be determined. Samples shall be taken before and after the test and acceptance criteria shall be in accordance with IEC/IEEE guidelines. | NOT VERIFIED | 130°C; 135 °C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 345 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0627 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Full details of the test arrangements, procedures and conditions shall be supplied with the test certificates and shall include the following: | Full details of the test arrangements, procedures and conditions shall be supplied with the test certificates and shall include the following: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 346 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0628 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | General | SAFETY |  Purchaser’s reference number and site designation  Manufacturer’s name and transformer serial number  MVA rating and voltage ratio  Vector group  Altitude of test bay  Designation of terminals supplied and terminals strapped  Colour photographs of the four sides and top of the transformer. v. Overload test: | NOT COVERED | NOT VERIFIED | NOT VERIFIED |  Purchaser’s reference number and site designation  Manufacturer’s name and transformer serial number  MVA rating and voltage ratio  Vector group  Altitude of test bay  Designation of terminals supplied and terminals strapped  Colour photographs of the four sides and top of the transformer. v. Overload test: | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 346 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0629 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | A log of the following quantities taken at a minimum of 30-minute intervals:  time  voltage between phases  current in each phase  power in each phase and total power  ambient temperature  top oil temperature  cooler inlet and outlet temperatures  average winding temperatures  hot spot temperatures (make use of probes) Notes: Measurement methods for hot spots, their location and the number of sensors shall be agreed with Purchaser prior to the test. The probes may be left in position provided the reliability and integrity of the unit will not be jeopardized during its long life expectancy. 9. Dielectric Tests | A log of the following quantities taken at a minimum of 30-minute intervals:  time  voltage between phases  current in each phase  power in each phase and total power  ambient temperature  top oil temperature  cooler inlet and outlet temperatures  average winding temperatures  hot spot temperatures (make use of probes) Notes: Measurement methods for hot spots, their location and the number of sensors shall be agreed with Purchaser prior to the test. The probes may be left in position provided the reliability and integrity of the unit will not be jeopardized during its long life expectancy. 9. Dielectric Tests | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 346 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0630 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Following Test shall be performed in the sequence given below as per IEC 60076-3:2013 clause 7.2.3 shall be followed: a) Lightning impulse tests (LIC, LIN) b) Switching impulse (SI) c) Applied voltage test (AV) d) Line terminal AC withstand test (LTAC) e) Induced voltage test with partial discharge measurement (IVPD) | Following Test shall be performed in the sequence given below as per IEC 60076-3:2013 clause 7.2.3 shall be followed: a) Lightning impulse tests (LIC, LIN) b) Switching impulse (SI) c) Applied voltage test (AV) d) Line terminal AC withstand test (LTAC) e) Induced voltage test with partial discharge measurement (IVPD) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 346 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0631 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | General | SAFETY | 2.1: IV Terminal 3.1 & 3.2: LV or Tertiary Terminal Acceptance criteria Transfer surge at Tertiary should not exceed 250kVp at any conditions for 400kV Voltage class Transformer. For other transformer it shall be below the impulse level of LV winding. 11. Chopped wave & full wave lightning impulse test for the line terminals | NOT COVERED | NOT VERIFIED | 400kV | 2.1: IV Terminal 3.1 & 3.2: LV or Tertiary Terminal Acceptance criteria Transfer surge at Tertiary should not exceed 250kVp at any conditions for 400kV Voltage class Transformer. For other transformer it shall be below the impulse level of LV winding. 11. Chopped wave & full wave lightning impulse test for the line terminals | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 347 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0632 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | Chopped wave lightning impulse and Switching impulse test shall be performed at normal and extreme taps on Unit-1, Unit-2 and Unit-3 respectively for 1-Ph unit, otherwise R ph, Y Ph and B Ph respectively for 3- Ph unit. All the parameters as per IEC shall be mentioned in the report. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Chopped wave lightning impulse and Switching impulse test shall be performed at normal and extreme taps on Unit-1, Unit-2 and Unit-3 respectively for 1-Ph unit, otherwise R ph, Y Ph and B Ph respectively for 3- Ph unit. All the parameters as per IEC shall be mentioned in the report. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 347 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0633 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | Losses of each fan and pumps including spare shall be measured at rated voltage and frequency. Fans and Pumps shall be mounted with cooler bank as per approved drawing during measurement. Serial No, Applied voltage, measured current, frequency and make shall be furnished in the test report. 13. Short duration (LTAC) AC withstand test (LTAC) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 348 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0634 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, AIS | NOT VERIFIED | Testing | AIS | TESTING | For 765kv Class transformer, the IV terminal voltage shall be shall be raised to 570kVrms or below so that maximum HV voltage shall be shall be limited to 970kV rms. Test method shall be as per IEC. 14. Dynamic short circuit withstand test | For 765kv Class transformer, the IV terminal voltage shall be shall be raised to 570kVrms or below so that maximum HV voltage shall be shall be limited to 970kV rms. Test method shall be as per IEC. 14. Dynamic short circuit withstand test | NOT VERIFIED | 765kv; 970kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 348 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0635 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | The test shall be carried out as per IEC 60076-5. Dynamic short circuit test shall be carried out in HV-IV combination at nominal & extreme tap positions. For LV winding, dynamic short circuit shall be carried out either on HV-LV or IV-LV combination, whichever draws higher short circuit current as per calculation. Type tests shall be carried out before short circuit test. Following shall also be conducted before and after Short Circuit test: | The test shall be carried out as per IEC 60076-5. Dynamic short circuit test shall be carried out in HV-IV combination at nominal & extreme tap positions. For LV winding, dynamic short circuit shall be carried out either on HV-LV or IV-LV combination, whichever draws higher short circuit current as per calculation. Type tests shall be carried out before short circuit test. Following shall also be conducted before and after Short Circuit test: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 348 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0636 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance Schedule | DGA | SCHEDULE | i) Dissolved gas analysis ii) Frequency response analysis iii) All routine tests | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 348 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0637 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Detail test procedure shall be submitted by contractor & shall be approved before short circuit test. | Detail test procedure shall be submitted by contractor & shall be approved before short circuit test. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 348 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0638 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Testing | Transformer Oil | TESTING | After the Reactor has been under oil without excitation for at least 3 h, the average oil temperature shall be determined and the temperature of the winding shall be deemed to be the same as the average oil temperature. The average oil temperature is taken as the mean of the top and bottom oil temperatures. In measuring the cold resistance for the purpose of temperature-rise determination, special efforts shall be made to determine the average winding temperature accurately. Thus, the difference in temperature between the top and bottom oil shall not exceed 5 K. To obtain this result more rapidly, the oil may be circulated by a pump. 2. Reactance and loss measurement | After the Reactor has been under oil without excitation for at least 3 h, the average oil temperature shall be determined and the temperature of the winding shall be deemed to be the same as the average oil temperature. The average oil temperature is taken as the mean of the top and bottom oil temperatures. In measuring the cold resistance for the purpose of temperature-rise determination, special efforts shall be made to determine the average winding temperature accurately. Thus, the difference in temperature between the top and bottom oil shall not exceed 5 K. To obtain this result more rapidly, the oil may be circulated by a pump. 2. Reactance and loss measurement | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 349 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0639 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | corrected as per factors derived from the type tested unit.  Measurement shall also be carried out during 2-hour excitation test. | corrected as per factors derived from the type tested unit.  Measurement shall also be carried out during 2-hour excitation test. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 349 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0640 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | The following details shall be recorded under the heading of losses on the test certificate: | The following details shall be recorded under the heading of losses on the test certificate: | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 349 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0641 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Maintenance Schedule | Insulation Resistance | SCHEDULE |  Voltage reading  Current reading  CT & PT Ratio  Tan delta  the power reading  total losses measured  Total losses corrected to 75°C winding temperature  the frequency reading  the instrument constants and corrections (if any)  The magnetization curve of the reactor (Type Tested unit) 3. Measurement of insulation resistance & Polarization Index | NOT COVERED | NOT VERIFIED | 75°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 349 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0642 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Insulation Resistance | TESTING | Measurement of D.C. insulation resistance between each winding to earth and between windings shall be carried out at 5000V DC. The polarisation index is a ratio of insulation resistance value at the end of 10 min test to that at the end of 1 min test at a constant voltage. It is recommended that PI value shall be better than 1.3. | Measurement of D.C. insulation resistance between each winding to earth and between windings shall be carried out at 5000V DC. The polarisation index is a ratio of insulation resistance value at the end of 10 min test to that at the end of 1 min test at a constant voltage. It is recommended that PI value shall be better than 1.3. | NOT VERIFIED | 5000V | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 349 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0643 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | Reactor shall be tested in GST mode only between winding to tank for the measurement of capacitance & tan delta of winding to earth by applying 2kV and 10kV. Tan delta of winding shall not exceed 0.5% at ambient temperature. No temperature correction factor shall be applied. 5. Measurement of insulation power factor and capacitance of bushings | Reactor shall be tested in GST mode only between winding to tank for the measurement of capacitance & tan delta of winding to earth by applying 2kV and 10kV. Tan delta of winding shall not exceed 0.5% at ambient temperature. No temperature correction factor shall be applied. 5. Measurement of insulation power factor and capacitance of bushings | NOT VERIFIED | 2kV; 10kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 350 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0644 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Bushing | NOT VERIFIED | Testing | Tan Delta | TESTING | Bushing shall be tested in UST mode by applying 10kV and 2kV. Tan delta of bushing shall not exceed 0.4% at ambient temperature. No temperature correction factor shall be applied. 6. Core assembly dielectric and earthing continuity tests. | Bushing shall be tested in UST mode by applying 10kV and 2kV. Tan delta of bushing shall not exceed 0.4% at ambient temperature. No temperature correction factor shall be applied. 6. Core assembly dielectric and earthing continuity tests. | NOT VERIFIED | 10kV; 2kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 350 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0645 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Insulation Resistance | INSTALLATION | The insulation of the magnetic circuit and between the magnetic circuit and the core clamping structure, including core-bolts, bands and/ or buckles shall withstand the application of a test voltage of either 2 kVac or 3 kV dc for 60 seconds. The insulation of core to tank, core to yoke clamp (frame) and yoke clamp (frame) to tank shall be able to withstand a voltage of 2.5 kV (DC) for 1 minute. Insulation resistance shall be minimum 1 GΩ for all cases mentioned above. The continuity of the single-point earthing shall be verified before despatch. The results of the works tests shall be recorded on the test certificate, and shall include the resistance reading obtained from a measurement made between the core and core clamping structure by means of at least 1.5 kV ac or 2 kV dc. During erection, the contractor shall repeat this measurement at site. The records of these tests shall also be included in the test report. 7. Dielectric Tests | The insulation of the magnetic circuit and between the magnetic circuit and the core clamping structure, including core-bolts, bands and/ or buckles shall withstand the application of a test voltage of either 2 kVac or 3 kV dc for 60 seconds. The insulation of core to tank, core to yoke clamp (frame) and yoke clamp (frame) to tank shall be able to withstand a voltage of 2.5 kV (DC) for 1 minute. Insulation resistance shall be minimum 1 GΩ for all cases mentioned above. The continuity of the single-point earthing shall be verified before despatch. The results of the works tests shall be recorded on the test certificate, and shall include the resistance reading obtained from a measurement made between the core and core clamping structure by means of at least 1.5 kV ac or 2 kV dc. During erection, the contractor shall repeat this measurement at site. The records of these tests shall also be included in the test report. 7. Dielectric Tests | NOT VERIFIED | 3 kV; 2.5 kV; 1 minute; 1.5 kV; 2 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 350 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0646 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | Following Tests (as applicable) shall be performed in the sequence given below as per IEC 60076-3:2013 clause 7.2.3 shall be followed: a) Lightning impulse tests (LIC, LIN) b) Switching impulse (SI) c) Applied voltage test (AV) d) Induced voltage test with partial discharge measurement Testing shall be performed in line with IEC. DGA tests shall be performed before and after Dielectric Tests. | Following Tests (as applicable) shall be performed in the sequence given below as per IEC 60076-3:2013 clause 7.2.3 shall be followed: a) Lightning impulse tests (LIC, LIN) b) Switching impulse (SI) c) Applied voltage test (AV) d) Induced voltage test with partial discharge measurement Testing shall be performed in line with IEC. DGA tests shall be performed before and after Dielectric Tests. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 350 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0647 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Testing | DGA | TESTING |  Each reactor to be excited at 1 p.u. for 2 hours except type tested unit.  Measure reactance, loss and vibration  DGA rate interpretation shall be as per IEC/ CIGRE/ IEEE guidelines  Test shall be performed before partial discharge test 9. Vibration & Stress measurement |  Each reactor to be excited at 1 p.u. for 2 hours except type tested unit.  Measure reactance, loss and vibration  DGA rate interpretation shall be as per IEC/ CIGRE/ IEEE guidelines  Test shall be performed before partial discharge test 9. Vibration & Stress measurement | NOT VERIFIED | 2 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 351 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0648 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, GIS | NOT VERIFIED | Testing | GIS | TESTING | After all dielectric test reactor shall be energised at rated voltage and mark atleast 4 points on each side wall where vibration is more. Stress will be measured on the same points. Similar process shall be followed for 1.05Ur voltage. 10. Temperature rise test (As per IEC-60076) | After all dielectric test reactor shall be energised at rated voltage and mark atleast 4 points on each side wall where vibration is more. Stress will be measured on the same points. Similar process shall be followed for 1.05Ur voltage. 10. Temperature rise test (As per IEC-60076) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 351 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0649 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Testing | DGA | TESTING | Temperature rise shall be guaranteed and tested at rated voltage (1 p.u). The tests shall be done for a minimum of 24 hours with saturated temperature for at least 4 hours. DGA tests shall be performed before and after heat run test and DGA results shall generally conform to IEC61181. During this test the following shall be measured. - Voltage - Current - Reactance and loss - Audible sound - Vibration - Colour photographs of the four sides and top of the reactor together with the corresponding series of thermal images (colour) during starting and end of the test. It is also recommended to take thermal images 4 more times to take care of any unforeseen situation. - Temperature measurement with internal probes during test. The heat run type test results shall serve as a “finger print” for the other units to be routine tested. Specified winding hotspot temperatures shall not be exceeded. | Temperature rise shall be guaranteed and tested at rated voltage (1 p.u). The tests shall be done for a minimum of 24 hours with saturated temperature for at least 4 hours. DGA tests shall be performed before and after heat run test and DGA results shall generally conform to IEC61181. During this test the following shall be measured. - Voltage - Current - Reactance and loss - Audible sound - Vibration - Colour photographs of the four sides and top of the reactor together with the corresponding series of thermal images (colour) during starting and end of the test. It is also recommended to take thermal images 4 more times to take care of any unforeseen situation. - Temperature measurement with internal probes during test. The heat run type test results shall serve as a “finger print” for the other units to be routine tested. Specified winding hotspot temperatures shall not be exceeded. | NOT VERIFIED | 24 hours; 4 hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 351 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0650 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | The temperature rises recorded by infra red shall not be more than 10°C above top oil temperature or 15°C above the local oil temperature. Full details of the test arrangements, procedures and conditions shall be provided with the test certificates and the following shall at least be included. | The temperature rises recorded by infra red shall not be more than 10°C above top oil temperature or 15°C above the local oil temperature. Full details of the test arrangements, procedures and conditions shall be provided with the test certificates and the following shall at least be included. | NOT VERIFIED | 10°C; 15°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 351 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0651 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE |  Employer’s order number and reactor site designation.  Manufacturer’s name and reactor serial number.  Ratings of reactor:  MVA  Voltage:  Frequency  Rated currents:  Class of cooling  Measured load losses at 75° C.  Altitude of test bay. Top oil temperature rise test A log of the following parameters taken at 30 minute intervals: | NOT COVERED | NOT VERIFIED | 30 minute | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 352 |  MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0652 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING |  time  Voltage  Current  Total power  Ambient temperature measured on not less than three thermometers  Top oil temperature: and  Cooler inlet and outlet oil temperatures.  Infra red pictures during the heating up phases Winding temperature rise test |  time  Voltage  Current  Total power  Ambient temperature measured on not less than three thermometers  Top oil temperature: and  Cooler inlet and outlet oil temperatures.  Infra red pictures during the heating up phases Winding temperature rise test | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 352 |  MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0653 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | per kilogram, the ‘cold’ resistance of each winding and the simultaneous top oil and ambient air temperatures, together with the time required for the effect to disappear.  Record the thermal time constant of the winding.  Log the half–hourly readings of the parameters as for the top oil | NOT COVERED | NOT VERIFIED | NOT VERIFIED | per kilogram, the ‘cold’ resistance of each winding and the simultaneous top oil and ambient air temperatures, together with the time required for the effect to disappear.  Record the thermal time constant of the winding.  Log the half–hourly readings of the parameters as for the top oil | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 352 |  MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0654 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | temperature rise test.  Provide a table of readings, after shut-down of power, giving the following | temperature rise test.  Provide a table of readings, after shut-down of power, giving the following | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 352 |  MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0655 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Winding Resistance | TESTING | information;  Time after shut- down:  Time increment:  Winding resistance: Record the resistance values for minimum 20 | information;  Time after shut- down:  Time increment:  Winding resistance: Record the resistance values for minimum 20 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 352 |  MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0656 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | during initiation of the oil circulating pumps. Temperature measurements as per special probes or sensors placed at various locations shall also be recorded. 11. Measurement of harmonic content of current (Measured in Cold state) | during initiation of the oil circulating pumps. Temperature measurements as per special probes or sensors placed at various locations shall also be recorded. 11. Measurement of harmonic content of current (Measured in Cold state) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 353 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0657 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Testing | General | TESTING | Test shall be performed as per clause 7.8.12 of IEC 60076-6 and IEC 60076- 10. The measured value shall not be exceeded the limit as specified at Annexure-A of this specification. 13. Knee point voltage measurement of reactor (Measured in Cold state) | Test shall be performed as per clause 7.8.12 of IEC 60076-6 and IEC 60076- 10. The measured value shall not be exceeded the limit as specified at Annexure-A of this specification. 13. Knee point voltage measurement of reactor (Measured in Cold state) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 353 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0658 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | The test shall be carried out as per IEC 60076-6 clause B.7.1 “DC current charging – discharging method (theory)” or applying AC voltage from 0.7p.u, 0.8p.u, 0.9p.u and so on upto the level as per specification and measure the current at various voltages and calculate the tolerance of reactance as per annexure-A of this specification. 14. Measurement of zero-sequence reactance (Applicable for three phase | The test shall be carried out as per IEC 60076-6 clause B.7.1 “DC current charging – discharging method (theory)” or applying AC voltage from 0.7p.u, 0.8p.u, 0.9p.u and so on upto the level as per specification and measure the current at various voltages and calculate the tolerance of reactance as per annexure-A of this specification. 14. Measurement of zero-sequence reactance (Applicable for three phase | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 353 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0659 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | The test shall be generally performed as per IEC 60076-1. This measurement shall be carried out at a voltage corresponding to a neutral current equal to the rated phase current. | The test shall be generally performed as per IEC 60076-1. This measurement shall be carried out at a voltage corresponding to a neutral current equal to the rated phase current. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 353 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0660 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor | NOT VERIFIED | Testing | Transformer Oil | TESTING | The test shall be performed on each phase of the Reactor by taking open circuit response of complete winding as HV to neutral terminal and vice versa. The response shall be compared with other units of same design for reference. FRA shall also be carried out without oil in main tank for reference purpose. 16. Routine tests on Neutral Grounding Reactor | The test shall be performed on each phase of the Reactor by taking open circuit response of complete winding as HV to neutral terminal and vice versa. The response shall be compared with other units of same design for reference. FRA shall also be carried out without oil in main tank for reference purpose. 16. Routine tests on Neutral Grounding Reactor | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 354 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0661 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Bushing | NOT VERIFIED | Testing | Bushing | TESTING | In addition to the routine tests listed in the IEC-60076 the volt-current characteristics test shall also be carried out on each neutral grounding reactor preferably at least upto short time rated current. Calculated value of hot spot temperature shall be furnished by the Contractor. Further, Lighting impulse voltage withstand test and ohmic value measurement shall be carried out. 17. Routine tests on Bushings: Routine test on bushings shall be done as per | In addition to the routine tests listed in the IEC-60076 the volt-current characteristics test shall also be carried out on each neutral grounding reactor preferably at least upto short time rated current. Calculated value of hot spot temperature shall be furnished by the Contractor. Further, Lighting impulse voltage withstand test and ohmic value measurement shall be carried out. 17. Routine tests on Bushings: Routine test on bushings shall be done as per | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 354 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0662 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | TC --- Test Certificate PD- Perpendicular Direction CD- Cross Direction MD- Machine Direction PICC-Paper Insulated Copper Conductor CTC- Continuously Transposed Conductor | NOT COVERED | NOT VERIFIED | NOT VERIFIED | TC --- Test Certificate PD- Perpendicular Direction CD- Cross Direction MD- Machine Direction PICC-Paper Insulated Copper Conductor CTC- Continuously Transposed Conductor | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 355 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0663 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 1 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 1 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 355 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0664 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 2 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 2 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 356 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0665 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 3 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 3 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 357 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0666 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Average value: 10 Ω cm2 (min.) Individual value: 05 Ω cm2 (min.) (e) Accelerated Aging test (type test) | Average value: 10 Ω cm2 (min.) Individual value: 05 Ω cm2 (min.) (e) Accelerated Aging test (type test) | NOT VERIFIED | 10 Ω; 05 Ω | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 357 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0667 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 4 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 4 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 358 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0668 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | > 1.6-3 mm - 11 kV/mm > 3-3.6 mm - 10 kV / mm > 6-8 mm TK - 9 kV/mm (k) Dielectric Strength in Oil Up to 1.6 - 40 kV/ mm | NOT COVERED | NOT VERIFIED | 1.6-3 mm; 11 kV; 3-3.6 mm; 10 kV; 6-8 mm; 9 kV; 1.6 - 40 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 358 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0669 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 5 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 5 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 359 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0670 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING |  Dried (tested at 23°C)  Dried (tested at 120°C retention)  Oil impregnated (tested at 23°C)  Aged for 1 week at 120°C in oil (tested at 23°C retention) | NOT COVERED | NOT VERIFIED | 23°C; 120°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 359 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0671 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 6 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 6 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 360 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0672 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 7 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 7 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 361 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0673 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | (g) Loss of oil & Surge test GOR - 1: 70 to 130 CC GOR - 2: 75 to 140 CC GOR - 3: 90 to 160 CC | (g) Loss of oil & Surge test GOR - 1: 70 to 130 CC GOR - 2: 75 to 140 CC GOR - 3: 90 to 160 CC | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 361 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0674 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 8 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 8 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 362 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0675 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 9 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 9 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 363 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0676 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | and center level (within tolerance as per specifications) (c) 2kV HV test for 1 min between all terminal | and center level (within tolerance as per specifications) (c) 2kV HV test for 1 min between all terminal | NOT VERIFIED | 2kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 363 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0677 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | (d) Leak test with air for 6 Hours No leakage at 4 kg /cm2 (e) Switch/contact operation test Operate at Min level indication (f) Contact Rating | (d) Leak test with air for 6 Hours No leakage at 4 kg /cm2 (e) Switch/contact operation test Operate at Min level indication (f) Contact Rating | NOT VERIFIED | 6 Hours | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 363 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0678 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 10 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 10 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 364 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0679 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 11 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 11 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 365 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0680 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 12 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 12 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 366 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0681 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | (h) Operational test on Surge relay Satisfactory working of trip & reset (i) Milli volt drop/contact resistance | (h) Operational test on Surge relay Satisfactory working of trip & reset (i) Milli volt drop/contact resistance | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 366 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0682 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING | (k) Measurement of Tan delta To be provided (value to be used for benchmark) as per manufacturer’s standard (l) Helium Test (barrier board leakage | (k) Measurement of Tan delta To be provided (value to be used for benchmark) as per manufacturer’s standard (l) Helium Test (barrier board leakage | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 366 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0683 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | input and output terminal (c) Check communication interface (d) Test for complete function include | input and output terminal (c) Check communication interface (d) Test for complete function include | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 366 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0684 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 13 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 13 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 367 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0685 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Winding Resistance | TESTING | (e) Accuracy Ratio As per IS 16227/ IEC 61869-2 (f) Secondary winding resistance for | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 367 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0686 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 14 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 14 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 368 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0687 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 15 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 15 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 369 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0688 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Inspection | INSPECTION | B. IN-PROCESS INSPECTION I CRGO Lamination for core 1. Visual check, check length & slitting | B. IN-PROCESS INSPECTION I CRGO Lamination for core 1. Visual check, check length & slitting | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 369 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0689 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 16 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 16 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 370 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0690 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 17 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 17 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 371 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0691 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Inspection | Insulation Resistance | INSPECTION | Check of insulation resistance between CC-CL, CC-Yoke Bolt, CL-Yoke Bolt-2kV Megger 9. Visual check for inter-coil insulation -- As per design - P W | Check of insulation resistance between CC-CL, CC-Yoke Bolt, CL-Yoke Bolt-2kV Megger 9. Visual check for inter-coil insulation -- As per design - P W | NOT VERIFIED | 2kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 371 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0692 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Insulation) / Process Termination parameters 7. Check total process time (Hrs.) 8. Check Oil characteristics before impregnation | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 371 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0693 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 18 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 18 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 372 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0694 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 19 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 19 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 373 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0695 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 373 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0696 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 20 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 20 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 374 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0697 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 21 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 21 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 375 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0698 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Maintenance Schedule | General | SCHEDULE | complete cycle before LV test) and other tests such as One complete operating cycle at 85 % of auxiliary supply voltage,one complete operating cycle with Transformer energized at rated voltage and frequency at no load.Ten tap change operation with +/- 2 steps of principal tap with as far as possible the rated current of Transformer with one winding short circuited etc. as per IS 2026 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 375 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0699 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | dielectric liquid from each separate oil compartment except diverter switch compartment. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 375 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0700 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 22. Check of core and frame insulation P W 23. Leak testing with pressure for liquid | 22. Check of core and frame insulation P W 23. Leak testing with pressure for liquid | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 375 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0701 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 22 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 22 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 376 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0702 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 23 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 23 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 377 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0703 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | Um/√3 level Cold and Hot state for the unit on which temperature rise test is performed & in Cold state for all other units. (Measurement shall also be carried out at 1.05Um/√3 level for reference purpose) | Um/√3 level Cold and Hot state for the unit on which temperature rise test is performed & in Cold state for all other units. (Measurement shall also be carried out at 1.05Um/√3 level for reference purpose) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 377 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0704 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 24 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 24 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 378 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0705 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | 5. Lightning impulse test for the neutral terminals (LIN) 6. Switching impulse test for the line | 5. Lightning impulse test for the neutral terminals (LIN) 6. Switching impulse test for the line | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 378 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0706 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 25 of 25 | * Category of Responsibility: P - Actual Test Performance V - Verify and Accept W - Witness Actual testing, verify and accept Annexure-E: Manufacturing Quality Plan Page 25 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 379 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0707 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Inspection | SAFETY | No load loss = Core weight x Watts/kg at 1.7 Tesla x Building Factor x 10-3 kW = 42452.3 x 0.78 x 1.11x 10-3= 36.755 kW (Where the value of building factor taken is 1.11) Guaranteed No Load Loss = 39.0kW Calculated No load loss < (Guaranteed loss figure) Estimation of copper quantity during stage Inspection | NOT COVERED | NOT VERIFIED | NOT VERIFIED | No load loss = Core weight x Watts/kg at 1.7 Tesla x Building Factor x 10-3 kW = 42452.3 x 0.78 x 1.11x 10-3= 36.755 kW (Where the value of building factor taken is 1.11) Guaranteed No Load Loss = 39.0kW Calculated No load loss < (Guaranteed loss figure) Estimation of copper quantity during stage Inspection | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 382 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0708 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | Customer/Purchaser always desires that transformer/reactor manufactured and delivered is of good quality and must perform trouble free service for its “Specified Design Life”. The consistency in quality of material used & manufacturing process are main cause for variation in quality of transformer/reactor. It is also equally very important that transformer/reactor is manufactured in a clean dust free and humidity controlled environment. Any compromise on this aspect will have adverse effect in expected design life of transformer/reactor, however good is the quality of material used. A broad list of facilities the transformer/reactor manufacturers should have are given below: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 386 | BASIC MANUFACTURING FACILITY & MANUFACTURING ENVIRONMENT | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0709 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Installation | General | INSTALLATION | 2. Vapor Phase Drying Oven (adequately sized to accommodate offered transformer and have facility to record temperature, vacuum, moisture etc.) 3. Air Casters for material handling | 2. Vapor Phase Drying Oven (adequately sized to accommodate offered transformer and have facility to record temperature, vacuum, moisture etc.) 3. Air Casters for material handling | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 386 | BASIC MANUFACTURING FACILITY & MANUFACTURING ENVIRONMENT | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0710 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (a) Guaranteed Technical Particulars (GTPs) and other Technical particulars (b) Rating and Diagram Plate giving details of terminal marking and connection diagram (c) General Arrangement (GA) drawing (as built drawing) of transformer/reactor showing Plan, Elevation, End view (left side & right side view looking from HV side) and 3D view identifying various fittings & accessories, dimensions, weight, clearances, quantity of insulating oil, centre of gravity etc. (d) View showing maximum lifting height of core-coil assembly and maximum clearance over tank top required for taking out the bushing. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 389 | LIST OF DRAWINGS/DOCUMENTS TO BE SUBMITTED BY THE | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0711 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Testing | Bushing | TESTING | (e) List of all accessories, description, make, weight and quantity (f) Bill of Materials (BoM) with description, make & quantity (g) Drawing relating to Neutral formation of 1-phase units of three phase bank (h) Drawing relating to Delta formation of 1-phase units of 3- phase bank (i) Foundation Plan (combined foundation drawing for 1-phase transformers/ reactors) showing Rail gauge, fixing details of foundation bolts, clamping arrangement to restrict movement during earthquake & location of jacking pads and loading details (j) Bushing Drawing showing dimensions, electrical & mechanical characteristics, mounting details and test tap details (as applicable) | (e) List of all accessories, description, make, weight and quantity (f) Bill of Materials (BoM) with description, make & quantity (g) Drawing relating to Neutral formation of 1-phase units of three phase bank (h) Drawing relating to Delta formation of 1-phase units of 3- phase bank (i) Foundation Plan (combined foundation drawing for 1-phase transformers/ reactors) showing Rail gauge, fixing details of foundation bolts, clamping arrangement to restrict movement during earthquake & location of jacking pads and loading details (j) Bushing Drawing showing dimensions, electrical & mechanical characteristics, mounting details and test tap details (as applicable) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 389 | LIST OF DRAWINGS/DOCUMENTS TO BE SUBMITTED BY THE | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0712 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | OLTC, Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | ii) IV Bushing iii) LV Bushing iv) Neutral Bushing (k) Transport Dimension Drawing indicating transport weight, transport condition (oil filled/gas filled), lifting bollards, jacking pads, pulling eyes, quantity and location of impact recorder etc. (l) General Arrangement Drawing of Cooler Control Cabinet, Marshalling box (m) GA drawing for bus duct termination (if applicable) indicating position of bus duct mounting flanges (n) General Arrangement Drawing of RTCC panel (if applicable) (o) GA drawing for Junction Box (if applicable) (p) GA drawing for Cable Box (if applicable) (q) Cooler Control Scheme: Schematic wiring diagram of cooling arrangement along with write up on scheme (r) Tap Changer Control Scheme (if applicable): Schematic wiring diagram of OLTC along with write up on scheme (s) Mounting Arrangement and wiring diagram of remote WTI along with write up. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 390 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0713 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Maintenance Schedule | Bushing | SCHEDULE | (t) Alarm/Trip Indication Scheme (u) Valve Schedule Plate drawing showing all valves, air vents, drain plugs etc. with type, size, material and quantity of valves (v) Technical literature of all fittings and accessories (w) Calculation in support of thermal withstand capability of transformer due to short circuit (x) Calculation of hot spot temperature (y) Value of air core reactance with a typical write-up of calculation (z) Magnetisation Characteristics of bushing CTs and neutral CTs (aa) Hysteresis Characteristics of iron core (bb) Over fluxing withstand duration curve (cc) Typical heating and cooling curves (dd) Drawing showing winding arrangement & geometrical sequence w.r.t core with winding ID/OD, height & separation distance between windings etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 390 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0714 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | (ee) Twin bi-directional roller assembly drawing (ff) Oil Flow Diagram (gg) List of spares (hh) Connection diagram of all protective devices to marshalling box showing physical location | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 390 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0715 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | (ii) Insulating oil storage tank drawing (jj) Oil sampling Bottle details (kk) Customer inspection schedule (ll) Test procedure of transformer/reactor (mm) Manufacturer Quality Program (MQP) and Field Quality Plan | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 391 | (FQP) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0716 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing | NOT VERIFIED | Maintenance Schedule | Transformer Oil | SCHEDULE | (FQP) (nn) Field Welding Schedule for field welding activities (if applicable) (oo) Type test reports (pp) O&M manual (hard copy and soft copy) of transformer/reactor inter-alia including instructions for Aircell, Oil filling, Bushing removal and Core Coil Assembly un-tanking etc. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 391 | (FQP) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0717 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 1 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 1 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 394 | CRITERIA FOR SELECTION OF SIMILAR REFERENCE TRANSFORMER | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0718 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | CRITERIA FOR SELECTION OF SIMILAR REFERENCE TRANSFORMER FOR DYNAMIC SHORT CIRCUIT WITHSTAND TEST | CRITERIA FOR SELECTION OF SIMILAR REFERENCE TRANSFORMER FOR DYNAMIC SHORT CIRCUIT WITHSTAND TEST | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 394 | CRITERIA FOR SELECTION OF SIMILAR REFERENCE TRANSFORMER | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0719 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | distribution, interconnection transformer;  Same conceptual design, for example dry type, oil-immersed type, core | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 394 | CRITERIA FOR SELECTION OF SIMILAR REFERENCE TRANSFORMER | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0720 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 2 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 2 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 395 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0721 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 3 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 3 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 396 | -NA- | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0722 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 4 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 4 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 397 | OIL-IMMERSED, CORE TYPE, | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0723 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 5 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 5 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 398 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0724 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 6 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 6 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 399 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0725 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 7 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 7 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 400 | 11 Same clamping and | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0726 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 8 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 8 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 401 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0727 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 9 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 9 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 402 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0728 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 10 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 10 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 403 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0729 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 11 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 11 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 404 | 40 Deg C | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0730 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 12 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 12 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 405 | LV (LI/LIC/AC) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0731 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 13 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 13 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 406 | 10.05 Window Height (top of Bottom yoke | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0732 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 14 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 14 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 407 | LV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0733 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 15 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 15 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 408 | 14.00 No of Turns (Max / Nor / Min) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0734 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 16 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 16 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 409 | HV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0735 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 17 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 17 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 410 | 19.00 Spacers / Circle (Nos. x Width) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0736 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 23.00 Oil Quantity during first filling 100 kL 115 kL 24.00 Tank Thickness 24.01 Side 12 mm 12 mm 24.02 Top 25 mm 25 mm | NOT COVERED | NOT VERIFIED | 12 mm; 25 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 410 | 19.00 Spacers / Circle (Nos. x Width) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0737 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 18 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 18 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 411 | 24.03 Bottom | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0738 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 19 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 19 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 412 | REV: _________________ | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0739 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 20 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 20 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 413 | IV | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0740 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 21 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 21 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 414 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0741 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 22 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 22 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 415 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0742 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 23 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 23 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 416 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0743 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 24 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 24 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 417 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0744 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 25 of 25 | Annexure-J: Criteria for selection of similar reference transformer for dynamic short circuit withstand test Page 25 of 25 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 418 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0745 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | General | SAFETY | *values at the end of oxidation stability test D Health, safety and environment (HSE) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | *values at the end of oxidation stability test D Health, safety and environment (HSE) | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 422 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0746 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | III. Oil used for first filling, testing and impregnation of active parts at manufacturer's works shall meet parameters as mentioned below | III. Oil used for first filling, testing and impregnation of active parts at manufacturer's works shall meet parameters as mentioned below | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 425 | 135 °C(Min.) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0747 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | 1 Break Down voltage (BDV) - 70kV (Min.) 2 Moisture content - 5 ppm (Max.) 3 Tan-delta at 90°C - 0.005 (Max.) 4 Interfacial tension - 0.04 N/m (Min.) IV. Each lot of the oil shall be tested prior to filling in main tank at site for the following: 1 Break Down voltage (BDV) - 70 kV (Min.) 2 Moisture content - 5 ppm (Max.) 3 Tan-delta at 90°C - 0.0025 (Max.) 4 Interfacial tension - 0.04 N/m (Min.) | 1 Break Down voltage (BDV) - 70kV (Min.) 2 Moisture content - 5 ppm (Max.) 3 Tan-delta at 90°C - 0.005 (Max.) 4 Interfacial tension - 0.04 N/m (Min.) IV. Each lot of the oil shall be tested prior to filling in main tank at site for the following: 1 Break Down voltage (BDV) - 70 kV (Min.) 2 Moisture content - 5 ppm (Max.) 3 Tan-delta at 90°C - 0.0025 (Max.) 4 Interfacial tension - 0.04 N/m (Min.) | NOT VERIFIED | 70kV; 5 ppm; 90°C; 70 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 425 | 135 °C(Min.) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0748 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 3 Tan-delta at 90°C - 0.005 (Max.) 4 Interfacial tension - 0.04 N/m (Min.) 5 *Oxidation Stability - a) Acidity 0.3 (mg KOH /g) (Max.)-For Inhibited Oil 1.2 mg KOH/g (Max.)-For Uninhibited Oil b) Sludge - 0.05 % (Max.) - For Inhibited Oil 0.8 % (Max.) - For Uninhibited Oil | NOT COVERED | NOT VERIFIED | 90°C | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 425 | 135 °C(Min.) | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0749 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Tan Delta | TESTING | c) Tan delta at 90 °C - 0.05 (Max.) - For Inhibited Oil 0.5 (Max.) - For Uninhibited Oil 6 Total PCB content* Not detectable (< 2 mg/kg) * Separate oil sample shall be taken and test results shall be submitted | c) Tan delta at 90 °C - 0.05 (Max.) - For Inhibited Oil 0.5 (Max.) - For Uninhibited Oil 6 Total PCB content* Not detectable (< 2 mg/kg) * Separate oil sample shall be taken and test results shall be submitted | NOT VERIFIED | 90 °C; 2 mg/kg | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 426 | 0.05 (Max.) - For Inhibited Oil | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0750 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | L2 Length between bottom seat of flange and bottom of the oil end shield/ stress relieving electrode/ oil end terminal whichever is the longest L6 Length for accommodating Bushing Current Transformer (BCT) D2 Maximum diameter of oil immersed end D3 Outside diameter of fixing flange D4 Pitch Circle Diameter of fixing holes of flange D5 Diameter of fixing hole N Number of fixing holes D6 Maximum diameter of oil end shield/stress relieving electrode D8 Diameter of hole for oil end terminal | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 427 | STANDARD DIMENSIONS FOR LOWER PORTION OF CONDENSER BUSHINGS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0751 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, CT, Bushing | Current Transformer | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Symbol Description L2 Length between bottom seat of flange and bottom of the oil end shield/ stress relieving electrode/ oil end terminal whichever is the longest L6 Length for accommodating Bushing Current Transformer (BCT) D2 Maximum diameter of oil immersed end D3 Outside diameter of fixing flange D4 Pitch Circle Diameter of fixing holes of flange D5 Diameter of fixing hole N Number of fixing holes D6 Maximum diameter of oil end shield/stress relieving electrode L11 Horizontal Distance between holes for bushing bottom connection for 4 hole connection L12 Vertical Distance between holes for bushing bottom connection for 4 hole connection L13 Vertical Distance between holes for bushing bottom connection for 2 hole connection D7 Diameter of hole for bushing bottom connection for 2 hole connection D8 Diameter of hole for bushing bottom connection for 4 hole connection | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 429 | STANDARD DIMENSION FOR LOWER PORTION OF CONDENSER BUSHINGS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0752 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Reactor, Bushing | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | a for 765 kV class shunt reactor Notes: 1. All dimensions are in mm. 2. No positive tolerance where maximum dimension specified and no negative tolerance where minimum dimension is specified. 3. For other details of oil end terminal for 2000 A (145 kV/245 kV) solid stem type bushing, refer Fig 4 of IS 12676. 4. For other details of oil end terminal for 2000 A, 72.5 kV solid stem type bushing, refer Fig 3B of IS 12676. 5. For other details of oil end terminal for 800 A and 1250 A (52kV/72.5 kV/145 kV/245 kV/420 kV) solid stem type bushing, refer Fig 3A of IS 12676. | NOT COVERED | NOT VERIFIED | 765 kV; 2000 A; 145 kV; 245 kV; 72.5 kV; 800 A; 1250 A; 52kV; 420 kV; 3A | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 431 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0753 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | switching arrangement in such a way that spare unit can replace any of the other units, without physical shifting of the spare unit from its location. For this purpose, HV & IV connections (in case of transformer) and Line end connection (in case of reactor) of spare unit shall be extended up to the other unit(s) by forming auxiliary buses using flexible/rigid conductor and isolators of suitable rating (as shown below in the single line diagram). The Tertiary delta formation and connection with neutral bus shall be done by direct connection without the use of any isolator to make the connection simple. The tertiary bus for delta formation (for transformer) and neutral bus (for transformer/reactor) shall be supported on structure with bus post insulators at suitable intervals using flexible/rigid conductor and suitable clamps & connectors. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 432 | CONNECTION ARRANGEMENT FOR BRINGING SPARE UNIT INTO | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0754 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Tertiary bus and connections shall be insulated with heat shrinkable insulating sleeve of adequate thickness suitable for at least 52kV. All associated materials like Bus post insulators, Aluminium tube, conductors, clamps & connectors, insulator strings, hardware, cables, support structures shall be provided for the above- mentioned arrangement. However, the detail configuration and hardware shall be finalised during detailed engineering and shall be subject to purchaser’s approval. (b) The spare unit shall be completely erected, oil filled and | NOT COVERED | NOT VERIFIED | 52kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 432 | CONNECTION ARRANGEMENT FOR BRINGING SPARE UNIT INTO | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0755 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | commissioned similar to the other units and kept on the foundation after completing all necessary activities for long-term storage. The contractor shall carry out all pre-commissioning tests on the spare unit similar to the unit kept in service. Any special maintenance | commissioned similar to the other units and kept on the foundation after completing all necessary activities for long-term storage. The contractor shall carry out all pre-commissioning tests on the spare unit similar to the unit kept in service. Any special maintenance | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 432 | CONNECTION ARRANGEMENT FOR BRINGING SPARE UNIT INTO | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0756 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Bushing, Substation | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | not feasible because of use of high current bus duct on low voltage side or oil to SF6 bushings and for substations where sufficient space is not available for erecting auxiliary buses, neutral bus & isolators, the spare transformer/reactor unit shall be physically shifted to replace faulty unit in case of failure of any of the running units. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | not feasible because of use of high current bus duct on low voltage side or oil to SF6 bushings and for substations where sufficient space is not available for erecting auxiliary buses, neutral bus & isolators, the spare transformer/reactor unit shall be physically shifted to replace faulty unit in case of failure of any of the running units. | Transformers and reactors, 66 kV and above voltage class | PDF p. 433 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0757 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | facilitate quick movement. The spare unit may be required to be stored for long duration. The spare unit shall be completely erected and commissioned similar to the other units. However, erection of separate cooler bank is not envisaged. In case conservator is cooler bank mounted, suitable arrangement for mounting of conservator on tank top cover shall be provided. The contractor shall carry out all pre-commissioning tests on the spare unit similar to the other units kept in service. Any special maintenance procedure required for long term storage shall be clearly brought out in the OEM’s instruction manual. | facilitate quick movement. The spare unit may be required to be stored for long duration. The spare unit shall be completely erected and commissioned similar to the other units. However, erection of separate cooler bank is not envisaged. In case conservator is cooler bank mounted, suitable arrangement for mounting of conservator on tank top cover shall be provided. The contractor shall carry out all pre-commissioning tests on the spare unit similar to the other units kept in service. Any special maintenance procedure required for long term storage shall be clearly brought out in the OEM’s instruction manual. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 433 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0758 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Failure | FAILURE_ANALYSIS | 1.0 One of the objectives of standardization is to achieve physical interchangeability of transformers/reactors of different makes, procured by utility(ies), by standardizing the minimum foundation loading to be considered for civil foundation design of transformers/reactor. In case of failure of any transformer/reactor, outage time to replace a failed unit by a spare unit/new unit of different make would be minimized as it can be accommodated in the same space without/minor modification in existing foundation. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 1.0 One of the objectives of standardization is to achieve physical interchangeability of transformers/reactors of different makes, procured by utility(ies), by standardizing the minimum foundation loading to be considered for civil foundation design of transformers/reactor. In case of failure of any transformer/reactor, outage time to replace a failed unit by a spare unit/new unit of different make would be minimized as it can be accommodated in the same space without/minor modification in existing foundation. | Transformers and reactors, 66 kV and above voltage class | PDF p. 437 | PHYSICAL INTERCHANGEABILITY OF TRANSFORMERS/ REACTORS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0759 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 2.0 In general, the foundation layout & design of transformer depends on weight of the transformer/reactor (with oil and all fittings & accessories), design of soak pit (with or without remote oil collecting pit) with trans rack/grating & gravels and free space to be kept below the transformer/reactor to accommodate oil and water in case of fire. The number of rails, number & location of jacking pads of transformers are also equally important. 3.0 The foundation design should take into account the following points: | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 437 | PHYSICAL INTERCHANGEABILITY OF TRANSFORMERS/ REACTORS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0760 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, OLTC, Bushing, Substation, Switchyard, Fire Protection | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | c) The plinth height of transformer/reactor foundation may be kept from 300 mm to 500 mm above finished ground level of the substation/switchyard depending upon the size of the transformer/reactor. Pulling blocks should be provided for shifting of transformer/reactor for maintenance purposes. d) The pedestal support should be provided for supporting the cooler bank, firefighting system etc. The RCC Rail-cum-road system integrated with the transformer/reactor foundation may be provided to enable installation and the replacement of any failed unit. The transfer track system should be suitable to permit the movement of any failed unit fully assembled (including OLTC, bushings) with oil. | NOT COVERED | NOT VERIFIED | 300 mm; 500 mm | EXPLICIT IN SOURCE | c) The plinth height of transformer/reactor foundation may be kept from 300 mm to 500 mm above finished ground level of the substation/switchyard depending upon the size of the transformer/reactor. Pulling blocks should be provided for shifting of transformer/reactor for maintenance purposes. d) The pedestal support should be provided for supporting the cooler bank, firefighting system etc. The RCC Rail-cum-road system integrated with the transformer/reactor foundation may be provided to enable installation and the replacement of any failed unit. The transfer track system should be suitable to permit the movement of any failed unit fully assembled (including OLTC, bushings) with oil. | Transformers and reactors, 66 kV and above voltage class | PDF p. 437 | PHYSICAL INTERCHANGEABILITY OF TRANSFORMERS/ REACTORS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0761 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | This system should enable the removal of any failed unit from its foundation to the nearest road. If trench/drain crossings are required, then suitable R.C.C. culverts should be provided in accordance with I.R.C. standard/relevant IS. e) Foundation of each transformer/reactor including oil conservator tank and cooler banks etc. should be placed in a self-sufficient pit surrounded by RCC retaining walls (Pit walls). The retaining wall of the pit from the transformer/reactor should be such that no part of transformer/reactor is outside the periphery of retaining wall. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | This system should enable the removal of any failed unit from its foundation to the nearest road. If trench/drain crossings are required, then suitable R.C.C. culverts should be provided in accordance with I.R.C. standard/relevant IS. e) Foundation of each transformer/reactor including oil conservator tank and cooler banks etc. should be placed in a self-sufficient pit surrounded by RCC retaining walls (Pit walls). The retaining wall of the pit from the transformer/reactor should be such that no part of transformer/reactor is outside the periphery of retaining wall. | Transformers and reactors, 66 kV and above voltage class | PDF p. 438 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0762 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | f) An oil soak pit of adequate capacity should be provided below each oil filled transformer/reactor to accommodate at least 150% of full quantity of oil contained in the transformer/reactor and minimum 300 mm thick layer of gravels/pebbles of approximately 40 mm size (spread over a steel iron grating/trans rack) providing free space below the grating. Alternatively, an oil soak pit should be provided below each transformer/reactor to accommodate 1/3rd of total quantity of oil contained in the transformer/reactor and minimum 300 mm thick layer of gravels/pebbles of approximately 40 mm size (spread over a steel iron grating/trans rack) providing free space below the grating provided a common remote oil collecting pit of capacity at least equal to oil quantity in the largest size transformer/reactor is provided for a group of transformers/reactors. | NOT COVERED | NOT VERIFIED | 300 mm; 40 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 438 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0763 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Bottom of the soak pit below the transformer/reactor should be connected to the common oil collecting pit with drain pipe (two or more Hume/concrete pipes) of minimum 150 mm diameter with a slope not less than 1/96 for fast draining of oil and water through gravity from soak pit to the burnt oil collecting pit, which is generally located away from transformers/reactors. g) Every soak pit below a transformer/reactor should be suitably designed to contain oil dropping from any part of the transformer/reactor. h) The common remote oil collecting pit and soak pit (when remote oil collecting pit is not provided) should be provided with suitable automatic pumping facility, to always keep the pit empty and available for an emergency. i) The disposal of transformer oil should be carried out in an environmental friendly manner. | NOT COVERED | NOT VERIFIED | 150 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 438 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0764 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | General | DESIGN_REFERENCE | j) The minimum height of the retaining walls of pit should be 150 mm to 200 mm above the finished ground level to avoid outside water pouring inside the pit. The bottom of the pit is generally made of PCC | NOT COVERED | NOT VERIFIED | 150 mm; 200 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 438 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0765 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | M15 grade and should have a uniform slope towards the sump pit. While designing the oil collection pit, the movement of the transformer/reactor must be taken into account. k) The grating shall be made of MS flat of size 30 mm x 5 mm at spacing of 30 mm and MS bar of 6 mm dia at spacing of 150 mm at right angle to each other. Maximum length & width of grating should be 2000 mm & 500 mm respectively. The gratings, supported on ISMB 150 mm, should be placed at the formation level and will be covered with 300 mm thick layer of stone aggregate having size 40 mm (approximate). All steel work used for grating and supports should be painted with epoxy based zinc phosphate primer (two packs) confirming to IS: 13238-1991, thereafter with two or more coat of bituminous paint of approved quality should be applied. | NOT COVERED | NOT VERIFIED | 30 mm; 5 mm; 6 mm; 150 mm; 2000 mm; 500 mm; 300 mm; 40 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 439 | 300 mm thick layer of stone aggregate having size 40 mm | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0766 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Fire Protection | NOT VERIFIED | Corrective Action | Fire Protection | CORRECTIVE_ACTION | l) In case of transformers with separately mounted cooler / radiator bank, the position of the cooler / radiator bank has been recommended on the left side of the transformer when viewing from HV side. However, transformer shall be designed in such a way that cooler / radiator bank can be positioned on either side of the main tank. Similarly the conservator shall be on the left side of the tank while viewing from HV side. m) The separation wall(s) or fire barrier wall(s) of four hours fire | NOT COVERED | NOT VERIFIED | NOT VERIFIED | EXPLICIT IN SOURCE | l) In case of transformers with separately mounted cooler / radiator bank, the position of the cooler / radiator bank has been recommended on the left side of the transformer when viewing from HV side. However, transformer shall be designed in such a way that cooler / radiator bank can be positioned on either side of the main tank. Similarly the conservator shall be on the left side of the tank while viewing from HV side. m) The separation wall(s) or fire barrier wall(s) of four hours fire | Transformers and reactors, 66 kV and above voltage class | PDF p. 439 | 300 mm thick layer of stone aggregate having size 40 mm | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0767 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor, Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | withstand rating shall be provided between the transformers and/or reactors or between the transformer(s)/reactor(s) & the adjacent wall of a building if wall of the building do not have the capability to withstand fire for a duration of four (4) hours as per Central Electricity Authority (Measures relating to Safety and Electric Supply) Regulations. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | withstand rating shall be provided between the transformers and/or reactors or between the transformer(s)/reactor(s) & the adjacent wall of a building if wall of the building do not have the capability to withstand fire for a duration of four (4) hours as per Central Electricity Authority (Measures relating to Safety and Electric Supply) Regulations. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 439 | 300 mm thick layer of stone aggregate having size 40 mm | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0768 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | n) Other requirement related to civil construction of foundation may be specified by the utility in line with relevant BIS standards and best practices. 4.0 It is a fact that maximum weight of transformer (with oil and all fittings & accessories) and outline dimension do not vary much from manufacturer to manufacturer for same rating. Hence a common foundation layout plan with soak pit (with oil and all fittings & accessories) with loading details would facilitate the interchangeability of transformers/reactors of different make of similar/same ratings. The utilities shall strive to standardize the foundation plan for different rating of transformers/reactors so that transformers/reactors of different makes could be accommodated in the same space with minor modification/without any modification in the | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 439 | 300 mm thick layer of stone aggregate having size 40 mm | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0769 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | Annexure-Q: Standard GA drawings and limits of supply between suppliers of transformer and dry-type cable/GIS termination for hydro plants Page 1 of 5 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 443 | STANDARD GA DRAWINGS AND LIMITS OF SUPPLY BETWEEN SUPPLIERS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0770 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | STANDARD GA DRAWINGS AND LIMITS OF SUPPLY BETWEEN SUPPLIERS OF TRANSFORMER AND DRY-TYPE CABLE/GIS TERMINATION FOR HYDRO PLANTS | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 443 | STANDARD GA DRAWINGS AND LIMITS OF SUPPLY BETWEEN SUPPLIERS | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0771 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | Annexure-Q: Standard GA drawings and limits of supply between suppliers of transformer and dry-type cable/GIS termination for hydro plants Page 2 of 5 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 444 | 100 MVA | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0772 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | Annexure-Q: Standard GA drawings and limits of supply between suppliers of transformer and dry-type cable/GIS termination for hydro plants Page 3 of 5 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 445 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0773 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Earthing | DESIGN_REFERENCE | cable termination Conductor current terminal with removable link 1 X Connection interface including fixing elements 2 X Connection interface 3 X Shielding electrode* 4 X Socket 5 X Cable connection box 6 X Bolts, washers, nuts 7 X Clamping flange# 8 X Intermediate gasket# 9 X O-ring seal 10 X Cable gland 11 X Insulating liquid 12 X Earthing terminal 13 X *divided or removable because of mounting #If needed | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 445 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0774 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | Annexure-Q: Standard GA drawings and limits of supply between suppliers of transformer and dry-type cable/GIS termination for hydro plants Page 4 of 5 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 446 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0775 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, GIS | NOT VERIFIED | Design / Technical Reference | GIS | DESIGN_REFERENCE | Annexure-Q: Standard GA drawings and limits of supply between suppliers of transformer and dry-type cable/GIS termination for hydro plants Page 5 of 5 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 447 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0776 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Bushing | NOT VERIFIED | Design / Technical Reference | Bushing | DESIGN_REFERENCE | Screw, washer, nuts 7 X Seal 8 X Bushing 9 X Transformer tank 10 X Screw, washer and nuts 11 X | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 447 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0777 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Safety | Fire Protection | SAFETY | 1.1 Separate cables shall be used for AC & DC. 1.2 Separate cables shall be used for DC1 & DC2. 1.3 At least one (1) core shall be kept as spare in each copper control cable of 4C, 5C or 7C size whereas minimum no. of spare cores shall be two (2) for control cables of 10 core or higher size. 1.4 The Aluminium/Copper conductors used for manufacturing the cables shall be true circular in shape before stranding; shall be of good quality, free from defects and shall conform to IS 8130. 1.5 The fillers and inner sheath shall be of non-hygroscopic, fire retardant material, shall be softer than insulation and outer sheath shall be suitable for the operating temperature of the cable. 1.6 Progressive sequential marking of the length of cable in metres at every one metre shall be provided on the outer sheath of all cables. | NOT COVERED | NOT VERIFIED | 4C; 5C; 7C | 1.1 Separate cables shall be used for AC & DC. 1.2 Separate cables shall be used for DC1 & DC2. 1.3 At least one (1) core shall be kept as spare in each copper control cable of 4C, 5C or 7C size whereas minimum no. of spare cores shall be two (2) for control cables of 10 core or higher size. 1.4 The Aluminium/Copper conductors used for manufacturing the cables shall be true circular in shape before stranding; shall be of good quality, free from defects and shall conform to IS 8130. 1.5 The fillers and inner sheath shall be of non-hygroscopic, fire retardant material, shall be softer than insulation and outer sheath shall be suitable for the operating temperature of the cable. 1.6 Progressive sequential marking of the length of cable in metres at every one metre shall be provided on the outer sheath of all cables. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 448 | 1100 V GRADE POWER & CONTROL CABLES | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0778 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Fire Protection | NOT VERIFIED | Testing | Fire Protection | TESTING | 1.7 Strip wire armouring method (a) mentioned in Table 5, Page-6 of IS: 1554 (Part 1) – 1988 shall not be accepted for any of the cables. For control cables only round wire armouring shall be used. 1.8 The cables shall have outer sheath of a material with an oxygen index of not less than 29 and a temperature index of not less than 250°C. 1.9 All the cables shall conform to fire resistance test as per IS: 1554 (Part - I). 1.10 The normal current rating of all PVC insulated cables shall be as per IS: 3961. 1.11 Repaired cables shall not be accepted. 1.12 Allowable tolerance on the overall diameter of the cables shall be ± 2 mm. 1.13 PVC Power Cables 1.13.1 The PVC insulated 1100V grade power cables shall be of Fire Retardant | 1.7 Strip wire armouring method (a) mentioned in Table 5, Page-6 of IS: 1554 (Part 1) – 1988 shall not be accepted for any of the cables. For control cables only round wire armouring shall be used. 1.8 The cables shall have outer sheath of a material with an oxygen index of not less than 29 and a temperature index of not less than 250°C. 1.9 All the cables shall conform to fire resistance test as per IS: 1554 (Part - I). 1.10 The normal current rating of all PVC insulated cables shall be as per IS: 3961. 1.11 Repaired cables shall not be accepted. 1.12 Allowable tolerance on the overall diameter of the cables shall be ± 2 mm. 1.13 PVC Power Cables 1.13.1 The PVC insulated 1100V grade power cables shall be of Fire Retardant | NOT VERIFIED | 250°C; 2 mm; 1100V | EXPLICIT IN SOURCE | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 448 | 1100 V GRADE POWER & CONTROL CABLES | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0779 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 1. Oil storage tank shall be of adequate capacity as specified by the utility along with complete accessories. The oil storage tank shall be designed and fabricated as per relevant Indian Standards e.g. IS: 803 or other internationally acceptable standards. Transformer oil storage tanks shall be towable on pneumatic tyres and rested on manual screw jacks of adequate quantity & size. The tank shall be cylindrical in shape and mounted horizontally and made of mild steel plate of adequate thickness. Diameter of the tank shall be 2.0 meter approximately. The tank shall be designed for storage of oil at a temperature of 100C. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 450 | SPECFICATION FOR OIL STORAGE TANK | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0780 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 3. The tank shall have adequate number of jacking pad so that it can be kept on jack while completely filled with oil. The tank shall be provided with suitable saddles so that tank can be rested on ground after removing the pneumatic tyres. 4. The tank shall also be fitted with manhole, outside & inside access ladder, silica gel breather assembly, inlet & outlet valve, oil sampling valve with suitable adopter, oil drainage valve, air vent etc. Pulling hook on both ends of the tank shall be provided so that the tank can be pulled from either end while completely filled with oil. The engine capacity in horse power to pull one tank completely fitted with oil shall be indicated. 5. Oil level indicator shall be provided with calibration in terms of litre so that at any time operator can have an idea of oil in the tank. 6. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 450 | SPECFICATION FOR OIL STORAGE TANK | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0781 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | Solenoid valve (Electro-mechanically operated) with Centrifugal pump shall be provided at bottom inlet so that pump shall be utilised both ways during oil fill up and draining. Suitable arrangement shall also be provided to prevent overflow and drain from the tank. 7. The following accessories shall also form part of supply along with each Oil storage tank. | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 450 | SPECFICATION FOR OIL STORAGE TANK | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0782 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (a) Four numbers of 50 NB rubber hoses suitable for Transformer oil application up to temperature of 100C, full vacuum and pressure up to 2.5 Kg/cm2 with couplers and unions each not less than 10 metre long shall be provided. | (a) Four numbers of 50 NB rubber hoses suitable for Transformer oil application up to temperature of 100C, full vacuum and pressure up to 2.5 Kg/cm2 with couplers and unions each not less than 10 metre long shall be provided. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 450 | SPECFICATION FOR OIL STORAGE TANK | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0783 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (b) Two numbers of 100 NB rubber hose suitable for full vacuum without collapsing & kinking vacuum hoses with couplers & unions, each not less than 10 metre long, shall also be provided. (c) One number of digital vacuum gauge with sensor capable of reading up to 0.001 torr, operating on 240V 50Hz AC supply shall be supplied. Couplers and unions for sensor should block oil flow in the sensor. Sensor shall be provided with at-least 8 meter cable so as to suitably place the Vacuum gauge at ground level. (d) The painting of oil storage tank and its control panel shall be as per Annexure-K. (e) The tank shall contain a self-mounted centrifugal oil pump with inlet and outlet valves, with couplers -suitable for flexible rubber hoses and necessary switchgear for its control. There shall be no rigid connection to the pump. The pump shall be electric motor driven, and shall have a discharge of not less than 6.0 kl/hr. with a discharge head of 8.0m. The pump motor and the control cabinet shall be enclosed in a cubicle with IP-55 enclosure. | (b) Two numbers of 100 NB rubber hose suitable for full vacuum without collapsing & kinking vacuum hoses with couplers & unions, each not less than 10 metre long, shall also be provided. (c) One number of digital vacuum gauge with sensor capable of reading up to 0.001 torr, operating on 240V 50Hz AC supply shall be supplied. Couplers and unions for sensor should block oil flow in the sensor. Sensor shall be provided with at-least 8 meter cable so as to suitably place the Vacuum gauge at ground level. (d) The painting of oil storage tank and its control panel shall be as per Annexure-K. (e) The tank shall contain a self-mounted centrifugal oil pump with inlet and outlet valves, with couplers -suitable for flexible rubber hoses and necessary switchgear for its control. There shall be no rigid connection to the pump. The pump shall be electric motor driven, and shall have a discharge of not less than 6.0 kl/hr. with a discharge head of 8.0m. The pump motor and the control cabinet shall be enclosed in a cubicle with IP-55 enclosure. | NOT VERIFIED | 240V; 50Hz | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 451 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0784 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Failure / Failure Analysis | Transformer Oil | FAILURE_ANALYSIS | Measurement of Electrical Breakdown Strength of Transformer oil as per relevant standards. 2. The test results should have repeatability, consistency in | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Measurement of Electrical Breakdown Strength of Transformer oil as per relevant standards. 2. The test results should have repeatability, consistency in | Transformers and reactors, 66 kV and above voltage class | PDF p. 452 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0785 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | laboratory condition. Test Output 0-100 kV (Rate of rise: 0.5 to 5kV/Sec) Accuracy ± 1 kV Resolution 0.1 kV Switch off Time ≤ 1ms Display/Control LCD/Keypads Printer In-built/External | laboratory condition. Test Output 0-100 kV (Rate of rise: 0.5 to 5kV/Sec) Accuracy ± 1 kV Resolution 0.1 kV Switch off Time ≤ 1ms Display/Control LCD/Keypads Printer In-built/External | NOT VERIFIED | 0-100 kV; 5kV; 1 kV; 0.1 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 452 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0786 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | DGA | TESTING | instrument and it shall be of latest configuration with licensed preloaded Operating System and software for interpreting DGA results accordance with IEEE C57.104 and IEC 60599. Laptop carrying case shall also be provided. | instrument and it shall be of latest configuration with licensed preloaded Operating System and software for interpreting DGA results accordance with IEEE C57.104 and IEC 60599. Laptop carrying case shall also be provided. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 454 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0787 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | Transformer Oil | TESTING | supplier shall demonstrate repeatability of test results and the results are within the specified accuracy. Purchaser will provide only the insulating oil/ GAS-IN-OIL standard for testing. | supplier shall demonstrate repeatability of test results and the results are within the specified accuracy. Purchaser will provide only the insulating oil/ GAS-IN-OIL standard for testing. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 454 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0788 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | Warranty The entire test set up shall be covered on warranty for a period of 5 year from the last date of complete commissioning and taking over the test set up. If the kit is to be shifted to supplier’s works for repairs during warranty period, supplier will have to bear the cost of spares, software, transportation etc. of the kit. | Warranty The entire test set up shall be covered on warranty for a period of 5 year from the last date of complete commissioning and taking over the test set up. If the kit is to be shifted to supplier’s works for repairs during warranty period, supplier will have to bear the cost of spares, software, transportation etc. of the kit. | NOT VERIFIED | 5 year | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 455 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0789 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Installation | Transformer Oil | INSTALLATION | (CARTRIDGE TYPE) (For 400 kV & above transformer/reactor) In addition to provision of air cell in conservators for sealing of the oil system against the atmosphere, each transformer/reactor of 400 kV and above voltage class shall be provided with an on line insulating oil drying system of adequate rating with proven field performance. This system shall be separately ground mounted and shall be housed in metallic (stainless steel) enclosure. The bidder shall submit the mounting arrangement. This on line insulating oil drying system shall be: | (CARTRIDGE TYPE) (For 400 kV & above transformer/reactor) In addition to provision of air cell in conservators for sealing of the oil system against the atmosphere, each transformer/reactor of 400 kV and above voltage class shall be provided with an on line insulating oil drying system of adequate rating with proven field performance. This system shall be separately ground mounted and shall be housed in metallic (stainless steel) enclosure. The bidder shall submit the mounting arrangement. This on line insulating oil drying system shall be: | NOT VERIFIED | 400 kV | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 456 | SPECIFICATION FOR ON-LINE INSULATING OIL DRYING SYSTEM | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0790 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 1. Designed for very slow removal of moisture that may enter the oil system or generated during cellulose decomposition. Oil flow to the equipment shall be controlled through pump of suitable capacity (at least 5 litres/minute). | NOT COVERED | NOT VERIFIED | 5 litres | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 456 | SPECIFICATION FOR ON-LINE INSULATING OIL DRYING SYSTEM | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0791 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Safety | Transformer Oil | SAFETY | 2. The equipment shall display the moisture content in oil (PPM) of the inlet and outlet oil from the drying system. 3. In case, drying system is transported without oil, the same shall be suitable for withstanding vacuum to ensure that no air/ contamination is trapped during commissioning. 4. In case, drying system is transported with oil, the oil shall conform to the specification for unused oil. Before installation at site, oil sample shall be tested to avoid contamination of main tank oil. 5. Minimum capacity of moisture extraction shall be 10 Litres before replacement of cartridge. Calculation to prove the adequacy of sizing of the on line insulating oil-drying system along with make and model shall be submitted for approval of purchaser during detail engineering. 6. | NOT COVERED | NOT VERIFIED | 10 Litres | 2. The equipment shall display the moisture content in oil (PPM) of the inlet and outlet oil from the drying system. 3. In case, drying system is transported without oil, the same shall be suitable for withstanding vacuum to ensure that no air/ contamination is trapped during commissioning. 4. In case, drying system is transported with oil, the oil shall conform to the specification for unused oil. Before installation at site, oil sample shall be tested to avoid contamination of main tank oil. 5. Minimum capacity of moisture extraction shall be 10 Litres before replacement of cartridge. Calculation to prove the adequacy of sizing of the on line insulating oil-drying system along with make and model shall be submitted for approval of purchaser during detail engineering. 6. | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 456 | SPECIFICATION FOR ON-LINE INSULATING OIL DRYING SYSTEM | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0792 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Substation | NOT VERIFIED | Commissioning | Commissioning | COMMISSIONING | The installation and commissioning at site shall be done under the supervision of OEM representative or OEM certified representative. 7. The equipment shall be capable of transferring data to substation automation system confirming to IEC 61850 through FO port. Necessary interface arrangement shall be provided by the contractor for integration with the automation system. 8. The equipment shall be supplied with Operation Manual (2 set for every unit), Software (if any), and CD/DVD giving operation procedures of Maintenance Manual & Trouble shooting instructions. | The installation and commissioning at site shall be done under the supervision of OEM representative or OEM certified representative. 7. The equipment shall be capable of transferring data to substation automation system confirming to IEC 61850 through FO port. Necessary interface arrangement shall be provided by the contractor for integration with the automation system. 8. The equipment shall be supplied with Operation Manual (2 set for every unit), Software (if any), and CD/DVD giving operation procedures of Maintenance Manual & Trouble shooting instructions. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 456 | SPECIFICATION FOR ON-LINE INSULATING OIL DRYING SYSTEM | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0793 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer, Reactor | NOT VERIFIED | Testing | DGA | TESTING | 1. Oil sampling bottles shall be supplied as specified by the utility and shall be suitable for collecting oil samples from transformers and shunt reactors, for Dissolved Gas Analysis (DGA). Bottles shall be robust enough, so that no damage occurs during frequent transportation of samples from site to laboratory. | 1. Oil sampling bottles shall be supplied as specified by the utility and shall be suitable for collecting oil samples from transformers and shunt reactors, for Dissolved Gas Analysis (DGA). Bottles shall be robust enough, so that no damage occurs during frequent transportation of samples from site to laboratory. | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 457 | SPECFICATION FOR OIL SAMPLING BOTTLES | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0794 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | 2. Oil sampling bottles shall be made of stainless steel having a capacity of one litre. Oil Sampling bottles shall be capable of being sealed gas-tight and shall be fitted with cocks on both ends. 3. The design of bottle & seal shall be such that loss of hydrogen shall not exceed 5% per week. 4. An impermeable oil-proof, transparent plastic or rubber tube of about 5 mm diameter, and of sufficient length shall also be provided with each bottle along with suitable connectors to fit the tube on to the oil sampling valve of the equipment and the oil collecting bottles respectively. | NOT COVERED | NOT VERIFIED | 5 mm | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 457 | SPECFICATION FOR OIL SAMPLING BOTTLES | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0795 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Design / Technical Reference | Transformer Oil | DESIGN_REFERENCE | SPECFICATION FOR OIL SYRINGE 1. If specified by the utility, the glass syringe of capacity 50 ml (approx.) and three way stop cock valve shall be supplied. The syringe shall be made from Heat resistant borosilicate Glass, shall have metal luer lock tip and shall comply with BS EN ISO 595-2 and ISO 80369-7. The material and construction should be resistant to breakage from shock and sudden temperature changes, reinforced at luer lock tip Centre and barrel base. 2. The cylinder-plunger fitting shall be leak proof and shall meet the requirement of IEC-60567. Plunger shall be grounded and fitted to barrel for smooth movement with no back flow. Barrel rim should be flat on both sides to prevent rolling and should be wide enough for convenient finger tip grip. The syringe shall be custom fit and uniquely numbered for matching. The syringe shall be clearly marked with graduations of 2.0 ml and 10.0 ml and shall be permanently fused for life time legibility. | NOT COVERED | NOT VERIFIED | 50 ml; 2.0 ml; 10.0 ml | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 457 | SPECFICATION FOR OIL SAMPLING BOTTLES | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0796 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Maintenance | Transformer Oil | MAINTENANCE | IEC 60296-2020 - Fluids for electrotechnical applications – Mineral insulating oils for electrical equipment IEC 60422: 2013 - Mineral insulating oils in electrical equipment - Supervision and maintenance guidance IS 6792: 2017 | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 459 | IS 3024: 2015 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0797 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Testing | General | TESTING | ANSI-C57.12.80 - General requirements for Distribution, Power and Regulating Transformers ANSI-C57.12.90 - Test Code for Distribution, Power and Regulation Transformers NEMA-TR-1 | ANSI-C57.12.80 - General requirements for Distribution, Power and Regulating Transformers ANSI-C57.12.90 - Test Code for Distribution, Power and Regulation Transformers NEMA-TR-1 | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 460 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0798 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Testing | General | TESTING | - High Voltage Test Techniques - Measurement of Partial Discharges by Electromagnetic and Acoustic Methods | - High Voltage Test Techniques - Measurement of Partial Discharges by Electromagnetic and Acoustic Methods | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 460 | NOT VERIFIED | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0799 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | NOT VERIFIED | NOT VERIFIED | Installation | General | INSTALLATION | - Ready Mixed Paint, Air Drying, Red Oxide - Zinc Chrome, Priming - Specification | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 462 | IS 12444: 1988 | Extracted from source page; verify surrounding context if using as a final answer.
D08-C0800 | D08 | Transformer_Manual__Amendment_01.pdf | Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV & Above Voltage Class) | Central Electricity Authority / Ministry of Power | HIGH | Transformer | NOT VERIFIED | Safety | Installation | SAFETY | CIGRE TB 436 Experiences in service with new insulating liquids Central Electricity Authority (Measures Relating to Safety and Electric Supply) Regulations Central Electricity Authority (Technical Standard for Construction of Electrical Plants and Electric Lines) Regulations Central Electricity Authority (Installation and Operation of Meters) Regulations CBIP Manual on Transformers (Publication No. 317) ISO 9001: Quality System – Model for Quality Assurance in Design/Development. ISO-14001 (Environmental Management System) OHSAS 18001 (Occupational Health and Safety Management System) | NOT COVERED | NOT VERIFIED | NOT VERIFIED | CIGRE TB 436 Experiences in service with new insulating liquids Central Electricity Authority (Measures Relating to Safety and Electric Supply) Regulations Central Electricity Authority (Technical Standard for Construction of Electrical Plants and Electric Lines) Regulations Central Electricity Authority (Installation and Operation of Meters) Regulations CBIP Manual on Transformers (Publication No. 317) ISO 9001: Quality System – Model for Quality Assurance in Design/Development. ISO-14001 (Environmental Management System) OHSAS 18001 (Occupational Health and Safety Management System) | NOT COVERED | Transformers and reactors, 66 kV and above voltage class | PDF p. 464 | CIGRE TB 436 | Extracted from source page; verify surrounding context if using as a final answer.
D09-C0001 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | General/Distribution System | NOT VERIFIED | Maintenance Practices | Overview of maintenance types | GENERAL_GUIDANCE | Distribution utilities follow three maintenance practices: Preventive Maintenance, Predictive Maintenance, and Reactive/Break-down Maintenance. Reactive maintenance is unplanned and carried out after failure; Preventive and Predictive maintenance are planned, proactive activities. | NOT COVERED | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 33/11kV distribution substations | PDF p. 6 | 1.2 Maintenance Practices | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 2). [PAGE CORRECTED: internal doc-label page(s) '2' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0002 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | General/Distribution System | NOT VERIFIED | Preventive Maintenance | Definition and common practices | PROCEDURE | Preventive (scheduled) maintenance is carried out at regular intervals based on Time Directed conditions (number of operations/operating hours/seasonal changes) or Operating/Useful-life based conditions (when equipment condition reaches a limit). Common preventive practices include regular equipment inspection, cleaning and lubrication, testing (insulation, electrical connections), replacement of worn-out components, tree trimming/vegetation management, and equipment upgrades. | YES | Regular/scheduled | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Transformers, circuit breakers, general substation equipment | PDF p. 7-9 | 1.3 Preventive Maintenance | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 3-5). [PAGE CORRECTED: internal doc-label page(s) '3-5' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0003 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | General/Distribution System | NOT VERIFIED | Predictive Maintenance | Condition monitoring approach | PROCEDURE | Predictive maintenance schedules equipment maintenance based on condition-monitoring data collected periodically via sensors that track parameters such as temperature and oil level in transformers and overloading of lines/transformers. Techniques include thermo-vision cameras and partial-discharge detectors for hotspot/PD detection, periodic transformer oil testing, and drone-mounted thermal scanning for overhead line inspection. | YES | As deemed necessary based on condition data | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Transformers, overhead lines | PDF p. 9-10 | 1.4 Predictive Maintenance/Condition Monitoring | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 5-6). [PAGE CORRECTED: internal doc-label page(s) '5-6' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0004 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | General/Distribution System | NOT VERIFIED | Critical vs Non-Critical Equipment | Equipment criticality classification | VERIFIED_FACT | Critical equipment includes Power Transformer and substation major equipment (switchgears & protection system), 33kV/11kV/LT lines & cables, Distribution Transformers, and HT switchgears/RMUs/LT circuit breakers. Non-critical equipment includes service lines, meters, and distribution boxes that can be replaced immediately from store. | NOT COVERED | NOT COVERED | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 33/11kV distribution substations | PDF p. 11 | 1.6 Process of Adopting Various Maintenance Practices | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 7). [PAGE CORRECTED: internal doc-label page(s) '7' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0005 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Transformer | Distribution Transformer | Trippings/Interruptions - Faults | Fault causes and remedial actions | TROUBLESHOOTING | Distribution transformer trippings/interruptions can be caused by defective bushing (HV/LV) and oil leakage, poor breather/conservator condition, high unbalancing current, continuous overloading, frequent LT cable faults, improper HT/LT protection, hot spot development, poor/defective earthing, bird/animal electrocution, poor maintenance, high-rating fuse use, or moisture ingress into the cable chamber. | NOT COVERED | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Remedial actions include tightening/insulating HT-LT connections, proactive thermo-scanning, checking/tightening earth values during planned shutdown, proactive patrolling and sealed drain valves, segregating multiple LT feeders, top-fencing in animal-prone substations, DT overhaul/replacement, sealing chambers against moisture, reconditioning silica gel, checking oil level, and periodic insulation resistance measurement and oil tests (BDV, moisture content, acidity, IFT, colour, resistivity). | Distribution Transformers | PDF p. 13 | 1.7 Fault/Point of Concern Table - DT Trippings | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 9). [PAGE CORRECTED: internal doc-label page(s) '9' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0006 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Circuit Breaker | 11kV Outgoing Breaker | Breaker Tripping - Faults | Fault causes and remedial actions | TROUBLESHOOTING | 11kV outgoing breaker tripping is typically caused by overloading or phase/earth faults. | NOT COVERED | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Remedial actions: check relay tripping parameters for analysis, perform line inspection before re-charging, and check gas pressure in case of a gas (SF6) breaker. | 11kV outgoing feeders | PDF p. 15 | 1.7 Fault/Point of Concern Table - 11kV Breaker Tripping | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 11). [PAGE CORRECTED: internal doc-label page(s) '11' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0007 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Power Transformer | NOT VERIFIED | Operating Conditions | Recommended operating limits | VERIFIED_FACT | Recommended operating conditions for power transformers: operating temperature should preferably be less than 70°C (via Oil Temperature Indicator/OTI); the transformer should generally not be operated at more than 2/3 of its maximum MVA capacity; long-duration overloading should be avoided; heavy overloading is mitigated via an Over Load Trimming Scheme (OLTS) to remove non-critical loads. | NOT COVERED | NOT COVERED | 70°C max preferred operating temperature (OTI); loading not more than 2/3 of maximum MVA capacity | NOT VERIFIED | NOT COVERED | Power transformers (33/11kV substation) | PDF p. 18-19 | 2.2.1 Major Operating Conditions for Power Transformers | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 14-15). [PAGE CORRECTED: internal doc-label page(s) '14-15' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0008 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Power Transformer | NOT VERIFIED | Best O&M Practices | General supervision checklist | PROCEDURE | Best-practice general supervision of power transformers includes: inspecting external surfaces for dirt/dust and cleaning as required; regular inspection for rust; checking mechanical damage especially at radiators; checking all welded and gasketted joints for signs of oil leakage (clean any suspected leak area with methyl alcohol and spray with liquid chalk to confirm); checking oil level at conservator and all oil-filled bushings; and checking the silica-gel breather colour (should be blue/pink transition monitored). | YES | Regular | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Power transformers | PDF p. 20-21 | 2.2.3 Best Operation & Maintenance Practices | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 16-17). [PAGE CORRECTED: internal doc-label page(s) '16-17' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0009 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Power Transformer | NOT VERIFIED | Maintenance Schedule (Manned S/S) | Inspection items and frequency | PROCEDURE | Periodic inspection items for power transformers at manned substations, with frequency: ambient temperature (hourly), winding/oil temperature (hourly), load/voltage (hourly), oil level in transformer (weekly), oil level in bushings (weekly), relief vent diaphragm condition (weekly), abnormal internal noise (weekly), bus bar/cable box condition (weekly), dehydrating breather silica gel condition (monthly), bushings and gaskets (yearly), cooler fan/pump bearings (yearly), on-load tap changer mechanism (yearly), insulation resistance (yearly), oil dielectric strength test (yearly), earth resistance (yearly), major overhaul including lifting of core and coils (7 to 10 years). On-Load Tap Changer (OLTC) major maintenance items on the same manned-substation schedule include: checking leakage/seepage of oil from the main tank to the OLTC tank (weekly) and oil leakage from the OLTC itself (weekly); OLTC drive mechanism, OSR alarm/trip, and oil BDV/DGA for the OLTC tank (yearly); transformer turn ratio/voltage ratio and Dynamic Contact Resistance Measurement (DCRM) for health assessment of the tap changer, both at 5 years or after replacement of any primary part of the OLTC; and winding resistance of the HV winding on all taps, at the time of OLTC maintenance. | YES | Hourly to 7-10 years depending on item; OLTC oil leakage/seepage checks (weekly); DCRM (5 years or after OLTC primary-part replacement) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Power transformers at manned substations | PDF p. 26-30 | 2.2.4 Major Maintenance/Inspection Practices for Power Transformers | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 22-26). [PAGE CORRECTED: internal doc-label page(s) '22-26' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.] [KB_v1.1 CORRECTION: enriched Verified Information/Frequency to include the OLTC oil-leakage/seepage (weekly) and DCRM (5-year) items that appear on PDF p.29-30, within this chunk's existing declared page span (26-30), but were omitted from the original curated summary. Verified directly against the D09 PDF supplied for this task. Chunk ID, page span, and all other fields unchanged.]
D09-C0010 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Circuit Breaker | Vacuum/SF6 | Maintenance Schedule (Manned S/S) | Inspection items, mostly yearly | PROCEDURE | Before maintenance, the VCB/SF6 breaker must be isolated, auxiliary supply disconnected, and springs discharged by manual operation. Yearly maintenance items include: general/pole-assembly cleaning, insulator cleaning, lubricating/greasing operating mechanism, checking nut/bolt tightness, checking indications and tripping alarm, protection healthiness check (remote/local/manual/relay operation with reduced-voltage trip test), control/CT connection tightness, high-voltage testing, contact erosion check, earthing check, interlock check, closing/opening time measurement, contact resistance measurement, SF6 gas pressure and quality (dew point, purity, SO2 content) for SF6 breakers, vacuum interrupter test for VCBs. | YES | Mostly Yearly | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Vacuum Circuit Breakers (up to 33kV) and SF6 Circuit Breakers (66kV and above) | PDF p. 34-35 | 2.3.2 VCB/SF6 Breaker Maintenance Practices | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 30-31). [PAGE CORRECTED: internal doc-label page(s) '30-31' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0011 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Circuit Breaker | Oil Circuit Breaker | Maintenance Schedule (Manned S/S) | Inspection items by frequency | PROCEDURE | Oil Circuit Breaker (OCB) maintenance items span multiple frequencies: oil leakage check (weekly), oil level in gauges (weekly), tank temperature/noise/smell (weekly), cabinet lights and heaters (weekly), breathers and vents condition (weekly), nuts/bolts/jumpers tightness (monthly), drain plug tightness (monthly), local/remote operation check (yearly), latch and trip mechanism (yearly), IR values (yearly), earth resistance (yearly), main contacts inspection (yearly), oil dielectric and acidity test (yearly - oil should be filtered/replaced if dielectric strength falls below 25kV), oil testing in oil-filled bushings (two-yearly), complete overhaul (once in two years, subject to manufacturer recommendation). | YES | Weekly to two-yearly depending on item | NOT VERIFIED | Oil dielectric strength should not fall below 25kV; replace/filter oil if below this or if carbon suspension visible | NOT COVERED | Oil Circuit Breakers | PDF p. 36-39 | 2.3.3 Oil Circuit Breaker Maintenance Practices | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 32-35). [PAGE CORRECTED: internal doc-label page(s) '32-35' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0012 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Current Transformer (CT) | NOT VERIFIED | Maintenance Activities | Inspection items by frequency | PROCEDURE | Major CT maintenance activities: visual damage/deterioration check (weekly), oil leakage check (weekly), oil level (yearly), structure condition (yearly), unused core shorting verification (yearly), cable gland entry check (yearly), abnormal sound check with ultra-probe (yearly), bushing/terminal/junction box checks (yearly), IR values for primary-to-earth, secondary-to-earth, and primary-to-secondary (yearly), tan delta and CT turn ratio (yearly), body earth resistance (yearly), partial discharge/UHF/RFI/TEV signal checking (yearly). | YES | Weekly to Yearly | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Current Transformers in substation metering/protection circuits | PDF p. 40-41 | 2.4 Current Transformer (CT) - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 36-37). [PAGE CORRECTED: internal doc-label page(s) '36-37' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0013 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Potential Transformer (PT) | NOT VERIFIED | Maintenance Activities | Inspection items by frequency | PROCEDURE | Major PT/VT maintenance activities: abnormal sound check with ultrasonic detector (weekly), visual damage check (weekly), oil leakage check (weekly), fuse condition check (weekly), oil level sight glass/junction box/bushing checks (yearly), IR values for primary-to-earth, secondary-to-earth, primary-to-secondary (yearly), turns ratio and tan delta measurement (yearly), partial discharge/UHF/RFI/TEV signal checking (yearly), PT analysis (3-yearly). | YES | Weekly, Yearly, and 3-Yearly | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Potential/Voltage Transformers used for metering and protection | PDF p. 41-42 | 2.5 Potential Transformer (PT) - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 37-38). [PAGE CORRECTED: internal doc-label page(s) '37-38' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0014 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Surge Arrester | Lightning Arrester | Maintenance Activities | Inspection items by frequency | PROCEDURE | Major surge/lightning arrester (LA) maintenance activities: surge counter reading and leakage current recording (monthly), base/support inspection for cracking or shifting (monthly), surge monitor connection check (monthly), jumper/clamp tightness (yearly), porcelain shell cleaning and chip repair with lacquer (yearly), grading ring tightness (yearly), external gap check and readjustment (yearly), weather shed/hook fastening (yearly), line and ground connection tightness plus ground resistance check (yearly), operation tests / leakage or third-harmonic current measurement (yearly). | YES | Monthly and Yearly | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Surge/Lightning Arresters protecting switchyard equipment | PDF p. 43 | 2.6 Surge Arrester/Lightning Arrester - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 39). [PAGE CORRECTED: internal doc-label page(s) '39' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0015 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Isolator/Disconnector | NOT VERIFIED | Maintenance Activities | Inspection items, mostly yearly | PROCEDURE | Major isolator maintenance activities (all yearly): insulator crack/dirt check and chip repair with lacquer; blade seating in contacts; blade latch engagement; electrical and mechanical interlock check; bolt/nut/jumper tightness with petroleum jelly applied to male/female contacts; IR value, earth resistance and contact resistance measurement (CRM) checks, including double-earthing verification; auxiliary and limit switch contact condition; manual operating rod engagement and smoothness; operating mechanism box condition, vermin-proofing, interlocks, and DC leakage check. | YES | Yearly (all items) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Line isolators and earth switches | PDF p. 44 | 2.7 Line Isolators & Earth Switches - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 40). [PAGE CORRECTED: internal doc-label page(s) '40' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0016 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Gas Insulated Substation (GIS) | NOT VERIFIED | Maintenance Activities | Inspection items, all yearly | PROCEDURE | Major GIS maintenance activities (all yearly): physical inspection for damage/defects, indication working check, SF6 gas pressure check, outside-area cleanliness, CT secondary circuit connection check, insulation resistance test of all wiring, control and interlocking function test, contact resistance test, timing test for circuit breakers/disconnector switches/earth switches (with contact travel and speed analysis), trip-free and anti-pump circuit function test, equipment earthing check, repainting as needed, and component nomenclature verification. | YES | Yearly (all items) | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Gas Insulated Substations / Hybrid GIS | PDF p. 45 | 2.8 Gas Insulated Substation (GIS) - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 41). [PAGE CORRECTED: internal doc-label page(s) '41' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0017 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Battery Bank | NOT VERIFIED | Maintenance Activities | Inspection items by frequency | PROCEDURE | Battery system maintenance activities span multiple frequencies: battery room ventilation check (daily); dust cleaning of cells/charger (monthly); operation/charging rate/pilot cell specific gravity/temperature/floating voltage check (monthly); DC voltage at load bus and battery terminal check (monthly); leakage test by lamp or voltmeter method (monthly); cell jars/covers/plates/separators/electrolyte level checks (monthly); discharging and charging cycle per manufacturer schedule (half-yearly or continuous remote monitoring); battery cell temperature check (half-yearly or continuous remote monitoring); base/rack inspection, inter-cell connector cleaning, capacity discharge test, body earth resistance for charger, remote alarm circuit check (all yearly); complete overhaul as per manufacturer recommendation. | YES | Daily to Yearly depending on item | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Substation DC battery banks (Lead Acid / Nickel-Cadmium) and battery chargers | PDF p. 46-47 | 2.9 Battery Bank & Battery Chargers - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 42-43). [PAGE CORRECTED: internal doc-label page(s) '42-43' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0018 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Control & Relay Panel | 33kV/11kV | Maintenance Activities | Inspection items by frequency | PROCEDURE | C&R panel maintenance: indication lamp and illumination lamp/socket check (monthly); vermin-proofing of panel and door interlock switch, local/remote switch position, fuse/MCB rating, panel interior/exterior condition, relay/contactor condition, control connections, earthing connections, inter-panel coupling, multicore cable glands, cubicle heater/thermostat, wiring dressing, door sealing (all yearly); protection connections and space heater check at time of protection checking; communication connections check at time of communication checking. | YES | Monthly and Yearly, plus event-based checks | NOT VERIFIED | NOT VERIFIED | NOT COVERED | 33kV and 11kV Control & Relay Panels | PDF p. 48-49 | 2.10 Control & Relay Panel (33kV & 11kV) - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 44-45). [PAGE CORRECTED: internal doc-label page(s) '44-45' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0019 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Earthing System | NOT VERIFIED | Maintenance Activities | Inspection items by frequency | PROCEDURE | Substation earthing maintenance: earth pit check (monthly); earth connections at earth pits (half-yearly); double earthing for all equipment, earthing conductor adequacy/tightness, earthing pipe/conductor clamping, earth pit numbering, cast-iron lid availability, exposed conductor galvanizing/painting, earth isolator box green-colour marking, multicore cable earthing via cable gland, power cable single-end earthing, substation building/transformer neutral separate earth pits connected to switchyard mesh, earth pit resistance for power/distribution transformer neutral and for lightning arresters, and earth mesh resistance (all yearly). | YES | Monthly, Half-Yearly, Yearly | NOT VERIFIED | NOT VERIFIED | NOT COVERED | Substation earthing/grounding system | PDF p. 50-51 | 2.11 Earthing System of Sub-station - Major Maintenance Activities | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 46-47). [PAGE CORRECTED: internal doc-label page(s) '46-47' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0020 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Distribution Transformer | Oil-filled | Regular Inspection & Periodic Maintenance | Failure causes and preventive checklist | PROCEDURE | Major reasons for distribution transformer failure include insulation failure, HT/LT coil damage, core/lamination damage, tap switch/arrangement failure, water ingress, relay protection failure, and external LT-side faults. Minor reasons include improper HT/LT door closing (moisture/foreign-agent ingress), inadequate oil level due to leakage or pilferage, improper HT isolator homing, body/conservator rusting, tap link board failure, and high sludge content. Yearly maintenance checklist includes: oil level, silica gel breather colour (should be blue) and condition, bus-bar/palm connector arcing/pitting marks, gasket/flange/valve/radiator/bushing leak-free condition, lightning arrester connections, distribution/load cable joint tightness, bushing surface cleanliness and cracks, tank/neutral/body earthing, radiator surface cleanliness, fencing earthing, gasketed joint tightening, corrosion protection in corrosive environments, oil sampling for BDV, IR & PI measurement, partial discharge checking, explosion vent pipe checking. Distribution transformers are to be procured with standard ratings as per IS; the maximum allowable losses at rated voltage and rated frequency (permitted at 75°C) for distribution transformers are to be chosen by the utility as per IS 1180 (as amended), with no positive tolerance permitted. Per the Electrical Transformers (Quality Control) Order, 2015, distribution transformers must conform to IS 1180 Part-1 (2014) and bear the BIS Standard Mark (ISI marking is mandatory); BEE star rating is also mandatory on distribution transformers. | YES | Yearly (most items) | NOT VERIFIED | NOT VERIFIED | Insulation failure, HT/LT coil damage, core/lamination damage, tap switch failure, water ingress, relay protection failure, external LT-side fault, oil leakage/pilferage, rusting, tap link board failure, high sludge content | Oil-filled Distribution Transformers | PDF p. 53-57 | 3.1-3.2 O&M Benchmarking of Distribution Transformers | Verified against the official CEA D09 PDF supplied for this task; source content/page mapping checked against the rendered PDF (pp. 49-53). [PAGE CORRECTED: internal doc-label page(s) '49-53' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.] [KB_v1.1 CORRECTION: enriched Verified Information to include the IS 1180 max-allowable-losses / procurement-standard statement that appears on PDF p.54, within this chunk's existing declared page span (53-57), but was omitted from the original curated summary (which focused on the p.53 failure-causes content). Verified directly against the D09 PDF supplied for this task. Chunk ID, page span, and all other fields unchanged.]
D09-C0021 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | General | O&M Overview | Overhead line faults and corrective/preventive actions | GENERAL_GUIDANCE | Frequent overhead-line failures can result from damaged or punctured insulators, snapped/damaged conductors or jumpers, tree/foreign-material contact, bird faults, cracked poles, improper earthing, inadequate phase/neutral clearances, and inadequate clearances from other HT/LT lines. The guideline lists corrective/preventive actions covering replacement of defective insulators, jumper repair, tree pruning/removal of foreign material, bird-fault reduction, cracked-pole replacement, proper earthing, maintaining electrical clearances, pole guards, and public awareness about kite flying near power lines. | NOT COVERED | NOT COVERED | NOT VERIFIED | NOT VERIFIED | Overhead-line/conductor faults; insulator, conductor, pole, earthing and clearance issues | Sub-transmission and distribution overhead lines | PDF p. 68 | 4.1 Introduction; 4.1.1 Main Causes of Overhead Line Faults; 4.1.2 Corrective & Preventive Action | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '64' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0022 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | Sub-transmission & Distribution Lines | Repair & Maintenance Conditions | Worksite preparation and line maintenance requirements | PROCEDURE | For repair and maintenance of distribution lines, O&M personnel should de-energize and isolate the network, verify isolation with a neon tester, and properly ground the network. Branch lines in the working zone should be isolated and distribution transformers within the zone switched off to avoid back feeding. Personnel should have appropriate tools, accessories, safety apparel, spares and consumables. Where double circuits share a pole/tower, charged and dead lines should be identified using red and green flags. The guideline also specifies straight pole erection/maintenance, suitable stays, feeder-appropriate conductor checks, tightened earth connections, same-conductor jumpers, anti-climbing devices and danger boards, feeder identification, visual pole/insulator inspection, suitable guarding, conductor re-sagging, earth-wire/earth-electrode repair, and cable mounting with adequately strong clamps. | De-energize; isolate; verify with neon tester; ground the network; isolate branch lines and switch off DTs in the working zone; use proper tools/PPE/spares; mark charged/dead circuits; inspect poles, conductors, insulators and earthing; repair/replace defective components. | Before/during maintenance | Pole deviation >5° from end/branch-out poles is identified for stay provision in the guideline; jumper length >1 m should be supported by an insulator. | De-energization, isolation, grounding, safety apparel, danger boards and anti-climbing devices are required/identified for safe maintenance. | Back feeding; damaged conductor; improper earthing; defective insulators; pole deviation; line identification issues | Sub-transmission and distribution lines | PDF p. 68-70 | 4.2 Necessary Conditions during O&M of Sub-transmission & Distribution Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '64-66' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0023 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | Overhead Lines | Patrolling | Normal ground patrolling | PROCEDURE | Utilities should plan pre-monsoon and post-monsoon maintenance of the distribution network. HT overhead lines should normally be attended twice a year, before and after the monsoon. Ground-patrolling periodicity is to be decided based on line importance, terrain, proximity to habitations/forests/gardens/water bodies and environmental impact. Patrolmen should check location and pole information, ground and air clearances, pole condition, nearby obstructions such as trees/branches/structures, condition of insulators/conductors/earth wire/jumpers/clamps/dampers/spacers, guarding, and line-crossing clearances. | Conduct pre-monsoon and post-monsoon patrols; during patrol record line/pole location information and inspect clearances, poles, nearby obstructions, line hardware, guarding and crossings. | Twice yearly for HT lines; other periodicity based on line importance and site conditions | Pre-monsoon and post-monsoon patrolling is necessary. | NOT VERIFIED | Tree/structure obstruction; inadequate clearance; damaged line hardware; guarding/crossing issues | Overhead distribution network | PDF p. 70-71 | 4.2.1 Normal Ground Patrolling | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '66-67' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0024 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | Overhead Lines | Patrolling & Breakdown Maintenance | Special patrolling and breakdown maintenance | PROCEDURE | Special line patrolling should be carried out after momentary or permanent tripping or when defects are identified. Defects should be rectified immediately when they can be safely attended on a live line, or at the earliest available shutdown. Material and manpower should be planned so shutdown rectification takes minimum time and interruption to consumers is minimized. Permanent or semi-permanent faults can cause longer-duration breakdowns; examples include snapped conductors, disconnected jumpers, twisted cross-arms/poles and pole collapse, with possible causes including storms/heavy wind, aging, accidents and theft. | After tripping or observed defects, patrol the line, identify and rectify defects safely or arrange shutdown; plan material and manpower for rapid restoration. | After tripping/defect; at earliest shutdown where required | NOT VERIFIED | Live-line work is mentioned as an option only where the defect can be safely attended while the line is live; otherwise use shutdown. | Snapped conductors; disconnected jumpers; twisted/collapsed poles; storm, aging, accident or theft-related damage | Overhead distribution lines | PDF p. 71 | 4.2.2 Special Patrolling of the Lines; 4.2.3 Breakdown Maintenance | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '67' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0025 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | Overhead Lines | General Maintenance | Pole, stay, guarding and line-hardware inspection | PROCEDURE | General OH-line maintenance includes visual inspection of pole base and alignment, stay condition, GI wire condition/size, guy insulator, guarding-wire earthing, tension screw and anchor hook. Line hardware inspection covers disc and pin insulators, strain clamps, pin-insulator spindles, top hamper, V-arm and channel-arm condition, with replacement/straightening/tightening as applicable. Metal parts on the pole should have proper earthing. | Inspect poles, stays, GI wires, guy insulators, guarding, tension screws, anchor hooks and line hardware; replace cracked/flash-marked insulators or damaged hardware and tighten fixing nuts/bolts as specified. | NOT COVERED | NOT VERIFIED | Proper earthing of metal parts is required. | Tilted/bent poles; damaged stays/GI wires; cracked or flash-marked insulators; damaged clamps/arms | Overhead distribution lines | PDF p. 71-72 | 4.3 General Maintenance Activities of OH Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '67-68' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0026 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | ABC / Bare Conductor | Conductor & ABC Maintenance | Bare-conductor and aerial-bunched-cable inspection | PROCEDURE | For bare conductors, damaged sections should be replaced using the same conductor with a sleeve joint; loose conductors should be re-sagged and required conductor spacing maintained. For AB/ABC cable feeders, patrolling should identify and remove unauthorized tappings before work. The copper screen of HT ABC and messenger wire should be earthed at starting and ending points. Temporary AB-cable joints should not be used; emergency joints should be properly made the next day, and messenger-wire mid-span joints should use a sleeve rather than binding wire. AB cable should be laid using rollers and pulleys rather than dragged; branches may be trimmed where vegetation could abrade the cable. | Inspect conductor condition and sag; replace damaged conductor with same conductor and sleeve joint; patrol ABC feeders; check screen/messenger earthing; use proper joints and rollers/pulleys for AB cable installation. | NOT COVERED | NOT VERIFIED | Ensure proper earthing of HT ABC screen and messenger wire; use appropriate safety apparel and tools. | Damaged/loose conductor; unauthorized tapping; temporary/poor cable joints; vegetation abrasion | Overhead conductors and AB/ABC distribution feeders | PDF p. 72-73 | 4.3.1 Visual Inspection of Bare Conductor; 4.3.2 Inspection of ABC Line | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '68-69' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0027 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | 33 kV Lines | Maintenance Schedule | Poles, stays and cross-arms/pole-top steelwork | PROCEDURE | For 33 kV lines, half-yearly inspection covers steel/wood/cement poles for damage, breakage, ground-level erosion/corrosion, bowing/leaning, unauthorized attachments, exposure to animal/vehicle impact, distinct pole number plates, foundations and painting requirements. Stays should be checked for direction/angle, looseness or damage, intact stay insulators/earthing and rod corrosion. Cross-arms and pole-top steelwork should be checked for slipped clamps/knees, bending from uneven tension, excessive rusting, cracked/split wooden cross-arms and loose/damaged bracings. | Inspect poles, foundations, stays and cross-arms; attend damage, corrosion, leaning, painting, loose/damaged bracing and stay issues as required. | Half yearly | NOT VERIFIED | Check stay earthing and line condition before/while carrying out maintenance. | Damaged/broken/corroded poles; leaning poles; damaged stays; bent/rusted/cracked cross-arms | 33 kV overhead lines | PDF p. 73 | 4.4 Major Maintenance Activities for 33 kV Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '69' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0028 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | 33 kV Lines | Maintenance Schedule | Insulator inspection | PROCEDURE | For 33 kV lines, half-yearly inspection covers broken or chipped porcelain and flashover marks, tilted insulators, excessive deposits of dust/salt/coal or other pollution, and excessive rusting of fittings. Polluted insulators should be cleaned and rusted fittings replaced where required. | Inspect insulators and fittings; clean polluted insulators and replace rusted or damaged fittings as required. | Half yearly | NOT VERIFIED | NOT VERIFIED | Broken/chipped porcelain; flashover marks; tilted insulators; pollution deposits; rusted fittings | 33 kV overhead lines | PDF p. 73-74 | 4.4 Major Maintenance Activities for 33 kV Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '69-70' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0029 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | 33 kV Lines | Maintenance Schedule | Conductors, earth wire and line guards | PROCEDURE | For 33 kV lines, half-yearly inspection covers conductor/earth-wire attachment and sag, proximity to trees/objects/buildings, conductor-to-earth-wire and ground clearances, clearances from other electric/telephone lines, earth-wire support, line guards, jumper/conductor joints, broken strands, nicking near insulator necks or conductor clamps, loose binding wire, cracked mid-span joints, and proper clamps/jointing sleeves on aluminium-conductor joints. Jumpers and accessories should have suitable supports and clearances, proper insulation where specified, and no overheating/burning; thermo-scanning is listed as an inspection activity. | Inspect conductor sag, clearances, earth-wire support, guards, joints, strands, bindings, jumpers and fittings; correct defects and use thermo-scanning for signs of overheating/burning. | Half yearly | NOT VERIFIED | Maintain required clearances and line guards; inspect for overheating and defective joints. | Broken strands; cracked mid-span joints; loose bindings; overheating; inadequate clearances; defective clamps/sleeves | 33 kV overhead lines | PDF p. 74 | 4.4 Major Maintenance Activities for 33 kV Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '70' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0030 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | 33 kV Lines | Maintenance Schedule | Tree trimming, bird nests and insulators | PROCEDURE | For 33 kV lines, half-yearly maintenance includes tree trimming to maintain a minimum clearance of 1.8 m on each side of the line, removal of dead wood, and removal of bird nests before the monsoons or earlier if necessary. Insulators should be cleaned and examined for cracks or flashover, with replacement where necessary; this insulator inspection item is listed annually. | Trim trees and remove dead wood/bird nests; clean and examine insulators and replace where necessary. | Half yearly for tree/bird-nest activities; annually for the listed insulator cleaning/examination item | Minimum 1.8 m clearance on each side of the line for the tree-trimming item. | Vegetation and bird-nest removal must be performed as line-maintenance work with appropriate safety controls. | Tree contact; dead wood; bird nests; cracked/flashover insulators | 33 kV overhead lines | PDF p. 74-75 | 4.4 Major Maintenance Activities for 33 kV Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '70-71' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0031 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | 11 kV Lines | Maintenance Schedule | 11 kV line and cable-box maintenance | PROCEDURE | For 11 kV lines, the pole/stay/cross-arm/conductor/insulator/earth-wire/lightning-arrester/earthing-system maintenance is stated to be the same as recommended for 33 kV lines, with half-yearly/yearly frequency. GO switches/DO fuses are checked half-yearly for overheating/burning, corrosion/pitting, damaged insulators, tight earth connections, fuse-link continuity/tightness/correct rating, locking, switch-contact alignment, complete male/female contact fitting and intact arcing horns. 11 kV cable and cable boxes are checked annually for support, damaged insulators, tight/intact connections, proper earthing and overall cable/joint condition; damaged bushings, compound leakage, insulation resistance and records of insulation-resistance tests are also checked annually. | Perform the listed 11 kV inspections at the stated frequencies; check switches/DO fuses, cable supports, connections, earthing, bushings, compound level and insulation resistance. | Half yearly / Yearly depending on item | NOT VERIFIED | Proper earthing and safe inspection of 11 kV equipment are required. | Overheating/burning; corroded contacts; broken insulators; poor earthing; cable/joint damage; compound leakage; low insulation resistance | 11 kV overhead lines and cable boxes | PDF p. 75-76 | 4.5 Maintenance Activities for 11 kV Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '71-72' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0032 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | LT Lines | General Maintenance | LT line poles, hardware, conductor and earthing | PROCEDURE | General LT-line maintenance includes checking pole base/alignment and foundation, stays, GI wire, guy insulator, tension screw and anchor hook; visual inspection of line hardware such as insulators, spindles, double-line X-arms and fixing hardware; painting metal parts for durability; inspecting bare conductors and replacing damaged conductor using the same conductor with sleeve joint (with the number of joints limited to a maximum of 2 per span); using line spacers to prevent snapped-conductor fall and maintain conductor spacing; inspecting earthing and replacing damaged earth wire/electrode; inspecting joints and jumpers; mounting cables on OH feeders through GI/DWC/HDPE pipes with clamps/STP; and cleaning cable/conductor surfaces and applying anti-corrosive grease before termination at a distribution box. | Inspect and maintain poles, stays, line hardware, conductors, spacers, earthing, joints and cable mounting; replace damaged components and tighten/secure fixing hardware as specified. | NOT COVERED | Maximum 2 sleeve joints per span for the listed damaged-conductor replacement practice. | Inspect and maintain earthing; use appropriate line-maintenance safety practices. | Tilted/bent poles; damaged stays/insulators; conductor damage; earth-wire/electrode joints; cable-mounting issues | LT overhead lines | PDF p. 77-78 | 4.6 General Maintenance Activities of LT Lines; 4.6.1 General Maintenance | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '73-74' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0033 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Overhead Lines & Cables | LT Lines | Maintenance Schedule | LT switch and cable maintenance | PROCEDURE | For LT lines, annual maintenance checks include poles/stays/cross-arms/conductors/insulators/connectors/cable boxes as recommended above. LT switches are checked for intact covers, heating, broken cut-outs, overheating/burning contacts, correct fuse-wire size, earthing, rain-water protection, fuse-box and LT-neutral earthing, adequate LT-circuit capacity, damaged LT cable replacement, smooth switch operation, burnt/cracked cut-out replacement, switch-contact reconditioning, correct-capacity fuse replacement, tight connections, sealing cable entry against rain water, and removal of cobwebs/nests. | Inspect LT switches and associated cable components annually; repair/replace damaged cables, cut-outs, fuses, contacts and seals; tighten connections and clean internal switch areas. | Annually | NOT VERIFIED | Ensure proper switch and neutral/fuse-box earthing and protection from rain water. | Overheating; damaged cable; burnt/cracked cut-outs; incorrect fuse capacity; loose connections; water ingress | LT lines and LT switches | PDF p. 78-79 | 4.6.2 Maintenance Activities for LT Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '74-75' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0034 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Underground Cables | Cable Installation | Maintenance | Inspection and current-loading checks | PROCEDURE | For underground cable maintenance, the guideline states that the code of practice in IS-1255 should be followed. Maintenance includes inspection, routine current-loading checks, and care of cables and end terminations. Accessible cables/joints in manholes, ducts and distribution pillars should be periodically inspected; inspection frequency is to be determined from utility experience, with heavily loaded lines requiring more frequent attention. Direct-buried cables should be protected through regular inspection of digging operations by other utilities/persons in cable areas. In congested cities, maintenance teams should patrol areas where cables are exposed and inspect for deformation/dents and damage to troughs/ducts. Paper-insulated cables should not be overloaded; derating factors for grouping, ambient ground temperature and soil thermal resistivity should be considered. HV feeder cable panel ammeters should be read daily; distributor loads should be checked at intervals not exceeding three months. | Periodically inspect accessible cables/joints; patrol exposed cable areas; check current loading and account for derating factors; read HV feeder cable ammeters daily and check distributor loads at intervals not exceeding three months. | Daily for panel-mounted HV feeder ammeters; distributor loads at intervals not exceeding 3 months; other inspection frequency based on utility experience | Distributor load checks: not exceeding 3 months; paper-insulated cables should not be loaded beyond safe current-carrying capacity. | Cable work and excavation areas require appropriate protection and safe maintenance practices. | Cable damage from excavation; deformation/dents; overloading; environmental/soil derating | Underground distribution cables | PDF p. 79-80 | 4.7 Underground Cables; 4.7.1 Maintenance of Cable Installation | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '75-76' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0035 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Underground Cables | Cable Installation | Maintenance Quality | Cable repair and cross-checking of maintenance | PROCEDURE | Cable repairs generally involve replacement of a defective cable section by a length of new cable and insertion of two straight joints; repairs and new joints associated with repairs should be made in the same manner as joints on new cables. For quality maintenance, at least 5% of departmental maintenance work may be cross-checked by the Division office and 2% by the Circle office. Where work is outsourced, cross-checking should be done before passing contractor bills. Rigorous monitoring and feeder-wise SAIFI/SAIDI evaluation should be discussed in line-staff meetings; the guideline also describes recognition of the best feeder of the month. | Repair defective cable sections with new cable and two straight joints; cross-check maintenance work at the stated organizational levels; monitor feeder-wise SAIFI/SAIDI in line-staff meetings. | NOT COVERED | 5% departmental work may be cross-checked by Division office; 2% by Circle office. | NOT VERIFIED | Defective cable section; poor-quality maintenance; feeder reliability deterioration | Underground cable maintenance and outsourced/departmental maintenance work | PDF p. 80-81 | 4.7.1 Maintenance of Cables; 4.7.2 Quality of Maintenance & Cross Checking | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '76-77' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0036 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Live-Line / Hotline Maintenance | Distribution Lines & Substations | Live-Line Maintenance | Overview, benefits and application in India | GENERAL_GUIDANCE | Live-line/hotline maintenance is maintenance, repair or replacement carried out on an energized and operational line or switchyard apparatus using approved techniques and equipment. It is presented as a method to maintain system integrity/reliability and reduce interruptions while enabling maintenance on energized equipment. Listed benefits include reduction of scheduled outages and breakdown interruptions, greater maintenance-management flexibility, uninterrupted/timely maintenance, improved reliability/efficiency, timely routine maintenance, reduced breakdown expense, optimized generation facility, increased utility revenue, greater consumer satisfaction and reduced planned-outage maintenance. The guideline notes historical use in India for transmission at 220 kV and above and growing adoption at distribution level. | NOT COVERED | NOT COVERED | NOT VERIFIED | Live-line work is performed on energized equipment and therefore requires approved techniques, equipment and safe work procedures. | Interruptions/breakdowns requiring maintenance while maintaining supply continuity | Distribution lines and switchyards | PDF p. 81-82 | 4.8 Live Wire / Hot Line Maintenance of Distribution Lines; 4.8.1 Major Benefits; 4.8.2 Live-Line Working in India | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '77-78' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0037 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Live-Line / Hotline Maintenance | Distribution Lines | Live-Line Methods | Hot-stick, bare-hand and rubber-glove methods | PROCEDURE | The guideline describes live-line methods: hot-stick/distance technique uses an insulated glass stick and is generally suitable up to 220 kV; bare-hand technique places the lineman at the live potential while maintaining isolation from grounded surroundings and is used above 132 kV up to 800 kV; rubber-glove/contact technique electrically insulates the worker from ground using an insulated elevated platform and approved insulating gloves/sleeves and is useful for distribution networks up to 33 kV. Routine live-line tasks may include insulator replacement, on-load clamp/connector tightening, strengthening dead-end joints, jumper and mid-span-joint replacement, conductor repairs, and insulator-hardware maintenance/replacement using appropriate tools and equipment. Insulated aerial work platforms and conductor trolleys can improve live-line work access and safety. | Use the live-line method and equipment appropriate to the voltage and work; maintain required isolation from grounded surroundings and use approved insulating equipment. | NOT COVERED | Hot-stick generally up to 220 kV; bare-hand above 132 kV up to 800 kV; rubber-glove/contact useful for distribution networks up to 33 kV. | Live-line work requires approved insulating equipment, suitable isolation and safe working practices; use insulated aerial platforms/tools as described. | Insulator faults; connector/clamp issues; jumper/conductor defects; switchyard component maintenance | Live distribution lines and switchyards | PDF p. 82-84 | 4.8.3 Live-Line Working Methods | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '78-80' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0038 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Live-Line / Hotline Maintenance | Distribution Lines & Substations | Hotline Maintenance | Major works, safety practices and drone inspection | PROCEDURE | Listed hotline works include tightening/replacement of clamps and connectors; replacement of defective pin/disc insulators; full-load conductor and mid-span-joint repairs; cross-arm/insulator/support replacement; jumper repair/replacement; live-line insulator cleaning; uninterrupted tree trimming; hardware/spacer/damper changes; repair sleeves and mid-span joints; damaged-conductor repair; pole changing; live-line washing; online jumper tightening/nut-bolt changes; and switchyard bus/isolator work. Safety is to be supported by safe work procedures, standards/manuals, pre-service equipment such as hot sticks, ropes and conductive-suit testers, proper cleaning/conditioning of live-line tools, in-service leakage-current monitors, and controls against back-feeding or accidentally charged circuits. The guideline also describes drone-based inspection for critical lines/towers/equipment, AI/ML-based predictive-maintenance analysis, asset mapping, fault detection and vegetation/encroachment assessment. | Follow approved safe-work procedures and applicable manuals/regulations/standards; use and maintain live-line tools and equipment; use leakage-current monitoring and controls against back feeding/accidental energization. Drones may be used for inspection, mapping and vegetation/encroachment assessment. | NOT COVERED | NOT VERIFIED | Safe work procedures, hot sticks, ropes, conductive-suit testers, conditioned live-line tools and leakage-current monitors are specifically identified; back-feed/accidental energization risks should be controlled. | Live-line maintenance risks; back feeding; accidental charging; vegetation/encroachment issues | Distribution lines and substations | PDF p. 84-85 | 4.8.4 Major Hotline Maintenance Works; 4.8.5 Drone Based Inspection of Lines | Added from and verified against the official D09 PDF supplied for this task; Chapter 4 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '80-81' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0039 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Distribution Utilities | Safety Management | Safety Management System overview | GENERAL_GUIDANCE | A Safety Management System (SMS) provides a framework to improve employee safety and health, reduce workplace risks and create safer working conditions. The guideline describes SMS as an organization-wide approach involving processes, practices and policies for managing safety risks, and states that safety should be treated with the same importance as other fundamental business activities. | Establish and maintain a comprehensive safety management system covering safety risks, controls, policies and practices across the distribution utility. | NOT COVERED | NOT VERIFIED | Safety is to be treated as a fundamental business activity. | Workplace risks; employee safety and health | Distribution utilities | PDF p. 93 | Chapter 6 Safety Management | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '89' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0040 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Occupational Health & Safety | Safety Management | ISO 45001:2018 requirements | GENERAL_GUIDANCE | The guideline states that ISO 45001:2018 provides requirements for an occupational health and safety management system and can be applied by DISCOMs. Key requirements listed are hazard identification, risk assessment, legal compliance, objectives and targets, employee participation, training and competence, and emergency preparedness and response. | Identify hazards, assess associated risks, comply with applicable legal requirements, establish safety objectives and targets, involve employees, ensure competence, and maintain emergency-response procedures. | NOT COVERED | NOT VERIFIED | ISO 45001:2018 is identified as the occupational health and safety management system standard. | Electrical distribution hazards and occupational safety risks | Distribution utilities | PDF p. 93-94 | Chapter 6 Safety Management; ISO 45001:2018 key requirements | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '89-90' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0041 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Safety Competency | Training & Competence | Safety competency mapping and certificates | PROCEDURE | DISCOMs should create a system of safety competency mapping including class/field training and written or verbal competency tests, with competency certificates for critical operations. The guideline states that resources engaged in distribution-system operations, including vendor resources, should have valid safety competency certificates. | Conduct appropriate class/field safety training and competency tests and issue competency certificates for critical operations; ensure engaged resources have valid certificates. | NOT COVERED | NOT VERIFIED | Valid safety competency certificates are required for resources engaged in distribution-system operations. | Competency for critical operations; vendor resources | Distribution-system operations | PDF p. 93 | Chapter 6 Safety Management; ISO 45001:2018 training and competence | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '89' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0042 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Safety Management System | CEA safety provisions | Safety as an integral part of work processes | GENERAL_GUIDANCE | The distribution utility shall make safety an integral part of work processes to ensure safety for employees including employees of contractor, sub-contractor as well as visitors. | Integrate safety into work processes and apply safety controls to employees, contractor/subcontractor personnel and visitors. | NOT COVERED | NOT VERIFIED | Safety responsibility extends to employees, contractor/subcontractor employees and visitors. | NOT COVERED | Distribution utilities | PDF p. 94 | Chapter 6 Safety Management; CEA safety provisions | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '90' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0043 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Safety Management System | Policy, responsibilities and resources | Safety management system elements | PROCEDURE | The distribution utility shall set up a sound and scientific safety management system including a written safety and health policy signed by the owner and displayed prominently; defined and documented responsibilities for all functionaries including contractors; a detailed safety manual complying with statutory requirements; hazard-identification and control procedures with SOPs for hazardous events; adequate human, physical and financial resources; a safe working environment; medical facilities; adequate training; accident reporting, analysis and investigation; communication, documentation and records; emergency management planning; internal and external audits; periodic management review; and oversight of contractor safety performance. | Develop and document the safety policy, responsibilities, safety manual, hazard-control procedures, resources, medical arrangements, training, accident-management processes, records, emergency plans, audits and management review as applicable. | Periodic management review; otherwise NOT COVERED | NOT VERIFIED | Safety policy, hazard controls, training, medical facilities, accident reporting, emergency management, audits | NOT COVERED | Distribution utilities | PDF p. 94-95 | Chapter 6 Safety Management; CEA safety provisions (3)(a)-(n) | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '90-91' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0044 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Safety Officer | Safety Management Roles | Safety officer appointment and duties | PROCEDURE | Where the number of employees including contract workers exceeds 200, the distribution utility shall appoint one qualified safety officer; where the number of employees is less than 200, a suitable officer shall be designated as safety officer. The safety officer shall develop and organise safety training programmes at regular intervals and create safety awareness among employees. | Appoint/designate the required safety officer based on employee strength and organize regular safety training and safety-awareness activities. | Regular intervals | Qualified safety officer required when employees including contract workers exceed 200; suitable officer designated when fewer than 200. | Safety officer is responsible for safety training and awareness. | NOT COVERED | Distribution utilities | PDF p. 95 | Chapter 6 Safety Management; Safety officer | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '91' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0045 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Electrical Safety Officer | Safety Management Roles | Electrical Safety Officer | PROCEDURE | The distribution utility shall designate an Electrical Safety Officer for ensuring observance of safety measures specified in the CEA (Measures relating to Safety and Electric Supply) Regulations, 2010 for construction, operation and maintenance of power stations, substations, transmission and distribution lines. The Electrical Safety Officer shall meet the qualifying criteria in the regulations. | Designate an Electrical Safety Officer and ensure that the officer meets the regulatory qualifying criteria and oversees observance of specified safety measures. | NOT COVERED | NOT VERIFIED | The Electrical Safety Officer covers construction, operation and maintenance of power stations, substations, transmission and distribution lines. | NOT COVERED | Distribution utilities | PDF p. 95-96 | Chapter 6 Safety Management; Electrical Safety Officer | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '91-92' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0046 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Contractor Safety | Safety Management | Safety provisions relating to contractors | PROCEDURE | Safety provisions are to be incorporated in contract documents. Contractors must observe the contractual safety requirements, and the main contractor is responsible for ensuring safety requirements are followed by subcontractor employees. The contractor is responsible for non-compliance, implications, injuries, fatalities and compensation arising from such situations. In case of an accident, the contractor shall immediately submit a statement to the owner and safety officer containing accident, injury/casualty, property-damage and remedial-action details. | Include safety provisions in contracts; ensure contractor and subcontractor compliance; require immediate accident reporting with the specified details. | Immediately for accident reporting | NOT VERIFIED | Contractor and subcontractor safety requirements and accident reporting. | Non-compliance, injuries, fatalities and property damage arising from safety incidents. | Distribution utilities | PDF p. 96 | Chapter 6 Safety Management; Safety provisions relating to contractor | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '92' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0047 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Medical Facilities | Occupational Health | Medical facilities by workforce size | PROCEDURE | For premises with 50 or fewer employees including contract workers, the utility should arrange a medical officer on retainer-ship for pre-employment and periodic medical examination and emergency assistance, have at least five first-aid-trained persons with at least one available during working hours, and maintain a fully equipped first-aid box. For 51-200 employees, an occupational health centre, part-time medical officer visiting at least twice a week, a qualified dresser-cum-compounder during working hours, and fully equipped first-aid boxes in departments are specified. For more than 200 employees, an occupational health centre is specified. | Provide medical and first-aid arrangements according to the number of employees including contract workers at the premises. | At least twice a week for the specified part-time medical officer in the 51-200 category; first-aid availability during working hours | ≤50; 51-200; >200 employees including contract workers | Medical and first-aid facilities | NOT COVERED | Distribution utility premises | PDF p. 96-97 | Chapter 6 Safety Management; Medical facilities | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '92-93' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0048 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Safety Training | Training & Awareness | Safety training programme contents | PROCEDURE | Regular safety training programmes for employees are to include general safety awareness, first aid, emergency procedures including shock treatment, personal protective equipment, safety precautions while handling electro-mechanical equipment, firefighting equipment, emergency response for fire/flood/landslide/earthquake, site-specific hazards and precautions/response, and ten hours of training per year for each employee. The distribution utility shall ensure adequate safety training by contractors for their employees. Safety promotional activities may include safety days/weeks, fire-safety activities, competitions, posters, slogans, calendars and displays. | Conduct the listed safety training and awareness activities and ensure contractors provide adequate safety training to their employees. | Regular; 10 hours per year per employee | 10 hours training per year per employee | General safety, first aid, emergency response, PPE, firefighting, site-specific hazards | NOT COVERED | Distribution utilities and contractor employees | PDF p. 97 | Chapter 6 Safety Management; Safety training and awareness | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '93' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0049 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Safety Management | Electrical Accident Reporting | Accident Management | Electrical accident reporting deadlines | PROCEDURE | If an electrical accident occurs in connection with generation, transmission, distribution, supply or use of electricity, notice of the occurrence shall be reported to the Electrical Inspector. For a fatal accident, the utility shall send a telegraphic report within 24 hours of knowledge of the occurrence and a written report in Form A within 48 hours of knowledge of the occurrence of fatal and all other accidents. The Appropriate Government may require an Electrical Inspector or another appointed person to inquire into and report the cause. | Report electrical accidents to the Electrical Inspector using the specified reporting channels and deadlines; submit Form A within the stated period. | Telegraphic report within 24 hours for fatal accident; Form A written report within 48 hours for fatal and all other accidents | 24 hours and 48 hours reporting deadlines | Electrical accidents connected with generation, transmission, distribution, supply or use of electricity | NOT COVERED | Distribution utilities | PDF p. 98 | Chapter 6 Safety Management; Electrical Accident | Added from and verified against the official D09 PDF supplied for this task; Chapter 6 content mapped to the printed page numbers in the PDF. [PAGE CORRECTED: internal doc-label page(s) '94' -> verified physical PDF page(s) via direct page-marker mapping against real PDF, confirmed offset +4 (0 exceptions found across 115 sampled internal page labels). Cross-validated against Member 3's independent manual verification for overlapping sections — fully consistent.]
D09-C0050 | D09 | OM_Benchmarking_for_Discoms_CEA_Guidelines.pdf | Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities | Central Electricity Authority | HIGH | Circuit Breaker | Vacuum Circuit Breaker (VCB) / SF6 Circuit Breaker / Oil Circuit Breaker (OCB) | Circuit Breakers | Types, arc-quenching medium, and voltage-level applicability | FACT | Circuit breakers used in the network include Oil Circuit Breakers (OCB), Vacuum Circuit Breakers (VCB), and SF6 (Gas) Circuit Breakers. In VCBs, arc quenching takes place in a vacuum medium inside a vacuum interrupter; in OCBs, oil is used as the arc-quenching medium; in SF6 breakers, sulphur hexafluoride gas serves as both insulating and arc-quenching medium. VCBs are generally used up to 33 kV, while SF6 breakers are used at 66 kV and above voltage levels. | NO | NOT APPLICABLE | VCB: generally used up to 33 kV; SF6: used at 66 kV and above voltage levels | NOT COVERED | NOT COVERED | Circuit breakers (OCB/VCB/SF6) across substation voltage classes | PDF p. 33 | 2.3 Circuit Breakers | [KB_v1.1 ADDITION: new chunk created to close a chunk-coverage gap. D09-C0009 ends at PDF p.30 and D09-C0010 begins at PDF p.34, leaving PDF p.33 (Section 2.3 Circuit Breakers, VCB/SF6 voltage-level applicability) without any chunk in KB_v1. Verified directly against the D09 PDF supplied for this task. Chunk ID D09-C0050 is the next available number in the existing D09 sequence (D09-C0001 through D09-C0049).]

## README
Workbook | knowledge_chunks_MEMBER1_FINAL_VERIFIED.xlsx
Purpose | Quality-controlled core knowledge chunks for the SIH substation-maintenance RAG.
Sources included | D01, D02, D03, D04, D05, D06, D07, D08, D09 (all 9 catalog documents; IDs match document_catalog.xlsx).
Explicitly excluded | None — all 9 documents from document_catalog.xlsx are represented in this workbook.
Verification rule | Rows retained from the previous extraction only when the verified information was found on the claimed PDF page; duplicates and likely TOC/heading rows were removed.
D01 limitation | 765_powerplants.pdf is image-based. Only 23 chunks from OCR-confirmed pages available in this workspace were included. Unprocessed D01 pages are NOT claimed to be covered.
Important | This is a rebuilt verified core, not a claim that every useful statement in all 8 PDFs has been exhaustively extracted.
Recommended use | Use as a reviewed source layer; before production ingestion, review high-impact numerical limits, frequencies and procedures with the original PDF page.
Questions | No 55-question or 100-question dataset is included.
ID note | Document IDs in this workbook were realigned to match document_catalog.xlsx exactly (Tender_Part-1 = D07, Transformer_Manual = D08). Earlier drafts used different numbering.

## QA_Summary
Metric | Value
Total chunks | 1744
D01 chunks | 23
D02 chunks | 40
D03 chunks | 12
D04 chunks | 170
D05 chunks | 54
D06 chunks | 463
D07 chunks | 133
D08 chunks | 800
D09 chunks | 49