## Observable Issues
Issue | Equipment | Can genuinely be observed visually? | What evidence would an image provide? | What image cannot establish | Source
Visible corrosion | Multiple | Yes, for exposed surfaces | Image can show rust/corrosion, discoloration, pitting or degraded visible hardware. | Visual evidence does not establish structural integrity or electrical performance. | D01; D02; D05; D06; D09
Oil leakage/staining | Oil-filled transformer / oil-filled instrument equipment / applicable switchgear | Yes, as an observation | Image can show wet areas, oil staining, drips or residue around accessible external joints. | Image cannot establish leak rate, oil chemistry, internal fault, or safe operating condition. | D03; D04; D06; D08; D09
Physical damage/cracking | Insulators, bushings, enclosures, supports, panels | Yes, if visible and image quality is sufficient | Image can show cracks, chips, deformation, broken covers or damaged hardware. | A photo cannot determine dielectric strength or internal damage. | D01; D02; D06; D09
Vegetation/foreign-object obstruction | Switchyard / busbar area / equipment clearances | Yes, when visible | Image can show vegetation, debris or objects intruding into accessible visual field. | Image alone cannot prove electrical clearance compliance unless geometry/reference is known. | D01; D02; D05; D09
Discoloration/thermal damage | Connections, terminals, switchgear, busbar hardware, panels | Yes, as a visual symptom | Image may show localized discoloration, soot or heat damage. | Photo cannot quantify temperature or prove cause; thermography/measurement may be required. | D01; D06; D09
Gauge/indicator reading | Transformer and other equipment with readable indicators | Sometimes, if scale/digits are legible | Image can capture displayed value/status/position. | Image reading can be wrong due to angle, glare, resolution or scale; it does not prove underlying condition. | D04; D08; D09
Corroded/loose-looking earth connection | Earthing system / equipment bonds | Yes, for visible condition | Image can show corrosion, broken conductor, damaged clamp or obvious disconnected bond. | Photo cannot establish earth resistance, continuity of the whole grid, touch/step potential or fault-current performance. | D02; D05; D09
Damaged relay/panel indication | Protection relay/control panel | Yes, for visible alarms/labels/damage | Image can show alarm LEDs, target indications, display text and physical damage. | Photo cannot prove relay settings, logic, calibration or trip performance. | D01; D02; D05; D09
Battery swelling/leakage/corrosion | Battery bank | Yes, for externally visible symptoms | Image can show swelling, leakage, corrosion, damaged terminals or poor physical condition. | Photo cannot establish capacity, state of health or DC-system adequacy. | D02; D05; D09
Broken/damaged insulator | Busbar / isolator / surge arrester / bushing | Yes, if visible | Image can show cracks, chips, breakage or contamination. | Photo cannot establish dielectric withstand or hidden internal defects. | D01; D02; D06; D09
Internal transformer fault | Transformer | No | Ordinary image may show external symptoms but cannot diagnose an internal electrical fault. | Requires appropriate tests/condition monitoring and authoritative criteria. | D03; D06; D08
Transformer insulation health | Transformer | No | External appearance cannot establish insulation condition. | Requires appropriate electrical/oil/diagnostic testing. | D04; D06; D08
Circuit-breaker contact wear/internal mechanism condition | Circuit breaker | Generally no | External photo may show mechanism indicators but not internal contact condition. | Requires equipment-specific inspection/testing. | D06; D09
Protection relay correctness | Protection relay | No | Photo may show settings/display but cannot prove logic or test performance. | Requires approved testing and controlled settings records. | D01; D02; D05; D09
Earthing-grid adequacy | Earthing system | No | A photo cannot measure grid resistance/impedance or touch/step potential. | Requires approved measurement/testing and engineering assessment. | D02; D05; D09