## 20_Answerable
Question ID | Question | Expected Answer | Expected Document | Document ID (KB) | Expected Page | Expected Section | Difficulty | Answer Available
Q001 | What is the preferable maximum operating temperature for a power transformer as measured by the Oil Temperature Indicator (OTI)? | Operating temperature should preferably be less than 70°C (measured through the OTI). | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.18 | Section 2.2.1 Major Operating Conditions for Power Transformers | Easy | TRUE
Q002 | Up to what fraction of its maximum MVA capacity should a power transformer generally be operated? | Generally not more than 2/3 of its maximum rated capacity (MVA). | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.19 | Section 2.2.1 Major Operating Conditions for Power Transformers | Easy | TRUE
Q003 | What colour change in the silica gel of a transformer breather indicates it needs reconditioning? | The silica gel becomes pink (or dark green for orange-type silica gel) from bottom to top over time, indicating it needs reconditioning/replacement. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.21 | Section 2.2.3 General Supervision of Power Transformer, item 7 (Silica Gel Breather) | Easy | TRUE
Q004 | At a manned 33/11kV substation, how often should the oil level in transformer bushings be checked? | Weekly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.26 | Section 2.2.4(B), Major Maintenance/Inspection Practices for Power Transformers, item 5 | Easy | TRUE
Q005 | How often should the condition/colour of silica gel in the dehydrating breather be checked at a manned substation? | Monthly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.26 | Section 2.2.4(B), item 11 (Dehydrating breather) | Easy | TRUE
Q006 | At what frequency should power transformer bushings and gaskets be examined for cracks, paint/dirt deposits, and gap settings? | Yearly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.26-27 | Section 2.2.4(B), item 12 (Bushing and gaskets) | Medium | TRUE
Q007 | How is the insulation resistance (IR) test for a power transformer to be evaluated during yearly inspection? | Check the IR values using a 2.5kV rated meggar, convert the reading to the reference temperature, and compare with the value taken at the time of commissioning. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.27 | Section 2.2.4(B), item 16 (Insulation resistance) | Medium | TRUE
Q008 | What is the recommended periodicity for a major overhaul (complete), including lifting of core and coils, of a power transformer? | 7 to 10 years (periodicity may be adjusted based on oil seepage/leakage, humming, IR value, PI value, and overall health). | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.29 | Section 2.2.4(B), items 47-48 | Medium | TRUE
Q009 | How often should oil leakage/seepage from the main tank to the OLTC (On-Load Tap Changer) tank be checked? | Weekly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.29 | On-Load Tap Changer Major Maintenance/Inspection Practices, item 1 | Easy | TRUE
Q010 | Below what dielectric strength value should the insulating oil in an oil circuit breaker (OCB) be filtered or replaced? | If the dielectric strength of the oil is found to be below 25 kV (or if there is a noticeable amount of carbon in suspension at the bottom of the tank). | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.39 | Section 2.3.3, item 43 (Oil dielectric and acidity test) | Medium | TRUE
Q011 | At what frequency should a Current Transformer (CT) be visually checked for damage and deterioration in a manned substation? | Weekly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.40 | Section 2.4, Major Maintenance Activities for CT, item 1 | Easy | TRUE
Q012 | What is the standard secondary voltage rating of a Potential Transformer (PT) at rated primary voltage, per the guideline? | Typically 110V, to match the input rating of protective relays. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.41 | Section 2.5 Potential Transformer (PT), introductory text | Easy | TRUE
Q013 | How frequently should a surge (lightning) arrester's operation-indicator/surge-counter reading and leakage current be recorded? | Monthly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.43 | Section 2.6, Major Maintenance Activities for LA, item 1 (Surge Counter) | Easy | TRUE
Q014 | What is the daily maintenance check prescribed for a substation battery room? | Ensure the battery room entrance doors are kept closed, ventilation to outside air is open, and air is circulated by running the exhaust fan. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.46 | Section 2.9, Major Maintenance Activities for Battery System, item 1 | Easy | TRUE
Q015 | How often should substation earth pits be checked as part of the earthing system maintenance? | Monthly. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.50 | Section 2.11, Major Maintenance Activities for Earthing System, item 1 | Easy | TRUE
Q016 | According to the CEA guideline, what are two major reasons cited for failure of Distribution Transformers (DTs)? | Major reasons include insulation failure, damage to the HT coil, damage to the LT coil, damage to core and laminations, failure of the tap switch/tap arrangement, and water ingress (any two qualify). | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.53 | Chapter 3.1 Introduction, table of Major/Minor Reasons for DT Failure | Medium | TRUE
Q017 | Which Indian Standard (IS) governs the maximum allowable losses for Distribution Transformers referenced in the guideline? | IS 1180 (Part-1: 2014, as amended). | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.54 | Chapter 3.1 Introduction, procurement considerations | Medium | TRUE
Q018 | What are the three broad maintenance practice categories described for distribution utilities in this guideline? | Preventive Maintenance, Predictive Maintenance (Condition Monitoring), and Reactive/Break-down Maintenance. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.6 | Section 1.2 Maintenance Practices | Easy | TRUE
Q019 | According to the guideline, at what voltage level are Vacuum Circuit Breakers (VCBs) generally used, versus SF6 breakers? | VCBs are generally used up to 33 kV level, while SF6 breakers are used at 66 kV and above. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.33 | Section 2.3 Circuit Breakers, introductory text | Medium | TRUE
Q020 | What is the recommended periodicity for Dynamic Contact Resistance Measurement (DCRM) for health assessment of an OLTC tap changer? | 5 years, or after replacement of any primary part of the OLTC. | DOC-CEA-2024 — CEA Guidelines for Benchmarking of Operation & Maintenance (O&M) Norms for Distribution Utilities, Central Electricity Authority, 2024 | D09 | p.30 | On-Load Tap Changer Major Maintenance/Inspection Practices, item 31 | Medium | TRUE

## 20_Unanswerable
Question ID | Question | Why It's Unanswerable (from current KB) | Answer Available | Category | Risk If Hallucinated
U001 | What is the exact torque specification (in Nm) for tightening the HV bushing terminal bolts on a 33kV power transformer? | The CEA guideline says to 'check tightness' but gives no numeric torque value; this is manufacturer/OEM-specific (e.g., in the transformer's technical manual), which is not yet in our KB. | FALSE | General/Numeric limit | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U002 | What is the exact replacement interval, in number of operations, for the vacuum interrupter in a specific manufacturer's 33kV VCB? | The guideline gives yearly inspection frequency but not an operations-based replacement threshold; that is OEM datasheet-specific and not present in our KB. | FALSE | Maintenance interval | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U003 | What is the SF6 gas refill cost per kg for a POWERGRID 765kV GIS bay? | Cost/pricing data is not part of any technical maintenance document collected; this is a commercial/procurement figure. | FALSE | Commercial data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U004 | What is the mean-time-between-failure (MTBF) for a 220kV current transformer installed in coastal environments? | No reliability statistics of this kind appear in the CEA guideline or in general maintenance procedure documents; this requires utility failure-analysis datasets we do not have. | FALSE | Reliability statistic | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U005 | What is the exact DGA (Dissolved Gas Analysis) gas concentration threshold (in ppm) that triggers a 'take out of service' decision for a specific transformer make/model? | The guideline references DGA testing generically but does not give ppm thresholds; IEEE C57.104 / IS 10593 values are not yet part of our KB. | FALSE | Testing limit | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U006 | What is the specific model number of relay recommended for busbar protection at a 400kV substation? | Not covered — the guideline discusses protection relay categories generally, not specific product/model recommendations. | FALSE | Equipment specification | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U007 | How many spare 33kV VCB breakers does POWERGRID maintain as a strategic reserve nationally? | This is internal utility inventory/asset data, not published in any technical maintenance document we have collected. | FALSE | Internal utility data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U008 | What is the exact warranty period offered by BHEL for a newly supplied power transformer? | Warranty terms are commercial/contractual information found in purchase contracts, not in technical maintenance guidelines. | FALSE | Commercial/contractual data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U009 | What is the minimum bending radius (in mm) permitted for 33kV XLPE underground cable during installation? | Cable-specific bending radius values are manufacturer datasheet parameters not present in the CEA O&M guideline collected so far. | FALSE | Equipment specification | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U010 | What is the exact acceptable range of Tan Delta (%) for a bushing to be considered healthy versus requiring replacement? | The guideline mandates that a Tan Delta test be carried out but does not state numeric pass/fail thresholds; those come from IS/IEC test standards not yet in our KB. | FALSE | Testing limit | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U011 | What is the recommended firmware update frequency for a Feeder Remote Terminal Unit (FRTU) modem? | Not covered — the guideline lists FRTU maintenance checks but does not specify firmware update cadence. | FALSE | Maintenance interval | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U012 | How many personnel casualties due to substation accidents were recorded nationally in the last five years? | No safety-incident statistics are present in the technical maintenance documents collected; this would require CEA safety audit/incident reports not yet retrieved. | FALSE | Safety statistic | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U013 | What is the average time taken to replace a failed distribution transformer in rural Bihar specifically? | State/region-specific operational KPI data is not present in the general CEA guideline; would require state DISCOM performance reports. | FALSE | Regional performance data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U014 | What is the exact chemical composition (in %) of the silica gel used in transformer breathers? | Not covered — the guideline describes the visual colour-change indicator but not the chemical composition of the desiccant. | FALSE | Equipment specification | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U015 | What is the minimum ambient temperature rating for outdoor SF6 circuit breakers as per IEC 62271? | IEC 62271 standard values are not part of our currently collected knowledge base; only CEA O&M guideline content is loaded. | FALSE | Standard-specific value | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U016 | What is the current market price of a lead-acid VRLA battery bank of 120Ah/220V rating in India? | Pricing/commercial data is outside the scope of the technical maintenance documents collected. | FALSE | Commercial data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U017 | How many 33/11kV substations in Maharashtra have adopted predictive maintenance as of this year? | State-level adoption statistics are not present in the CEA guideline (a national-level best-practice document) and would need MSETCL-specific reports. | FALSE | Regional/statistical data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U018 | What is the exact partial discharge (PD) threshold in pC that indicates insulation degradation in a GIS busbar? | The guideline mentions PD testing as an activity but does not specify numeric pC thresholds; this requires IEC 60270 or OEM-specific limits not yet in our KB. | FALSE | Testing limit | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U019 | What is the recommended cybersecurity patching interval for SCADA RTUs used in unmanned substations? | Not covered — the guideline addresses electrical/mechanical maintenance of SCADA-monitored parameters, not IT/OT cybersecurity practices. | FALSE | Out-of-domain / IT security | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.
U020 | What is the exact procurement lead time for a replacement 100 MVA power transformer from an Indian manufacturer? | Lead-time/supply-chain data is commercial information not present in technical O&M maintenance guidelines. | FALSE | Commercial/supply-chain data | System would fabricate a plausible-sounding but false numeric/technical value — the exact failure mode this test set is designed to catch.

## 10_Ambiguous
Question ID | Question | Why It's Ambiguous | Ideal System Behavior | Category
A001 | What should be checked on the transformer? | Does not specify: which transformer (power/distribution/dry-type)? Which check category (daily/weekly/yearly)? Manned or unmanned substation? | Ask a clarifying question (equipment sub-type + frequency tier) OR surface the multiple applicable checklists and let the engineer pick. | Transformer
A002 | What maintenance is required? | No equipment specified at all — could refer to any of 11+ equipment types covered in the KB. | Request equipment type before retrieving; do not guess and answer for an arbitrarily chosen equipment. | General
A003 | How should the breaker be inspected? | Doesn't specify breaker type (VCB / SF6 / OCB / ACB) — each has a different inspection checklist and frequency in the KB. | Ask which breaker type, or list all breaker types with a one-line differentiator. | Circuit Breaker
A004 | Is the equipment healthy? | No equipment identified, no readings/parameters provided to judge 'healthy' against documented limits. | Ask which equipment and what specific readings/observations are available. | General
A005 | When should I do the yearly checks? | 'Yearly checks' spans dozens of distinct checklist items across multiple equipment types with different one-year-cycle anchors (commissioning date vs. calendar year). | Ask which equipment/checklist item, since 'yearly' is not a single unified schedule. | General
A006 | What is the limit? | No parameter (e.g., dielectric strength, IR value, temperature) or equipment specified. | Ask which parameter and which equipment before answering. | General
A007 | Why did it trip? | No indication of which alarm/trip (differential, OTI, WTI, Buchholz, O/C, E/F, etc.) or which equipment tripped. | Ask for the specific alarm/trip signal and equipment before retrieving probable-cause information. | Transformer / Protection
A008 | What documents do we have on batteries? | Ambiguous between battery bank maintenance, battery charger maintenance, or DC system troubleshooting — each is a distinct KB section. | Ask whether the query concerns the battery bank, the charger, or DC-system faults. | Battery
A009 | Is this within safe limits? | No parameter, value, or equipment given to compare against a documented limit. | Ask what value was measured, for which parameter, on which equipment. | General/Safety
A010 | How often should earthing be checked? | 'Earthing' spans several distinct sub-items (earth pits, earth conductors, mesh resistance, equipment-frame earthing) with different frequencies (monthly/half-yearly/yearly) in the KB. | Ask which earthing sub-item (pit inspection vs. resistance measurement vs. conductor tightness) is meant, or list all with their respective frequencies. | Earthing

## 5_Conflicting_PENDING
Status | Note
NOT YET CREATED | Per team rule: 'ONLY create these if we actually find legitimate different versions/documents. DO NOT manufacture conflicts.' As of this research pass, Member 1's document catalog contained only ONE authoritative document (CEA O&M Benchmarking Guidelines, 2024) reviewed in depth, plus several CEA/PFC/DISCOM regulatory documents (safety regulations, construction standards) that address different topics rather than conflicting versions of the same topic. No genuine version conflict (e.g., an older CEA circular vs. a newer one giving a different maintenance interval for the same equipment/parameter) has been confirmed yet. ACTION NEEDED: once Member 1 finalises document_catalog.xlsx, cross-check for same-topic documents with different effective dates (e.g., an older State DISCOM circular vs. this 2024 CEA guideline) and populate this sheet only with confirmed, source-cited conflicts. Do not fabricate placeholder conflicts.

## Correction_Log
Question ID | Old Expected Page | Corrected PDF Page | Verification Basis
Q001 | p.14 | p.18 | Rendered PDF p.18: 70°C OTI limit
Q002 | p.15 | p.19 | Rendered PDF p.19: 2/3 MVA capacity
Q003 | p.17 | p.21 | Rendered PDF p.21: silica gel colour change
Q004 | p.22 | p.26 | Rendered PDF p.26: bushing oil level, weekly
Q005 | p.22 | p.26 | Rendered PDF p.26: dehydrating breather, monthly
Q006 | p.22-23 | p.26-27 | Rendered PDF pp.26-27: bushings/gaskets, yearly
Q007 | p.23 | p.27 | Rendered PDF p.27: insulation resistance, yearly
Q008 | p.24-25 | p.29 | Rendered PDF p.29: major overhaul, 7–10 years
Q009 | p.25 | p.29 | Rendered PDF p.29: OLTC leakage/seepage, weekly
Q010 | p.35 | p.39 | Rendered PDF p.39: OCB oil dielectric threshold
Q011 | p.36 | p.40 | Rendered PDF p.40: CT maintenance section
Q012 | p.37 | p.41 | Rendered PDF p.41: PT secondary, typically 110 V
Q013 | p.39 | p.43 | Rendered PDF p.43: surge counter, monthly
Q014 | p.42 | p.46 | Rendered PDF p.46: battery room/ventilation, daily
Q015 | p.47 | p.50 | Rendered PDF p.50: earth pits, monthly
Q016 | p.49 | p.53 | Rendered PDF p.53: DT failure reasons
Q017 | p.51 | p.54 | Rendered PDF p.54: IS 1180 reference
Q018 | p.2 | p.6 | Rendered PDF p.6: maintenance practice categories
Q019 | p.29 | p.33 | Rendered PDF p.33: VCB/SF6 voltage levels
Q020 | p.26 | p.30 | Rendered PDF p.30: DCRM periodicity