## ambiguous
Question ID | Question | Why It's Ambiguous | Ideal System Behavior | Category
V2-A01 | What is the maximum operating temperature for the transformer? | D01 and D08 give several materially different 'temperature' limits depending on what is meant: winding hot-spot temperature during a cooling-system failure (140°C, D01-C0014/D08), top-oil temperature rise (40°C, D01-C0023), or oil-circulation process temperature (70°C ceiling to avoid oxidation, D07-C0079). Without specifying which temperature (oil vs winding; rise vs absolute; normal vs abnormal/failure condition) and which equipment/operating regime, no single correct answer exists. | Ask which temperature quantity is meant (top-oil rise, winding hot-spot, or a specific test/process temperature) and under what condition (normal operation vs cooling failure vs oil processing) before answering. | Transformer / thermal limits
V2-A02 | How often should the surge arrester be tested? | D06's recommendations describe conditionally-triggered actions, not a single fixed periodicity: the 3rd-harmonic leakage-current component should be 'regularly monitored' (no fixed interval given), an IR value test is only required once leakage exceeds 150µA, and removal/replacement is only triggered above 350µA. 'How often' has no single numeric answer without specifying which of these three actions is meant. | Clarify which surge-arrester check is meant (routine leakage-current monitoring vs. conditional IR test vs. replacement trigger) before giving a periodicity, since only some of these have a fixed interval and others are condition-triggered. | Surge arrester / testing frequency
V2-A03 | What is the short-circuit withstand current level for the transformer? | D08-C0047 gives materially different short-circuit levels depending on system voltage class: 63 kA/1sec for 765kV and 400kV systems, 50 kA/1sec for 220kV systems, and other values for 132kV/66kV. The question does not specify which voltage class of transformer/system is meant. | Ask which voltage class (765kV/400kV/220kV/132kV/66kV) the transformer belongs to before returning a specific kA/duration figure. | Transformer / short-circuit rating
V2-A04 | How long can the transformer be stored before oil-filling is required? | D07 gives two different thresholds that trigger two different actions: storage is permitted up to 6 months under maintained nitrogen pressure without further action (D07-C0039), but if storage without oil exceeds 18 months, BHEL must specifically be consulted (D07-C0040) — implying an intermediate zone (6-18 months) with different handling than either endpoint. The question as posed doesn't specify which threshold/outcome is being asked about. | Ask whether the question concerns the 'no special action needed' threshold (6 months) or the 'manufacturer consultation required' threshold (18 months), since these represent different decision points. | Transformer / storage before installation
V2-A05 | What test should be conducted on the circuit breaker? | D06 discusses multiple distinct circuit-breaker condition-monitoring tests (Dynamic Contact Resistance Measurement, Operational Analyzer-based diagnostics) without specifying which is being asked about, and 'circuit breaker' itself is not qualified by voltage class or type (SF6/vacuum/air-blast), each of which may have different applicable tests within the corpus. | Ask which test category is intended (contact-resistance/DCRM, operational timing/Operational Analyzer, or another) and which breaker type/voltage class, before answering with a specific test procedure. | Circuit breaker / testing
V2-A06 | What maintenance is required for the bushing? | Bushing-related content spans multiple distinct maintenance activities across D06 and D08 with different periodicities and triggers: monthly external cleaning (D08-C0532), capacitance/tan-delta measurement 'at periodic intervals' compared against previous references (D08-C0450), and DGA of bushing oil for health assessment (D06-C0137) — none of which is 'the' single maintenance activity implied by the question. | Ask which specific bushing maintenance activity is meant (routine cleaning, tan-delta/capacitance testing, oil DGA, or another) before answering, since each has a different procedure and periodicity. | Bushing / maintenance